## Fire Risk Assessment by Team Us
Fire Risk Assessment by Team / User
Total: 108
Risk Assessment | Process Start Date | Prop ref | Block | Process No | Proc Status | Iitem no | Priority | Category | Risk | Action | Team | Who | Action Due Date | Action taken | Comp date | Full or partial | Reporting User | Feedback Start Date | Feedback Due Date | Closure Start Date | Closure Due Date | Date Difference | In Target | Return Stage Startdate | Return Stage Duedate | Return User
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:18 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201707 | Active | 12a | High | Flat Door | The flat entrance door to flat number 5 has been changed to a 6 panel door, it is not known if this a self closing 30 minute fire rated door. | I would recommend that this flats entrance door is checked to see if it is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD 30s) If it is not then it should be replaced with FD 30s door complying with all the requirements of the Building Regulations. | Home Ownership | David Ward | 2015-07-08 | emailed leaseholder Leaseholder comments that the door has not been changed for 20 years since the property was purchased - referred back to H&S | 2015-07-08 | Partially Completed | David Ward | 2015-06-16 10:18 | 2015-07-07 10:29 | 2015-06-16 10:18 | 2015-08-07 15:32 | -21 | In target | 2015-06-16 10:18 | 2015-08-04 15:52 | David Ward
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 11:00 | S217009467707 | MORGAN ROAD ODD (1-11) | 102424 | Completed | 12 | Information Only | Flat Door | The flat entrance doors to flats 5, 7 and 11 are the originally fitted doors, these are not fitted with self closing devices. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | Jannie Pretorius |  | You may want to record that at the time of this FRA in February 2013 the assessor noted that the original doors were still in situ, however, if they are to be replaced they must then comply with all current fire safety standards. | 2013-08-28 | Fully Completed |  |  |  | 2013-08-19 11:00 | 2014-01-08 15:15 |  |  | 2013-08-19 11:00 | 2014-01-14 15:15 | Janice Wray
12 RUSSELL GARDENS - 2014.6.11 | 2014-06-30 15:49 | S217006670002 | RUSSELL GARDENS (12) | 151048 | Completed | 12a | High | Flat Door | The glazing in the vision panel of flat B's door is not fire rated, [REDACTED] verbally agreed to have the glazing in the vision panel of the door changed to fire rated glazing | Further to the verbal agreement to the Fire Risk Assessor from [REDACTED] can it please be confirmed that he has changed the piece of glass in this flat door's vision panel to a piece of fire rated glazing. (Alternatively a new 30minute self closing fire door can be fitted as flat B's entrance door.) | Home Ownership | Nazrul Islam |  | From: Nazrul Islam Sent: 09 July 2014 11:33 To:[REDACTED] Subject: 12B Russell gardens - front door (FRA) Dear [REDACTED] I'm writing to you regarding your front door. I understand from the Fire Risk Assessor that the glazing in the vision panel of flat B's door is not fire rated, you verbally agreed to have the glazing in the vision panel of the door changed to fire rated glazing Please confirm that you have changed the piece of glass in this flat door's vision panel to a piece of fire rated glazing. Alternatively a new 30minute self closing fire door can be fitted as flat B's entrance door. Please contact Janice Wray, Health and Safety Manager on [REDACTED], if you have any further enquiries. Regards Mr Nazrul Islam Home Ownership Officer t: [REDACTED] w: www.kctmo.org.uk a: Network Hub, 292a Kensal Road,London W10 5BE | 2014-07-09 | Fully Completed | Nazrul Islam | 2014-06-30 15:49 | 2014-07-21 15:50 | 2014-06-30 15:49 | 2014-07-31 10:22 | -21 | In target | 2014-06-30 15:49 | 2014-07-22 11:39 | Nazrul Islam
123 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:35 | S217002110005 | FINBOROUGH ROAD 123 A-H | 194201 | Completed | 12 | High | Flat Door | The flat entrance door to flat G has been changed from the originally fitted fire rated door. | Can it please be confirmed this flat entrance door is a self closing 30 minute fire rated door. | Home Ownership | Nazrul Islam |  | wrote to lesee From: Nazrul Islam Sen[REDACTED] Subject: Flat G 123 Finborough Road - Front Door Dear [REDACTED] I have been informed by our Health and Safety Manager that he flat entrance door to flat G 123 Finborough Road has been changed from the originally fitted fire rated door. As a result of this, it is possible that your front entrance door may not be a FD30 compliant door. I must therefore request the following: " Can it please be confirmed this flat entrance door is a self closing 30 minute fire rated door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] Regards Mr Nazrul Islam Home Ownership Officer t: [REDACTED] w: www.kctmo.org.uk a: Network Hub, 292a Kensal Road,London W10 5BE Carl Stokes viisted & assessed door on 11th June 2015 & has confirmed door & transom to be nominally fire rated & COMPLIANT | 2015-06-11 | Fully Completed | Nazrul Islam | 2015-04-27 09:35 | 2015-05-18 09:36 | 2015-04-27 09:35 | 2015-06-16 09:01 | -21 | In target | 2015-04-27 09:35 | 2015-06-22 09:00 | Janice Wray
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:42 | S217012740015 | BLANTYRE WALK 1-42 | 139342 | Completed | 12b | High | Flat Door | The lower fire rate glass pane in the flat entrance door of flat 9 Blantyre Walk is cracked straight across. | The fire rated glazing in the lower door panel should be replaced so that the flat entrance door is fully fire rated. | Home Ownership | David Ward |  | Please confirm which property this relates to; the block states Berenger Walk but the risk states 9 Blantyre Walk email sent to leaseholder 19.6.14 | 2014-06-19 | Fully Completed | David Ward | 2014-04-10 14:42 | 2014-05-01 14:44 | 2014-04-10 14:42 | 2015-04-10 14:25 | -21 | In target | 2014-04-10 14:42 | 2014-07-07 17:46 | David Ward
13 TADEMA ROAD, LONDON SW10 ONX - 2015.12.15 | 2016-02-16 09:12 | S217005360001 | TADEMA ROAD (13) | 243583 | Active | 0 | High | Miscellaneous | Structural building work has been undertaken within flat C which is now mostly an open plan dwelling. There is no record of any building work having been notified to the RBKC Building Control Department. | Can it please be confirmed that the TMO are aware of structural building work having been undertaken within flat C? Has the work including within this flat been signed off as compliant? No application received for works LEASEHOLD FLAT | Home Ownership | Nazrul Islam | 2016-03-17 | This is now with A&R (Leasehold Alteration team) please forward onto to Liza or Graham | 2016-02-16 | Fully Completed | Nazrul Islam | 2016-02-16 09:12 | 2016-03-08 09:14 | 2016-02-16 09:12 | 2016-02-17 15:21 | -21 | In target
13 TADEMA ROAD, LONDON SW10 ONX - 2015.12.15 | 2016-02-16 09:15 | S217005360001 | TADEMA ROAD (13) | 243585 | Active | 12 | High | Flat Door | A new flat entrance door has been fitted to flat C this year, this flat is being leased out. This new door is not marked as a 30 minute fire rated door (FD30) nor is it fitted with a self closing device or intumescent strips and cold smoke seals as it is required to be by the current Building Regulations. | This entrance door should be replaced with a self closing 30 minute fire rated door (FD30s) fitted with intumescent strips and cold smoke seals and complying with all the requirements of the Building Regulations. LEASEHOLD FLAT | Home Ownership | Nazrul Islam | 2016-03-17 | Liza has written to the leaseholder about the front door not complaince with (FD30s) | 2016-02-16 | Partially Completed | Nazrul Islam | 2016-02-16 09:15 | 2016-03-08 09:21 | 2016-02-16 09:15 | 2016-02-17 15:23 | -21 | In target
13 TADEMA ROAD, LONDON SW10 ONX - 2015.12.15 | 2016-02-16 09:22 | S217005360001 | TADEMA ROAD (13) | 243591 | Active | 17 | High | Fire Alarm | The new domestic fire alarm system within flat C does not appear the be installed in accordance with the British Standard, BS5839 Part 6 :2013. | I would recommend that the TMO ask the leaseholder of flat C for a copy of the BS 5839 Part 6 2013 installation, commissioning certificate for the installed domestic fire alarm system within this flat. LEASEHOLD FLAT | Home Ownership | Nazrul Islam | 2016-03-17 | Liza from (A&R) has written to the leaseholder . | 2016-02-16 | Fully Completed | Nazrul Islam | 2016-02-16 09:22 | 2016-03-08 09:23 | 2016-02-16 09:22 | 2016-02-17 15:26 | -21 | In target
140 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:54 | S217002110014 | FINBOROUGH ROAD (140) | 194211 | Active | 12c | High | Flat Door | The entrance door to flat A has been changed from the originally fitted fire rated door. | Can it be confirmed the entrance door to flat A is a 30 minute fire rated door, fitted with a self closing device, capable of shutting the door fully on to its stops. | Home Ownership | David Ward |  | emailed leaseholder Leaseholder asked for reference in the lease which there isnt so further advice sought from H&S 5/8/15 | 2015-07-08 | Partially Completed | David Ward | 2015-04-27 09:54 | 2015-05-18 09:55 | 2015-04-27 09:54 | 2015-08-06 14:35 | -21 | In target | 2015-04-27 09:54 | 2015-08-04 16:57 | David Ward
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:21 | S217012740003 | UPPER BERENGER WALK 1-42 | 139410 | Completed | 12d | Information Only | Flat Door | The flat entrance door has been changed from the originally fitted fire rated flat entrance door. This entrance door appearsnot to be fire rated. Flat 37 Upper Berenger Walk - lessee | Assessor recommends that a letter is sent to the leaseholders reminding them that if they change their flat entrance door that it must comply with the requirements of the current Building Regulations. ie all replacement flat entrance doors, even those off open external | Home Ownership | David Ward |  | The lessee received a letter of this type in 2012. | 2014-04-14 | Fully Completed |  |  |  | 2014-04-10 16:21 | 2014-04-15 09:59
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:19 | S217010567701 | LONGLANDS COURT (1-48) | 103179 | Completed | 12a | High | Flat Door | The entrance doors to flats 17 and 19 have been changed from the originally fitted doors and these doors now do not appear to be 30 minute fire rated doors (FD30). | The entrance doors to flats 17 and 19 should be checked to see that they are FD30 doors complying with the requirements of the Building Regulations and fitted with a self closing device. If they are not they should be replaced with FD 30 doors fitted with self closing devices. | Home Ownership | Jannie Pretorius |  | 28082013 Following letter forwarded to leaseholders of flats 17 & 19: Further to our letter of the 11th October 2012 in respect of the fire rating of leasehold front doors I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review of Longlands Court. As a result of this review, it has come to light that your front entrance door may not be a FD30 compliant door. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED]. Flat 17 assessed by Carl Stokes on 8th Oct 2013 & confirmed COMPLIANT. Flat 19 - lessee confirms door COMPLIANT & has provided info on door. | 2013-08-28 | Fully Completed | Jannie Pretorius | 2013-08-21 16:19 | 2013-09-11 16:21 | 2013-08-21 16:19 | 2014-01-03 10:49 | -21 | In target | 2013-08-21 16:19 | 2014-01-09 10:46 | Janice Wray
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:39 | S217010567701 | LONGLANDS COURT (1-48) | 103194 | Completed | 12d | Information Only | Flat Door | The following flat entrance doors are the original fire rated flat entrance doors and were fitted with a self closing device. These are flush solid doors and are all close fitting. These flats are numbers 9, 10, 11, 22, 29, 32, 33, 35, 36, 38, 41, 42, 46 and 47. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | Jannie Pretorius |  |  | 2013-08-29 | Fully Completed |  |  |  | 2013-08-21 16:39 | 2014-01-08 15:17 |  |  | 2013-08-21 16:39 | 2014-01-14 15:16 | Janice Wray
1-52 UPPER WHISTLER WALK - 2014.3..12 | 2014-04-11 09:14 | S217012740009 | UPPER WHISTLER WALK 1-52 | 139455 | Completed | 12d | Information Only |  | This flat entrance door has been changed from the originally fitted fire rated flat entrance door. This flat entrance doors appear not to be fire rated. Flat 21 Upper Whistler Walk - lessee Assessor confirms that this door does not require upgrade or replacement at this stage. | Assessor recommends that a letter is sent to the leaseholders reminding them that if they change their flat entrance door that it must comply with the requirements of the current Building Regulations. ie all replacement flat entrance doors, even those off open external | Home Ownership | David Ward |  | The owners of this property have not changed since the 'standard' letter to all leaseholders was sent in 2012 re firedoors. | 2014-04-14 | Fully Completed |  |  |  | 2014-04-11 09:14 | 2014-04-15 09:24
1-58 UPPER DARTREY WALK - 2014.3.12 | 2014-04-10 16:52 | S217012740007 | UPPER DARTREY WALK 1-58 | 139427 | Active | 12b | High | Flat Door | The door of flat 53 Upper Dartrey Walk is damaged with the fire rate glass cracked straight across the upper panel in the door. | This door and the glazing should be repaired or the door completely replaced so that the flat entrance door is fully fire rated. | Home Ownership | David Ward |  | Emailed leaseholder 19.6.14 leaseholder emailed again 7.5.15 letter sent 6.8.15 response 11.8.15 - financial constraints mean they cannot replace the glazing at this time. Also, had a repair issue outstanding for 12 months which add to their frustration | 2015-05-07 | Partially Completed | David Ward | 2014-04-10 16:52 | 2014-05-01 16:53 | 2014-04-10 16:52 | 2014-06-20 10:06 | -21 | In target | 2014-04-10 16:52 | 2014-07-03 10:00 | David Ward
162 FINBOROUGH ROAD, LONDON SW10 9AH - 2016.01.05 | 2016-01-28 12:46 | S217002110015 | FINBOROUGH ROAD (162) | 240046 | Completed | 12 | High | Flat Door | The entrance door of flat D, the 2nd floor level flat is an outward opening, 6 indented panel door, this is different to the other 2 flat entrance doors. | Can it please be confirmed that this flat entrance door is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals? (FD 30s) If it is not then it should be replaced with FD 30s door complying with all the requirements of the Building Regulations and the Fire Safety Order. | Home Ownership | Nazrul Islam | 2016-02-26 | Liza from A&R dealt with alteration ,which front door was inlcuded. | 2016-02-23 | Fully Completed | Nazrul Islam | 2016-01-28 12:46 | 2016-02-18 12:48 | 2016-01-28 12:46 | 2016-02-24 11:37 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:04 | S217002110007 | FINBOROUGH ROAD (169) | 194363 | Completed | 12 | High | Flat Door | Flat Ks flat entrance door has been changed from the originally fitted fire rated door. | Can it please be confirmed the entrance door to flat K is a 30 minute fire rated door, fitted with a self closing device capable of shutting the door fully on to its stop? | Home Ownership | Nazrul Islam |  | written to[REDACTED] to confirm if the front door is fire rated as requested. [REDACTED] requested C Stokes to visit and assess door (but but at home on day of visit). Assessor believes glazing in top of door may not be fire-rated but has confirmed it can remian in situ as bottom of door solid timber & because of location of flat walkwat etc.advised lessee | 2015-05-26 | Fully Completed | Nazrul Islam | 2015-04-27 16:04 | 2015-05-18 16:06 | 2015-04-27 16:04 | 2015-05-27 08:33 | -21 | In target | 2015-04-27 16:04 | 2015-06-02 08:30 | Janice Wray
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:13 | S217009620004 | OXFORD GARDENS (187) | 241811 | Active | 12 | High | Flat Door | The flat entrance door of flat 11 has been changed from the original fire rated door, this flat entrance door is now not a fire rated door. | This flat entrance door should be replaced with a self closing 30 minute fire rated door, complying with the requirements of the current Building Regulations. LEASEHOLD FLAT Door fitted since previous FRA Dec 2011 | Home Ownership | Samuel Anyanwu | 2016-03-01 |  |  |  | Cyril Morris | 2016-02-08 11:13 | 2016-02-29 11:15 |  |  | 37 | 37 days overdue
20 GUNTER GROVE, LONDON SW10 0UJ - 2015.11.30 | 2016-03-21 16:59 | S217002400001 | GUNTER GROVE (20) | 250336 | Active | 12 | High | Flat Door | Flat Bs entrance door appears to be a fire rated door, but it is not known if a self closing device is fitted to this flat entrance door. | Please can it be confirmed that the flat entrance door of flat B, which is a 4 indented panel timber door has a self closing device fitted to it? If it does not then a self closing device should be fitted to this flat entrance door. | Home Ownership | Nazrul Islam | 2016-04-18 |  |  |  | Cyril Morris | 2016-03-21 16:59 | 2016-04-11 17:00 |  |  | -4 | 4 days to target date
21 TO 29 NORWOOD ROAD - 2015.09.24 | 2015-10-05 11:41 | S206023300001 | NORWOOD ROAD (21-29) | 219969 | Active | 12a | High | Flat Door | he flat entrance door to flat 7 has been changes since the last FRA of this building was undertaken. | Can it please be confirmed if the flat entrance door of flat 7 is a 30 minute fire rated door and fitted with a self closing device? | Home Ownership | Nazrul Islam |  | letter sent 11/11/15 spoke to lessee 25/11/15 - no confirmation re door - details passed to Carl via Janice | 2015-11-11 | Partially Completed | David Ward | 2015-10-05 11:41 | 2015-10-26 11:42 | 2015-10-05 11:41 | 2015-11-12 10:19 | -21 | In target | 2015-10-05 11:41 | 2015-11-20 18:31 | David Ward
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 14:47 | S217001880014 | ELM PARK GARDENS (22) | 202858 | Completed | 12a | High | Flat Door | It is not known if the newly fitted flat entrance door of flat 7, fitted last year 2014, is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals, (FD30s) as required by the Building Regulations. | Can it please be confirmed that this flat exit door is a FD30s door, fitted with a self closing device? If it is not then a self closing FD30s door must be fitted. | Home Ownership | David Ward | 2015-09-23 | emailed managing agents this door has not been changed either Assessed by Carl Stokes in Feb 2016 and COMPLIANT | 2016-03-13 | Fully Completed | David Ward | 2015-06-23 14:47 | 2015-07-14 14:49 | 2015-06-23 14:47 | 2016-03-14 17:26 | -21 | In target | 2015-06-23 14:47 | 2016-03-20 17:24 | Janice Wray
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 11:05 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215855 | Active | 12a | High | Flat Door | The flat entrance door of flat 46 appear to be a newly fitted door. LEASEHOLD | Can it please be confirmed if the flat entrance door of flat 46 is a self closing 30 minute fire rated door? | Home Ownership | Samuel Anyanwu |  | emailed lessee 11.11.15 | 2015-11-11 | Partially Completed | David Ward | 2015-09-10 11:05 | 2015-10-01 11:07 |  |  | 188 | 188 days overdue
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 11:07 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215856 | Active | 12b | High | Flat Door | It is not known if the flat entrance door of flat 10 is a fire rated door. LEASEHOLD | Can it please be confirmed if the flat entrance door of flat 10 is a self closing 30 minute fire rated door? | Home Ownership | Samuel Anyanwu |  | emailed lessee 11.11.15 | 2015-11-11 | Partially Completed | David Ward | 2015-09-10 11:07 | 2015-10-01 11:08 | 2015-09-10 11:07 | 2015-11-12 11:23 | -21 | In target | 2015-09-10 11:07 | 2015-11-20 18:23 | David Ward
25 BASING STREET - 2015.08.13 | 2015-09-02 14:21 | S217008090003 | BASING STREET (25) | 214571 | Active | 12 | High | Flat Door | It appears that the Georgian wired fire rated glazing originally in the vision panel of flat 1's entrance door has been replaced with a piece of frosted glass. LEASEHOLD | Can it please be confirmed that the glazing in flat 1's entrance door is fire rated glazing? If it is not then it should be changed for fire rated glazing. | Home Ownership | Samuel Anyanwu |  | Emailed lessee 11.11.15 | 2015-11-11 | Partially Completed | Janice Wray | 2015-09-02 14:21 | 2015-09-23 14:23 | 2015-09-02 14:21 | 2015-09-17 16:36 | -21 | In target | 2015-09-02 14:21 | 2015-12-02 13:26 | David Ward
32 DAWSON PLACE, LONDON W2 4TJ - 2016.02.02 | 2016-02-23 16:30 | S217007110001 | DAWSON PLACE (32) | 245317 | Active | 12d | High | Flat Door | It is not known if a self closing device is fitted to flat 3's entrance door, this is an original apartment entrance door. LEASEHOLD | Flat entrance doors off internal protected areas should be fitted with self closing devices, I would recommend that a self closing device is fitted to this flat entrance door if one is not already fitted. | Home Ownership | Nazrul Islam | 2016-03-22 | E-mailed Lessee asking for comfirmation. Lessee sub-lets property and has agree to investigate. | 2016-03-15 | Partially Completed | Nazrul Islam | 2016-02-23 16:30 | 2016-03-15 16:32 | 2016-02-23 16:30 | 2016-03-29 16:27 | -21 | In target | 2016-02-23 16:30 | 2016-03-31 16:26 | Janice Wray
32 ST CHARLES SQUARE - 2015.04.20 | 2015-04-27 14:52 | S217010080001 | ST CHARLES SQUARE (32) | 194316 | Active | 12a | High | Flat Door | The area around the door lock on flat A's entrance door has been damaged. | I would recommend that this flat entrance door is checked to see that this door is still a fire rated door, if it is not then a new 30 minute fire rated door (FD 30S) complying with the requirements of the Building Regulations should be fitted. | Home Ownership | David Ward | 2015-09-08 | Emailed NHHG on 15.7.15 NHHG have asked for reference from the Lease that references that it has to be changed. This is not there so advice as to how to proceed sought from H&S | 2015-07-15 | Partially Completed | David Ward | 2015-04-27 14:52 | 2015-05-18 14:53 | 2015-04-27 14:52 | 2015-08-06 14:05 | -21 | In target | 2015-04-27 14:52 | 2015-08-04 16:53 | David Ward
51 STADIUM STREET, LONDON SW10 OPX - 2015.11.30 | 2016-04-04 16:17 | S217005190004 | STADIUM STREET (51) | 252415 | Active | 12 | High | Flat Door | The flat entrance door of flat A was fitted as part of the refurbished of this flat at the end of 2012 or in early 2013. | Please can it be confirmed this flat entrance door is a certified 30 minute fire rated door fitted with a self closing device and intumescent strips and cold smoke seals (FD30s) complying with all the requirements of the Building regulations. Documentation should be provided to show that the flat entrance door is a FD30s door and photographs showing the self closing device fitted top the door. If this is not a self closing FD30s door then one must be fitted. | Home Ownership | Nazrul Islam | 2016-05-09
51 STADIUM STREET, LONDON SW10 OPX - 2015.11.30 | 2016-04-04 16:20 | S217005190004 | STADIUM STREET (51) | 252416 | Active | 17 | High | Fire Alarm | When flat A was refurbished an interlinked electrically powered /operated domestic smoke and heat detection/sounder system was installed. A smoke detector/sounder of Flat A's system was installed within flat B as well. So when Flat A's system activates so does the sounder in flat B. The occupant of flat B has said that she asked the TMO about the installation of a device of flat A's fire detection system in her flat but received no advice back from the TMO and the leaseholder of flat A had the detector installed within the TMO tenanted flat. The tenant of flat B has complained to the TMO about the false activations but has not had any response back from the TMO. | I would strongly recommend that the domestic interlinked electrically powered/operated smoke detection/sounder of flat A's fire alarm system is removed from flat B as soon as possible. I would also recommend that the TMO records are examined and it is looked at as to why a fire alarm detector/sounder of a leaseholder's domestic fire alarm system, from their flat was allowed to be installed in a TMO tenanted flat. Installing domestic fire detectors/sounders, BS 5839 Part 6 devices interlinked in multiple flats is not to the requirements of this British Standard. | Home Ownership | Nazrul Islam | 2016-05-09
53 STADIUM STREET, LONDON SW10 OPX - 2015.11.30 | 2016-04-04 16:30 | S217005190005 | STADIUM STREET (53) | 252425 | Active | 12 | High | Flat Door | The flat entrance door of flat A or 1 was fitted as part of the refurbished of this flat in 2013/14. | Please can it be confirmed this flat entrance door is a certified 30 minute fire rated door fitted with a self closing device and intumescent strips and cold smoke seals (FD30s) complying with all the requirements of the Building regulations. Documentation should be provided to show that the flat entrance door is a FD30s door and photographs showing the self closing device fitted top the door. If this is not a self closing FD30s door then one must be fitted. | Home Ownership | Nazrul Islam | 2016-05-09
53 STADIUM STREET, LONDON SW10 OPX - 2015.11.30 | 2016-04-04 16:33 | S217005190005 | STADIUM STREET (53) | 252429 | Active | 17 | High | Smoke Alarms | There is a commercial BS 5839 Part 1 smoke detector, a fire alarm break glass call point and a siren installed in the ground floor level entrance hall area of this building. In the TMO controlled common part of this building along with a domestic BS 5839 Part 6 smoke detector on the ceiling next to the Part 1 smoke detector. It appears that these 2 different fire alarm systems were installed when flat A/1 was refurbished in 2013/14. No control panel was seen for the BS 5839 Part 1 fire alarm system. The common parts of this building do not require a fire alarm detection and warning system to be fitted in them, let along 2 different systems. One of which appears not to be under the control of the TMO. | I would recommend that both of the fire alarm systems are removed from the TMO controlled common parts of this building as soon as possible. If the fire alarm systems are not removed from the common parts of this building then this fire risk assessment should be reviewed to reflect the installation of both a Part 1 and a Part 6 BS 5839 fire alarm system in the TMO controlled common parts of a residential building. | Home Ownership | Nazrul Islam | 2016-05-09
53 STADIUM STREET, LONDON SW10 OPX - 2015.11.30 | 2016-04-04 16:35 | S217005190005 | STADIUM STREET (53) | 252435 | Active | 23 | High | Fire Alarm | There is a commercial BS 5839 Part 1 fire alarm or warning systems installed in the ground floor level entrance hall/lobby area of this building, ie in the TMO controlled common part of this building. Please see item 17 above as well. | These fire alarm systems are not being tested and as far as I know not being serviced, if the two fire alarm systems are not removed then servicing and testing must be undertaken and this FRA reviewed to cover fire alarm procedures etc for the residents of this building. Also fire action notices etc will have to be displayed in this building along with how the TMO will access the BS 5839 Part 1 fire alarm system control panel if it is located within the ground floor level flat. | Home Ownership | Nazrul Islam | 2016-05-09
61 GOLBORNE ROAD, LONDON W10 5NR - 2016.01.07 | 2016-02-17 12:38 | S217008770004 | GOLBORNE ROAD (61) | 244005 | Active | 1a | High | Mobility Scooters | An electrical cable has been tacked to the entrance hall skirting board, plugged into the landlords electrical supply and has a plug on the other end which is used to charge the battery of a mobility scooter, which is parked at the base of the staircase in the entrance hall area. | I would recommend that this electrical cable and socket is removed and the charging of the mobility scooter in the entrance hall area/means of escape route is stopped immediately. Mobility scooter belongs to lessee of flat A | Home Ownership | Samuel Anyanwu | 2016-03-16 |  |  |  | Cyril Morris | 2016-02-17 12:38 | 2016-03-09 12:40 |  |  | 28 | 28 days overdue
61 GOLBORNE ROAD, LONDON W10 5NR - 2016.01.07 | 2016-02-17 17:10 | S217008770004 | GOLBORNE ROAD (61) | 244145 | Active | 13 | High | Miscellaneous | At the time of this assessment there was a mobility scooter parked and being charged in the ground floor level entrance hall area of the residential part of this building. There is an electrical socket on the wall next to this mobility scooter. | The H M Government fire safety document for purpose built blocks of flats does not allow the charging of mobility scooters in the common parts of residential buildings. I would recommend that the electrical socket on the wall is removed so that charging cannot be undertaken in this area. | Home Ownership | Samuel Anyanwu | 2016-03-16 |  |  |  | Cyril Morris | 2016-02-17 17:10 | 2016-03-09 17:12 |  |  | 28 | 28 days overdue
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:15 | S217002110008 | FINBOROUGH ROAD (62) | 102945 | Completed | 12e | High | Flat Door | The entrance door to flat 27 has recently been changed from the originally fitted door. | Can it please be confirmed that this newly fitted flat entrance door is a 30 minute fire rated door fitted with a self closing device etc and complying with all the requirements of the Building Regulations. | Home Ownership | David Ward |  | Letter before action sent by Legal. Door assessed by Carl Stokes, TMO Fire Consultant, on 8th Nov 2013 & confirmed as COMPLIANT.(Lessee given copy of report.) | 2013-11-09 | Fully Completed | David Ward | 2013-08-20 16:15 | 2013-09-10 16:16 | 2013-08-20 16:15 | 2014-01-08 14:15 | -21 | In target | 2013-08-20 16:15 | 2014-01-14 14:15 | Janice Wray
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:20 | S217002110008 | FINBOROUGH ROAD (62) | 102950 | Completed | 12g | High | Flat Door | The entrance door to flat 48 in not the originally fitted door. | Can it please be confirmed that this flat entrance door is a 30 minute fire rated door fitted with a self closing device etc and complying with all the requirements of the Building Regulations. | Home Ownership | David Ward |  | Letter before action sent by Legal. Invoice provided by lessee on 10th October 2013 confirming door is fire-rated & COMPLIANT. | 2013-10-01 | Fully Completed | David Ward | 2013-08-20 16:20 | 2013-09-10 16:22 | 2013-08-20 16:20 | 2014-01-03 10:36 | -21 | In target | 2013-08-20 16:20 | 2014-01-09 10:29 | Janice Wray
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:22 | S217002110008 | FINBOROUGH ROAD (62) | 102952 | Completed | 12h | Information Only | Flat Door | The following flat entrance doors are the original fire rated flat entrance doors, these are flush solid doors which appear to be fire rated. These are flats numbers 2, 3, 5, 7, 9, 10, 11, 13, 14, 24, 25, 26, 30, 31, 38, 39, 46, 51 and 52. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | David Ward |  | For future information only | 2013-10-10 | Fully Completed |  |  |  | 2013-08-20 16:22 | 2014-01-14 09:58 |  |  | 2013-08-20 16:22 | 2014-01-20 09:56 | Janice Wray
65 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-03-23 16:36 | S217008660001 | ELGIN CRESCENT 65 (1-8) | 250840 | Active | 12b1 | High | Flat Door | It is not known if a self closing devices are fitted to the flat entrance door of flats 6 - this is the original apartment entrance door. Leasehold | Flat entrance doors off internal protected areas should be fitted with self closing devices. I would recommend that leaseholders are asked to confirm that their flat entrance door is fitted with a self closing device and if not that they give an assurance that they will fit one as per LFB requirements. | Home Ownership | Samuel Anyanwu | 2016-04-20
65 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-03-23 16:56 | S217008660001 | ELGIN CRESCENT 65 (1-8) | 250861 | Active | 12b2 | High | Flat Door | It is not known if self closing device are fitted to the flat entrance door of flat 7 - this are the original apartment entrance door Leasehold | Flat entrance doors off internal protected areas should be fitted with self closing devices. I would recommend that leaseholders are asked to confirm that their flat entrance door is fitted with a self closing device and if not that they give an assurance that they will fit one as per LFB requirements. | Home Ownership | Samuel Anyanwu | 2016-04-20 |  |  |  | Cyril Morris | 2016-03-23 16:56 | 2016-04-13 16:57 |  |  | -6 | 6 days to target date
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:19 | S217001880003 | ELM PARK GARDENS (7) | 102453 | Completed | 12a | High | Flat Door | The flat entrance door to flat number 7 has been changed from the originally fitted and the presently fitted door has indented panels and no self closing device fitted to it. | Can it be confirmed the entrance door to flat 7 is a 30 minute fire rated door, if it is, a self closing device should be fitted to it. If it is not a fire rated door then this door must be replaced with a self closing 30 minute fire rated door. | Home Ownership | David Ward |  | Letter before action sent by Legal. Access provided on 5th December 2013 for Carl Stokes to assess - COMPLIANCE confirmed. (Lessee provided with copyof report.) | 2013-10-01 | Fully Completed | David Ward | 2013-08-19 12:19 | 2013-09-09 12:21 | 2013-08-19 12:19 | 2014-01-03 10:15 | -21 | In target | 2013-08-19 12:19 | 2014-01-09 10:08 | Janice Wray
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:45 | S217002110009 | FINBOROUGH ROAD (80) | 122180 | Completed |  | Information Only | Miscellaneous | I understand that Flat 1 is a leaseholder occupied flat, this flat appears to be empty, there is newspaper up the windows of the ground floor level rooms and old curtains hanging in strips from the lower ground floor level windows. | I would recommend that the housing officer/caretaker is asked to visit this flat and check if anybody is living here. | Home Ownership | Nazrul Islam |  |  | 2013-01-07 | Fully Completed |  |  |  | 2013-12-31 14:45 | 2014-01-08 16:03 |  |  | 2013-12-31 14:45 | 2014-01-14 16:02 | Janice Wray
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:54 | S217002110009 | FINBOROUGH ROAD (80) | 122189 | Completed | 12 | Medium | Flat Door | The flap is missing from the letter box of flat 1 and the letter box is damaged, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that a new letter box and flap is fitted to the flat entrance door of flat 1 so that the compartmentation of the protected staircase is maintained | Home Ownership | Nazrul Islam |  | Hi Nazrul Just to advise that this door was assessed by Carl Stokes, the TMO's Fire Risk Assessor, on 31st Oct 2013 & confirmed as COMPLIANT. Could you please complete the workflow & send back to H&S Thanks Janice Janice Wray TMO Health, Safety & Facilities Manager t: [REDACTED] w: www.kctmo.org.uk a: : The Network Hub, 300 Kensal Road, W10 5BE P Before printing, please think about the environment | 2014-01-10 | Fully Completed | Nazrul Islam | 2013-12-31 14:54 | 2014-03-01 14:55 | 2013-12-31 14:54 | 2014-01-13 14:33 | -60 | In target | 2013-12-31 14:54 | 2014-01-14 15:58 | Nazrul Islam
80 LOTS ROAD - 2015.11.25 | 2015-12-14 16:43 | S217003270009 | LOTS ROAD (80) | 233113 | Active | 12 | High | Flat Door | The flat entrance door of flat A has been changed in the last 2 to 3 years I am told. (Not raised in previous FRA - Oct 2011) | Can it be confirmed that this flat entrance door is a self closing 30 minute fire rated door (FD30) fitted with intumescent strips and cold smoke seals and complying with all the requirements of the Building Regulations. | Home Ownership | Nazrul Islam | 2016-02-08 | lessee written to 8.2.16 | 2016-02-08 | Partially Completed | David Ward | 2015-12-14 16:43 | 2016-01-04 16:46 |  |  | 93 | 93 days overdue
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 10:50 | S217002110010 | FINBOROUGH ROAD (82) | 239726 | Active | 12 | High | Flat Door | The flat entrance doors of flats 1 have been changed I am told in the last 3 to 4 years. Not raised on previous FRA - Nov 2011 | Can it be confirmed that these two flat entrance doors are self closing 30 minute fire rated doors (FD30s) fitted with intumescent strips and cold smoke seals and complying with all the requirements of the Building Regulations. | Home Ownership | David Ward | 2016-02-25 | lessee written to 8.2.16 | 2016-02-08 | Partially Completed | David Ward | 2016-01-27 10:50 | 2016-02-17 10:56 |  |  | 49 | 49 days overdue
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 15:29 | S217002110010 | FINBOROUGH ROAD (82) | 239862 | Active | 12(2) | High | Flat Door | The flat entrance door of3 has been changed I am told in the last 3 to 4 years. Not raised on previous FRA - Nov 2011 | Can it be confirmed that this flat entrance door is self closing 30 minute fire rated door (FD30s) fitted with intumescent strips and cold smoke seals and complying with all the requirements of the Building Regulations. | Home Ownership | David Ward | 2016-02-25 | Emailed lessee 8.2.16 | 2016-02-08 | Partially Completed | David Ward | 2016-01-27 15:29 | 2016-02-17 15:31 |  |  | 49 | 49 days overdue
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:01 | S217010567703 | LONGLANDS COURT (82-87) | 103426 | Completed | 12a | High | Flat Door | The entrance door to flat 83 has been changed from the originally fitted door. | Can it be confirmed that this flats entrance door is a 30 minute fire rated door fitted with a self closing device capable of shutting the door fully on to its stops. | Home Ownership | Jannie Pretorius |  | 28082013 - Following letter forwarded to leaseholder of 83 Longlands Court: Further to our letter of the 11th October 2012 in respect of the fire rating of leasehold front doors I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review of Longlands Court. As a result of this review, it has come to light that your front entrance door may not be a FD30 compliant door. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] . Door assessed by C Stokes on 17th October 2013 & confirmed as COMPLIANT. (Lessee given copy of report.) | 2013-08-28 | Fully Completed | Jannie Pretorius | 2013-08-23 10:01 | 2013-09-13 10:03 | 2013-08-23 10:01 | 2014-01-03 10:58 | -21 | In target | 2013-08-23 10:01 | 2014-01-09 10:57 | Janice Wray
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:22 | S217010567703 | LONGLANDS COURT (82-87) | 103438 | Completed | 12b | Information Only | Flat Door | The flat entrance doors to flats 82, 84 and 85 are the originally fitted ones. These original flat entrance doors are solid close fitting doors which appear to be fire rated but do not have self closing devices fitted to them. When this building was constructed and these doors fitted it was not a requirement of the Building Regulations to have self closing devises fitted to the flat entrance doors of low rise blocks of purpose built flats. | If any of the original flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | Jannie Pretorius |  |  | 2013-08-29 | Fully Completed |  |  |  | 2013-08-23 10:22 | 2014-01-08 15:22 |  |  | 2013-08-23 10:22 | 2014-01-14 15:21 | Janice Wray
83 PRINCEDALE ROAD - 2014.03.17 | 2014-03-20 15:27 | S217009770001 | PRINCEDALE ROAD (83) | 135648 | Completed | 12 | High | Flat Door | The entrance door to flat A has been changed from the originally fitted door. | Can it be confirmed the entrance door to flat A is a 30 minute fire rated door, u | Home Ownership | Jannie Pretorius |  | Email sent to leaseholders 19/6/14, follow up letter sent 20/11/14. Email received from leaseholder confirming the door has been changed | 2015-05-07 | Fully Completed | David Ward | 2014-03-20 15:27 | 2014-04-10 15:30 | 2014-03-20 15:27 | 2015-05-08 15:47 | -21 | In target | 2014-03-20 15:27 | 2015-05-03 16:05 | David Ward
88 AND 90 BRAMLEY ROAD - 2015.09.29 | 2015-10-05 15:46 | S217008220001 | BRAMLEY ROAD (86-90) | 220093 | Active | 12b | High | Flat Door | The entrance door to flat 90 has a low level transfer grille/vent in it and it is not known if an intumescent block is installed within this hole in the door or the door has a self closing device is fitted to it. This flat is presently empty and may be in the process of being sold. | Can it be confirmed the vent in this flat's entrance door has an intumescent block in it and that a self closing device is fitted to this door. If there is no intumescent block fitted I would recommend that a new self closing 30 minute fire rated door is fitted, complying with all the requirements of the Building regulations. | Home Ownership | Samuel Anyanwu |  | emailed lessee 23.11.15 | 2015-11-23 | Partially Completed | David Ward | 2015-10-05 15:46 | 2015-10-26 15:48 |  |  | 163 | 163 days overdue
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:29 | S217010567704 | LONGLANDS COURT (88-93) | 103439 | Completed | 12b | Information Only | Flat Door | The flat entrance door to flats 91 is the original fitted door. The original flat entrance doors are solid close fitting doors which appear to be fire rated but do not have self closing devices fitted to them. When this building was constructed and these doors fitted it was not a requirement of the Building Regulations to have self closing devises fitted to the flat entrance doors of low rise blocks of purpose built flats. | If any of the original flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | Jannie Pretorius |  |  | 2013-08-29 | Fully Completed |  |  |  | 2013-08-23 10:29 | 2014-01-08 15:20 |  |  | 2013-08-23 10:29 | 2014-01-14 15:19 | Janice Wray
9, 10 AND 11 RADDINGTON ROAD, LONDON W10 5TG - 2015.12.22 | 2016-02-08 12:20 | S217009860005 | RADDINGTON ROAD | 241874 | Active | 12a | High | Flat Door | The Georgian wired fire rated glass in the vision panel of flat 10F's entrance door has been replaced with a piece of boarding, this boarding is not fire rated. | A piece of fire rated glazing correctly fitted should be reinserted into the vision panel area of this flat entrance door. Alternatively a new self closing 30 minute fire rated doors fitted with intumescent strips and cold smoke seals, (FD30s) could be fitted. Complying with all the requirements of the Building Regulations and with copies of the fire door certification forwarded on to the TMO. Leasehold flat | Home Ownership | Samuel Anyanwu | 2014-03-03 |  |  |  | Cyril Morris | 2016-02-08 12:20 | 2016-02-29 12:26 |  |  | 37 | 37 days overdue
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 14:51 | S217009120002 | LADBROKE GROVE (94) | 101761 | Completed | 12a | High | Flat Door | The entrance door to flat 3 is a double door set, this configuration has been changed from the door and screen which I believe was originally fitted. | Can it be confirmed this flats double door entrance doors are 30 minute fire rated doors fitted with a self closing devices capable of shutting the door fully on to its stops. Could the occupant please explain how this door set works ? ie is one door fixed locked shut and one used only ? | Home Ownership | Nazrul Islam | 2013-09-04 | From: Nazrul Islam Sent: 23 August 2013 11:16 To: [REDACTED] Subject: 3/94 Ladbroke Grove - FRA Re: Front Door - FRA Review Dear [REDACTED] Further to our letter of the 11th October 2012 in respect of the fire rating of leasehold front doors I write to inform you that as part of our on-going commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review of 94 Ladbroke Grove on 1st July 2013. The entrance door to flat 3 is a double door set, this configuration has been changed from the door and screen which the Consultant believe was originally fitted. As a result of this review, it has come to light that your front entrance door may not be a FD30 compliant door. I must therefore request the following: " Confirmation as to whether your double door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " Could the occupant please explain how this door set works? I.e. is one door fixed locked shut and one used only? " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] Mr Nazrul Islam Home Ownership Officer t: [REDACTED] w: www.kctmo.org.uk a: Network Hub, 292a Kensal Road,London W10 5BE Assessed by Sarl Stokes, Fire risk assessor & door COMPLIANT. | 2013-08-23 | Fully Completed | Nazrul Islam | 2013-08-14 14:51 | 2013-09-04 14:55 | 2013-08-14 14:51 | 2014-01-28 11:08 | -21 | In target | 2013-08-14 14:51 | 2013-09-12 11:36 | Janice Wray
96 - 98 BLENHEIM CRESCENT - 2015.06.16 | 2015-06-26 12:36 | S217008160001 | BLENHEIM CRESCENT (96) | 203586 | Active | 12a | High | Flat Door | The flat entrance door if flat F of number 96 has been changed from the original fire rated door. | I would recommend that this flat's entrance door is checked to see if it is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s) If it is not then it should be replaced with FD 30s door complying with all the requirements of the Building Regulations. | Home Ownership | Nazrul Islam | 2015-07-10 | ltr sent 10/7/15. [REDACTED] 99 Blenheim Crescent London e-mail: nislam@kctmo.org.uk W11 2EQ Date: 10th July 2015 Our Reference Your Reference Please Contact TMO/LHS/NI/ Flat F, 96 Blenheim Crescent Nazrul Islam Re: Front Door - FRA Review Dear [REDACTED] I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review. It is reported the flat entrance door of flat F of number 96 has been changed from the original fire rated door. TMO's Fire Risk Assessor recommended that this flat's entrance door is checked to see if it is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s). If it is not then it should be replaced with FD 30s door complying with all the requirements of the Building Regulations. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] Regards Nazrul Islam Home Ownership Officer | 2015-07-10 | Partially Completed | Nazrul Islam | 2015-06-26 12:36 | 2015-07-17 12:37 | 2015-06-26 12:36 | 2015-07-13 12:11 | -21 | In target | 2015-06-26 12:36 | 2015-08-04 15:45 | David Ward
96 - 98 BLENHEIM CRESCENT - 2015.06.16 | 2015-06-26 12:38 | S217008160001 | BLENHEIM CRESCENT (96) | 203587 | Active | 12b | High | Flat Door | There is clear glazing in the transom light area above the entrance door of flat F of number 96, instead of Georgian wired fire rated glazing. This clear glass does not appear to be marked as fire rated glazing. | This glazed transom light should be checked to ascertain if it is fire rated glazing or the occupier could produce documentation stating that it fire rated glazing. If it is not fire rated glazing it should be replaced with a suitable fire rated material so that the integrity of the protected corridor is maintained. l | Home Ownership | Nazrul Islam |  |  | 2015-07-10 | Fully Completed | Nazrul Islam | 2015-06-26 12:38 | 2015-07-17 12:53 | 2015-06-26 12:38 | 2015-07-31 15:42 | -21 | In target
ADELAIDE HOUSE - 2015.02.26 | 2015-03-27 08:32 | S217012270004 | ADELAIDE HOUSE | 190112 | Completed | 12b | High | Flat Door | Flat entrance door of Flat 8 (leaseholder) has been changed from the originally fitted flat entrance door. | Can the leaseholder be asked to provide documentation to confirm that door is fire-rated and self-closing. | Home Ownership | Earle Harriott |  | Letter sent to leaseholder today, regarding the Front Entrance Flat door/ FRA Review. copy on file Follow up 7 day letter sent 16/4/15. Assessed by C Stokes who has confirmed that this is at least "nominally fire rated" & therefore COMPLIANT | 2015-10-02 | Fully Completed | Earle Harriott | 2015-03-27 08:32 | 2015-04-17 08:33 | 2015-03-27 08:32 | 2015-10-07 16:42 | -21 | In target | 2015-03-27 08:32 | 2015-08-04 17:08 | Janice Wray
AGNES HOUSE - 2014.08.14 | 2014-08-20 10:45 | S217010050010 | AGNES HOUSE | 158165 | Active | 12a | High | Flat Door | The flat entrance doors to flats 2 and 5 have all been changed from the originally fitted fire rated flat entrance doors. These newly fitted flat entrance doors all have clear glass in them and these may not be fire rated doors. (Leaseholders) | I would recommend that the leaseholders of these two flats are asked to provide documentation showing that their flat entrance doors are 30 minute fire rated doors, fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? | Home Ownership | Earle Harriott | 2014-08-21 | Letter sent to leaseholder outlining the building regulation for front entrance flat doors and comply with requirements listed. Follow up 7 day letter sent 20/11/14. Door of flat 2 assessed by Carl Stokes in Dec 2014 (with lessee in attendance) and found to be NON-COMPLIANT. Report provided to Home Ownership | 2015-07-28 | Partially Completed | Earle Harriott | 2014-08-20 10:45 | 2014-09-10 10:46 | 2014-08-20 10:45 | 2015-11-16 18:39 | -21 | In target | 2014-08-20 10:45 | 2015-11-18 10:28 | Janice Wray
ANCHOR HOUSE -2015.02.28 | 2015-02-03 11:06 | S217012760008 | ANCHOR HOUSE | 181538 | Completed | 12 | High | Flat Door | The Georgian wired fire rated glazed vision panel in flat 2's entrance door appears to have been replaced with a frosted piece of glass. You can see where the beading around the vision panel has been removed. | Can it please be confirmed that the glazing in flats 2's entrance doors vision panel is fire rated glazing? If it is not the currently installed glazing should be removed and fire rated glazing correctly installed or a new 30 minute self closing fire rated door should be fitted, complying with all of the requirements of the Building Regulations. David Ward | Home Ownership | David Ward |  | works approved in 13/14 but no reference to the replacement window in the front door. Queried with the leaseholder and membership promoted. Leaseholder has confimred that the glass is compliant and this has been relayed to H&S. A copy of the confirmation is indexed against the tenancy on W2. | 2015-03-26 | Fully Completed | David Ward | 2015-02-03 11:06 | 2015-02-24 11:07 | 2015-02-03 11:06 | 2015-03-27 14:08 | -21 | In target | 2015-02-03 11:06 | 2015-04-02 12:44 | David Ward
ARCHER HOUSE - 2015.02.26 | 2015-03-27 11:36 | S217012270001 | ARCHER HOUSE | 190173 | Active | 12 | High | Flat Door | The flat entrance door of flat 6 (lessee) does not appear to be a 30 minute fire rated door. This flat entrance door is different to the other flat entrance doors in this building. | Can the leaseholder please be asked to provide confirmation & documentation that the entrance door is a 30 minute fire rated door, fitted with a self closing device? | Home Ownership | Earle Harriott |  | Letter sent today to leaseholder regarding Front Entrance Flat door/ FRA Review 30/3/15 and email sent 6/8/15 door confirmed as compliant and report available from H&S | 2015-10-08 | Fully Completed | Earle Harriott | 2015-03-27 11:36 | 2015-04-17 11:37 | 2015-03-27 11:36 | 2015-10-09 14:13 | -21 | In target | 2015-03-27 11:36 | 2015-10-16 13:03 | David Ward
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:47 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101959 | Completed | 12a (leasehold door) | High | Flat Door | The entrance door to flat 35 has been changed after this flat entrance door was damaged in an incident. The TMO are aware and a temporary entrance door was installed until new replacement door could be fitted. This temporary flat entrance door is not fire rated and does not have a self closing device fitted. | I would recommend that this temporary flat entrance door is replaced immediately with self closing certified 30 minute fire rated door complying with all the requirements of the Building Regulations. | Home Ownership | David Ward | 2013-09-05 | Letter before action sent by Legal. Access provided on 17th December 2013 for Carl Stokes to assess door. Consultant has comfirmed in writing that this door is COMPLIANT. Lessee informed. Jancie Wray 2/1/2014 | 2013-10-01 | Fully Completed | David Ward | 2013-08-15 11:47 | 2013-09-05 11:59 | 2013-08-15 11:47 | 2014-01-03 09:17 | -21 | In target | 2013-08-15 11:47 | 2014-01-09 09:02 | Janice Wray
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 12:00 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101972 | Completed | 12b | High | Flat Door | The entrance door to flat 33 has been changed from the originally fitted door and the glazing in this door appears not to be fire rated. | Can it be confirmed that this flat entrance door is a fire rated door? If it is not it should be replaced with a fire rated door complying to the requirements of the Building Regulations. | Home Ownership | David Ward | 2013-09-05 | Letter before action sent by Legal and further correspondence with Notting Hill Housing Trust who have now agreed to replace door with one of approved specification. Installation date of 15th April 2014 | 2014-04-10 | Fully Completed | David Ward | 2013-08-15 12:00 | 2013-09-05 12:05 | 2013-08-15 12:00 | 2014-04-11 11:47 | -21 | In target | 2013-08-15 12:00 | 2014-04-17 11:37 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:34 | S217012740002 | BERENGER TOWER 1-51 | 102377 | Completed | 12a | High | Flat Door | The entrance door to flat number 22 has been changed from the originally fitted door and the fire rated glazed side screen replaced with a screen that has an openable window in it. | The side screen next to this flat entrance door should be replaced with a fire rated one with no openings in it and can it be confirmed the entrance door to this flat is fire rated? | Home Ownership | David Ward | 2013-09-09 | Letter before action sent by Legal. [REDACTED] has given an undertaking to comply with our Fire Risk Assessors request that the 2 openable glazing blocks in the side screen adjacent to his front door need to be sealed shut | 2014-04-09 | Fully Completed | David Ward | 2013-08-19 09:34 | 2013-09-09 09:38 | 2013-08-19 09:34 | 2014-04-11 11:36 | -21 | In target | 2013-08-19 09:34 | 2014-04-17 11:34 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:38 | S217012740002 | BERENGER TOWER 1-51 | 102380 | Completed | 12b | High | Flat Door | The entrance door to flat number 32 has been changed from the originally fitted door and now has no fire rated at all and the fire rated glazed side screen has been replaced with a screen that is not fire rated. | This flat entrance door and the side screen next to it should be replaced with a fire rated door and side screen. | Home Ownership | David Ward | 2013-09-09 | Letter before action sent by Legal. Fire-rated supalux boarding installed on door and sidescreen - photos & invoice submitted - now COMPLIANT. | 2014-02-12 | Fully Completed | David Ward | 2013-08-19 09:38 | 2013-09-09 09:40 | 2013-08-19 09:38 | 2014-02-18 16:32 | -21 | In target | 2013-08-19 09:38 | 2014-02-24 16:30 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:41 | S217012740002 | BERENGER TOWER 1-51 | 102381 | Completed | 12c | High | Flat Door | The entrance door to flat number 40 and the side screen has been replaced with one large door. | Can it be confirmed this flat entrance door is fire rated? | Home Ownership | David Ward | 2013-09-09 | Letter before action sent by Legal Door assessed by C Stokes on 8th Oct 2013 & COMPLIANCE confirmed. | 2013-10-09 | Fully Completed | David Ward | 2013-08-19 09:41 | 2013-09-09 09:42 | 2013-08-19 09:41 | 2014-01-08 14:56 | -21 | In target | 2013-08-19 09:41 | 2014-01-14 14:54 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:43 | S217012740002 | BERENGER TOWER 1-51 | 102383 | Completed | 12d | High | Flat Door | The entrance doors to flat numbers 25, 47 and 50 have been changed from the originally fitted doors. | Can it be confirmed that these flat entrance doors are fire rated doors? | Home Ownership | David Ward | 2013-09-09 | CS assessed 25 & 47 & 50 - COMPLIANCE confirmed. | 2013-10-30 | Fully Completed | Janice Wray | 2013-08-19 09:43 | 2013-09-09 09:44 | 2013-08-19 09:43 | 2014-01-08 14:34 | -21 | In target | 2013-08-19 09:43 | 2014-01-14 14:31 | Janice Wray
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:26 | S217012740014 | BLANTYRE TOWER 1-65 | 102166 | Completed | 12a | High | Flat Door | The entrance door to flat 42 has been changed from the originally fitted door. | Can it be confirmed that thisreplacement flat entrance door is a fire rated door fitted with a self closing device? If this door is not a fire rated door it should be replaced with a fire rated door complying to the requirements of the Building Regulations. | Home Ownership | David Ward | 2013-09-06 | Inspected & assessed by C Stokes, Fire Consultant, on 13th jan 2014 & confirmed as COMPLIANT | 2014-01-14 | Fully Completed | David Ward | 2013-08-16 07:26 | 2013-09-06 07:29 | 2013-08-16 07:26 | 2014-01-15 13:07 | -21 | In target | 2013-08-16 07:26 | 2014-01-21 13:06 | Janice Wray
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 12:38 | S217012740014 | BLANTYRE TOWER 1-65 | 102249 | Completed | 12c | Information Only | Flat Door | The entrance doors to flats 5, 41, 60 and 61 have been changed or altered from the originally fitted doors, these doors have been checked and they appear to be fire rated doors. | No action is needed on this issue. | Home Ownership | David Ward |  |  | 2013-10-10 | Fully Completed |  |  |  | 2013-08-16 12:38 | 2014-01-14 10:01 |  |  | 2013-08-16 12:38 | 2014-01-20 10:01 | Janice Wray
BOWLING GREEN HOUSE, APOLLO PLACE, LONDON SW10 0DN - 2015.1.6 | 2015-01-30 13:28 | S217012760011 | BOWLING GREEN HOUSE | 181067 | Completed | 12 | High | Flat Door | The flat entrance door of flat 7 has been changed from the original fire rated one and the presently fitted door does not appear to be a fire rated door. | I would recommend that this flat entrance door is checked to see if it is a 30 minute fire rated door (FD 30). If it is not then it should be replaced with FD 30 door complying with the requirements of the Building Regulations. | Home Ownership | David Ward |  | Property leased to NHHG and used by RBKC for TA. Emailed Notting Hill in the first instance. | 2015-03-19 | Fully Completed | David Ward | 2015-01-30 13:28 | 2015-02-20 13:29 | 2015-01-30 13:28 | 2015-03-20 16:07 | -21 | In target
BURLEIGH HOUSE, BEAUFORT STREET, LONDON SW3 5BE - 2016.02.11 | 2016-04-04 15:43 | S217000310002 | BURLEIGH HOUSE BEAUFORT STREET | 252385 | Active | 12a | High | Flat Door | The entrance door to flat number 9 appears to have been changed from the originally fitted door. LEASEHOLD | Can it be confirmed this flat entrance door is a 30 minute fire rated door and fitted with a self closing device capable of shutting the door fully on to its stops. | Home Ownership | Nazrul Islam | 2016-05-09
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:27 | S217011760004 | CAMELFORD WALK LOWER 10-19 & UPPR 21-40 | 134505 | Completed |  | Information Only | Miscellaneous | There has recently been refurbishment/ construction work undertaken within flat 33 of this building. | Can it be confirmed that the TMO knows about the refurbishment/construction work which has been undertaken within flat 33. The work involved a new kitchen and bathroom being installed and a complete electrical rewiring I am told. A Building Regulations completion certificates should be asked for from the occupant and this flat and should be kept with the buildings file for future reference. Any fire detection installed within the flat should be to BS 5839 Part 6 2004. | Home Ownership | Jannie Pretorius |  | I have written to the leaseholder requesting further information on alterations carried out at flat and advised that permission is required before carrying out any alterations. | 2014-03-20 | Fully Completed |  |  |  | 2014-03-13 15:27 | 2014-04-07 15:29 |  |  | 2014-03-13 15:27 | 2014-03-27 13:41 | David Ward
CHELSEA MANOR COURT FLATS 27 TO 76 - 2015.07.07 | 2015-09-01 09:40 | S217000830004 | CHELSEA MANOR COURT 27-54 | 214223 | Active | 12a | High | Flat Door | The original Georgian wired fire rated glazing in the vision panel of flat 34's entrance door has been changed to a clear piece of glass which is not marked as fire rated glazing. | I would recommend that the occupant of this flat is asked if the clear glass in the flat doors vision panel is fire rated glazing. If it is not then a new piece of fire rated glazing should be fitted into this vision panel area. If the occupant provides documentation stating that the glazing is fire rated then no action is needed. | Home Ownership | Nazrul Islam |  | emailed [REDACTED] 11.11.15 | 2015-11-11 | Partially Completed | David Ward | 2015-09-01 09:40 | 2015-09-22 09:41 | 2015-09-01 09:40 | 2015-11-12 10:58 | -21 | In target | 2015-09-01 09:40 | 2015-11-20 18:38 | David Ward
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:27 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102335 | Completed | 12a | High | Flat Door | The entrance doors to flats 9, 41 and 49 have been changed from the originally fitted doors. | Can it be confirmed these flat entrance doors are 30 minute fire rated doors, each fitted with a self closing device, capable of shutting the door fully on to its stops. | Home Ownership | David Ward | 2013-09-06 | Flat 49 assessed by C Stokes on 3/10/2013 & COMPLIANCE confirmed. Flat 9 assessed as non-compliant on 24th Oct 2013 but confirmation of upgrading of door (photos, receipt etc..) to reach compliant standard provided in Dec 2013 so door now COMPLIANT. Flat 41 assessed on 10th Oct 2013 - NON-COMPLIANT. Lessee has given committment to upgrade & confiorm but not yet received - 2nd Jan 2014. Door now replaced - COMPLIANT. 1st May 2014 | 2014-05-01 | Fully Completed | Janice Wray | 2013-08-16 16:27 | 2013-09-06 16:29 | 2013-08-16 16:27 | 2014-05-06 07:33 | -21 | In target | 2013-08-16 16:27 | 2014-05-10 07:32 | Janice Wray
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:36 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102338 | Completed | 12b | High | Flat Door | The entrance door to flat 22 has been changed from the originally fitted door and a vent has been inserted in the boarded over side screen of the door set, which is now not fire rated. | Can it be confirmed that this flat entrance door is a fire rated door? If it is not it should be replaced with a fire rated door complying to the requirements of the Building Regulations. The side screen area should be reinstated back to its original fire rated standard or the whole door set replaced with a suitably fire rated one. | Home Ownership | David Ward | 2013-09-06 | Letter before action sent by Legal. Door assessed by Carl Stokes on 10th Oct 2013 & confirmed as COMPLIANT. | 2013-10-11 | Fully Completed | David Ward | 2013-08-16 16:36 | 2013-09-06 16:39 | 2013-08-16 16:36 | 2014-01-08 14:39 | -21 | In target | 2013-08-16 16:36 | 2014-01-14 14:37 | Janice Wray
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:44 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102340 | Completed | 12d | High | Flat Door | It appears that the entrance door and side screen to flat 35 have been changed from the originally fitted ones. | Can it be confirmed that this flats entrance door and the side screen are fire rated? If they are not they should be replaced with complete fire rated door set complying to the requirements of the Building Regulations. | Home Ownership | David Ward | 2013-09-06 | Letter before action sent by Legal Door assessed by C Stokes on 3rd Oct 2013 & confirmed as COMPLIANT. | 2013-10-04 | Fully Completed | David Ward | 2013-08-16 16:44 | 2013-09-06 16:46 | 2013-08-16 16:44 | 2014-01-08 14:59 | -21 | In target | 2013-08-16 16:44 | 2014-01-14 14:58 | Janice Wray
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 09:49 | S217010050003 | COPPERFIELD HOUSE | 157985 | Completed | 12a | High | Flat Door | The flat entrance door to flat 12 has been changed from the originally fitted door. | Can it be confirmed that the entrance door to flat 12 is a 30 minute fire rated door, fitted with a self closing device capable of shutting the door fully on to its stops. | Home Ownership | Earle Harriott | 2015-09-07 | Letter sent to leaseholder dated 19 August 2014. Follow up letter sent 20/11/14. Further follow up sent on 6/8/15 Assessed by C Stokes & considers as a minimum this is "nominally fire rated" and therefore COMPLIANT | 2015-10-02 | Fully Completed | Earle Harriott | 2014-08-19 09:49 | 2014-09-09 09:52 | 2014-08-19 09:49 | 2015-10-07 16:40 | -21 | In target | 2014-08-19 09:49 | 2015-08-04 19:46 | Janice Wray
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:10 | S217012740006 | DARTREY TOWER 1-49 | 102939 | Completed | 12a | High | Flat Door | The entrance doors to flats 9 and 23 have been changed from the originally fitted doors. | Can it be confirmed the entrance doors these flats are fire rated doors and that the side screens are also still fire rated? | Home Ownership | David Ward | 2013-09-10 | Letter before action sent by Legal. Flat 9 assessed 3rd Oct 2013 & assessor confirms COMPLIANT. Flat 23 assessed on 3rd Oct 2013 & confirmed by Carl Stokes as NON-COMPLIANT - lessee given copy of report. Replacement door fitted & CS inspected & confirmed COMPLIANT 6th Feb 2014 | 2014-02-10 | Fully Completed | David Ward | 2013-08-20 16:10 | 2013-09-10 16:12 | 2013-08-20 16:10 | 2014-02-11 12:18 | -21 | In target | 2013-08-20 16:10 | 2014-02-17 12:17 | Janice Wray
DENBIGH HOUSE -2015.02.26 | 2015-03-26 12:59 | S217012270003 | DENBIGH HOUSE | 189960 | Completed | 12a | High | Flat Door | The flat entrance door to flats 6 does not appear to be a 30 minute fire rated doors. This flat entrance door is different to the other flat entrance doors in this building. | Can the leaseholder please provide confirmation (& supporting documentation) that this door is 30 minute fire-rated and self-closing | Home Ownership | Earle Harriott |  | letter sent 26/3/15 and follow up email sent 6/8/15 Carl has confirmed that the door is complaint and H&S in receipt of his report 25/8/14 | 2015-10-08 | Fully Completed | Earle Harriott | 2015-03-26 12:59 | 2015-04-16 13:01 | 2015-03-26 12:59 | 2015-10-09 14:12 | -21 | In target | 2015-03-26 12:59 | 2015-08-04 20:05 | David Ward
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:02 | S217012270003 | DENBIGH HOUSE | 189964 | Completed | 12c | High | Flat Door | The flat entrance door to flat 10 does not appear to be a 30 minute fire-rated door - different to other doors in building. | Can the leaseholder please provide confirmation (& supporting documentation) that this door is 30 minute fire-rated and self-closing | Home Ownership | Earle Harriott |  | letter and email sent the 26/3/15 Further email sent on 6/8/15 Response from leaseholder in March and again on 6/8/15 advising that they have sold the property now whilst adding that it has not been changed since they purchased in 2008. Referred back to H&S Assessed by C STokes as a least nominally fire-rated - COMPLIANT. (Letter on file) | 2015-10-05 | Fully Completed | Earle Harriott | 2015-03-26 13:02 | 2015-04-16 13:05 | 2015-03-26 13:02 | 2015-10-07 12:48 | -21 | In target | 2015-03-26 13:02 | 2015-10-13 12:47 | Janice Wray
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:07 | S217012270003 | DENBIGH HOUSE | 189968 | Active | 12e | High | Flat Door | The flat entrance door to flat 15 does not appear to be a 30 minute fire-rated door - different to other doors in building.. | Can the leaseholder please provide confirmation (& supporting documentation) that this door is 30 minute fire-rated and self-closing | Home Ownership | Earle Harriott |  | letter sent 26/3/15 and again on 6/8/15 |  | Partially Completed | Earle Harriott | 2015-03-26 13:07 | 2015-04-16 13:08 | 2015-03-26 13:07 | 2015-03-27 16:37 | -21 | In target | 2015-03-26 13:07 | 2015-08-04 20:04 | David Ward
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:25 | S217008560001 | DIXON HOUSE | 244894 | Active | 12b | High | Flat Door | The flat entrance door of flat 42 was replaced in 2013 I am told. This appears to be a temporary type door. LEASEHOLDER | Can it please be confirmed that this is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations. If it is not then a self closing FD30s door must be fitted. | Home Ownership | Samuel Anyanwu | 2016-03-22
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:34 | S217010050009 | ESTELLA HOUSE | 158195 | Completed | 12c | High | Flat Door | The flat entrance door to flat 18 has been changed from the original door, this new door has Georgian wired glazing in it and a canopy has been fitted over this flat entrance door. (Leaseholder) | I would recommend that the leaseholder of this flat is asked to provide documentation showing that this door is a 30 minute fire rated door, fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? I would also recommend that the occupier is asked to provide documentation showing that the canopy over this flat entrance door is fire rated. | Home Ownership | Earle Harriott | 2014-08-21 | Letter sent to leaseholder outlining the building regulation for front entrance flat doors and comply with requirements listed in letter. Follow up 7 day letter sent 20/11/14. Email sent to Notting Hill regarding prevoius letters given a futher 7 day to comply or passed back to heath & safety team to enforce legal action Further email sent to NHHG 7.5.15 Appointment arranged between NHHG and Carl Stokes for 27.7.15 to check compliance and review canopy. C Stokes & NHHG have assessed & confirmed this is a nominally fire-rated door with georgian-wired glazing and as such is COMPLIANT. (Self-closer recommended & NHHG have agreed to fit.) | 2015-07-28 | Fully Completed | Earle Harriott | 2014-08-20 11:34 | 2014-09-10 11:35 | 2014-08-20 11:34 | 2015-07-29 14:22 | -21 | In target | 2014-08-20 11:34 | 2015-08-04 14:13 | Janice Wray
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-23 16:45 | S217008740001 | FRINSTEAD HOUSE | 245328 | Active | 12b | High | Flat Door | The flat entrance door of flat 64 has a padlock on the door at high level and the upper two panels of this "Manse" door are covered over with black masking tape. Also door not self-closing LEASEHOLD | This flat entrance door should be checked to see that this door is still a 30 minute fire rated door and that it is fitted with a self closing device. (FD30). If it is not then it should be replaced with a new 30 minute fire rated door fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations. | Home Ownership | Samuel Anyanwu | 2016-03-22
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 09:50 | S217008740001 | FRINSTEAD HOUSE | 245388 | Active | 12d2 | High | Flat Door | Whilst undertaking the fire risk assessment it was noted that the original apartment entrance door of flat 74 is not fitted with a self closing device. LEASEHOLD FLAT | Flat entrance doors off internal protected areas should be fitted with self closing devices, I would recommend that self closing devices are fitted to these flat entrance doors | Home Ownership | Samuel Anyanwu | 2016-03-23 |  |  |  | Cyril Morris | 2016-02-24 09:50 | 2016-03-16 09:51 |  |  | 21 | 21 days overdue
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:36 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172176 | Completed | 12i | Information Only | Flat Door | The following flat entrance doors are the original fire rated flat entrance doors and which were fitted with a self closing device. These are flush solid doors and are all close fitting. These flats are numbers 56, 61, 86, 92, 112, 142, 154, 156, 165,166, 174.185, 195, and 206. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. For information only - please fully complete | Home Ownership | David Ward |  | None | 2014-12-08 | Fully Completed | David Ward | 2014-12-01 10:36 | 2014-12-22 10:42 | 2014-12-01 10:36 | 2014-12-09 16:27 | -21 | In target
HORTENSIA HOUSE, FLATS 9 - 48 - 2015.06.15 | 2015-06-26 14:58 | S217002700004 | HORTENSIA HOUSE (9-48) | 203634 | Active | 12a | High | Flat Door | The flat entrance doors of flats 45 and 46 have been changed from the originally fitted flat entrance doors. | Can it please be confirmed the entrance door to flats 45 and 46 are self closing 30 minute fire rated doors, if they are not they should be replaced with 30 minute fire rated doors complying with the requirements of the Building Regulations fitted with a self closing devices capable of shutting the doors fully on to their stops. | Home Ownership | Nazrul Islam | 2015-07-10 | [REDACTED] 45 Hortensia House Hortensia Road e-mail: nislam@kctmo.org.uk London SW10 0HD Date: 10th July 2015 Our Reference Your Reference Please Contact TMO/LHS/NI/ Nazrul Islam Re: Front Door - FRA Review Dear [REDACTED] I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review. It is reported the flat entrance door of flat 45 has been changed from the original fire rated door. TMO's Fire Risk Assessor recommended that this flat's entrance door is checked to see if it is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s). If it is not then it should be replaced with FD30s door complying with all the requirements of the Building Regulations. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] Regards Nazrul Islam Home Ownership Officer |  | Partially Completed | Nazrul Islam | 2015-06-26 14:58 | 2015-07-17 15:00 | 2015-06-26 14:58 | 2015-07-13 15:13 | -21 | In target | 2015-06-26 14:58 | 2015-08-04 15:36 | David Ward
KINGSLEY HOUSE, BEAUFORT STREET, LONDON SW3 5BD - 2016.02.11 | 2016-04-04 14:46 | S217000310001 | KINGSLEY HOUSE | 252356 | Active | 12a | High | Flat Door | The entrance door to flat number 22 has been changed from the originally fitted door, this is now a 6 indented panel door. LEASEHOLD | Can it be confirmed this flat entrance door is a self closing 30 minute fire rated door and fitted with intumescent strips and cold smoke seals? With the self closing device capable of shutting the door fully on to its stops. | Home Ownership | Nazrul Islam | 2016-05-09 |  |  |  | Cyril Morris | 2016-04-04 14:46 | 2016-04-25 14:48 |  |  | -18 | 18 days to target date
LACLAND HOUSE, MILMAN STREET, LONDON SW10 0BP - 2016.01.28 | 2016-02-19 16:07 | S217012760002 | LACLAND HOUSE | 244684 | Completed | 12a | High | Flat Door | The flat entrance door of flat 4 is one of the original timber doors which has a piece of board nailed over a part of it. | This flat entrance door should be checked to see that it is still a 30 minute fire rated door. If it is not then a new self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations should be fitted. | Home Ownership | Nazrul Islam | 2016-03-21 | Letter to resident attached | 2016-03-15 | Fully Completed | Nazrul Islam | 2016-02-19 16:07 | 2016-03-11 16:08 | 2016-02-19 16:07 | 2016-03-21 15:01 | -21 | In target | 2016-02-19 16:07 | 2016-03-25 15:00 | Janice Wray
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 16:42 | S217008560002 | MARKLAND HOUSE | 244981 | Active | 12a1 | High | Flat Door | It is not known if the flat entrance door of flat 54 is 30 minute fire rated doors. Flat 54's door is a 6 indented panel door. Leasehold | I would recommend that this flat entrance door is checked to see if it is a 30 minute fire rated doors (FD 30). If not it should be replaced with self closing 30 minute fire rated doors fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations. u | Home Ownership | Samuel Anyanwu | 2016-03-21 |  |  |  | Cyril Morris | 2016-02-22 16:42 | 2016-03-14 16:43 |  |  | 23 | 23 days overdue
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 16:43 | S217008560002 | MARKLAND HOUSE | 244983 | Active | 12a2 | High | Flat Door | It is not known if the flat entrance doors of flat 55 is a 30 minute fire rated doors. Flat 55's is a 4 indented panel door. Leasehold | I would recommend that this flat entrance door is checked to see if it is a 30 minute fire rated doors (FD 30). If not it should be replaced with self closing 30 minute fire rated doors fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations | Home Ownership | Samuel Anyanwu | 2016-03-21
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 16:45 | S217008560002 | MARKLAND HOUSE | 244984 | Active | 12b | High | Flat Door | The flat entrance door of flat 8 is damaged, there is a piece of plywood nailed over a small part of this timber door. Leasehold | This flat entrance door should be replaced with a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals (FD30s) and complying with all the requirements of the Building Regulations. | Home Ownership | Samuel Anyanwu | 2016-03-21
MATTHEW CLOSE, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 10:22 | S217009400001 | MATTHEW CLOSE (1-28) | 225101 | Active | 12b1 | High | Flat Door | The flat entrance doors of flat 20 has been changed within the last couple of years I am told, from the originally fitted fire rated doors. | Can it please be confirmed that this flat entrance door is self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s) If not then it should be replaced with FD 30 door complying with all the requirements of the Building Regulations. | Home Ownership | Samuel Anyanwu |  | email dialogue with lessee - has suggested that this info has been provided previously. requested again. | 2015-11-25 | Partially Completed | David Ward | 2015-11-02 10:22 | 2015-11-23 10:24 |  |  | 135 | 135 days overdue
MATTHEW CLOSE, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 10:24 | S217009400001 | MATTHEW CLOSE (1-28) | 225103 | Active | 12b2 | High | Flat Door | The flat entrance doors of flat 22 has been changed within the last couple of years I am told, from the originally fitted fire rated doors | Can it please be confirmed that this flat entrance door is self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s) If not then it should be replaced with FD 30 door complying with all the requirements of the Building Regulations. | Home Ownership | Samuel Anyanwu |  | letter sent to lessee 23.11.15. Advised in 2012 that the door was compliant on the back of then advice | 2015-11-23 | Partially Completed | David Ward | 2015-11-02 10:24 | 2015-11-23 10:26 |  |  | 135 | 135 days overdue
MILMAN HOUSE, MILMAN STREET, LONDON SW10 0BU - 2016.01.28 | 2016-02-19 10:27 | S217012760005 | MILMANS HOUSE | 244470 | Active | 12a | High | Flat Door | The flat entrance door of flat 4 has been changed from the original timber door. | Can it please be confirmed that this flat entrance door is a certified 30 minute fire rated door fitted with a self closing device and intumescent strips and cold smoke seals (FD30s). So complying with all the requirements of the Building Regulations. If it is not it should be replaced with a self closing FD30s door. | Home Ownership | Nazrul Islam | 2016-03-21 | letter sent on 23.2.16 | 2016-02-23 | Fully Completed | Nazrul Islam | 2016-02-19 10:27 | 2016-03-11 10:29 | 2016-02-19 10:27 | 2016-02-24 14:09 | -21 | In target | 2016-02-19 10:27 | 2016-03-20 11:02 | David Ward
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:46 | S217010030001 | OCTAVIA HOUSE | 205868 | Active | 12c | High | Flat Door | A non fire rated door and screen has been erected next to flat 35's entrance door which has separated off part of the balcony so that the residents of this flat now have a private storage area. | Is this structural change known about by the TMO? The door etc is not constructed of fire rated materials but if the TMO are happy with this cupboard then I do not think that any further action is needed on this issue apart from to confirm that the residents of flat 35 are not using this cupboard/area as a utility room etc and that there is no electrical power in there, apart from a light unit. If either of the above is true then the structure should be rebuilt to conform to all the requirements of the Building Regulations, ie 30 minute fire rated construction etc. | Home Ownership | Samuel Anyanwu |  | can we have photos of the modifications please? This relates to alterations and should be passed to David G/Liza for comment as to whether consent has been given | 2015-11-11 | Partially Completed | David Ward | 2015-07-09 14:46 | 2015-07-30 14:48 | 2015-07-09 14:46 | 2015-11-12 10:54 | -21 | In target | 2015-07-09 14:46 | 2015-08-24 10:22 | David Ward
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:09 | S217010030001 | OCTAVIA HOUSE | 102893 | Completed | 12d | Medium | Miscellaneous | A non fire rated door and screen has been erected next to flat 35's entrance door which has separated off part of the balcony so that the residents of this flat now have a private storage area. | Is this structural change known about by the TMO? The door etc is not constructed of fire rated materials but if the TMO are happy with this cupboard then I do not think that any further action is needed on this issue apart from to confirm that the residents of flat 35 are not using this cupboard/area as a utility room etc and that there is no electrical power in there, apart from a light unit. If either of the above is true then the structure should be rebuilt to conform to all the requirements of the Building Regulations, ie 30 minute fire rated construction etc. | Home Ownership | Jannie Pretorius |  | Following letter forwarded to leaseholder: [REDACTED] 35 Octavia House Southern Row Facsimile: London W10 5AE E-Mail: jpretorius@kctmo.org.uk Date: 30 August 2013 Our Reference Your Reference Please Contact TMO/LHS/JP Jannie Pretorius Dear Sirs Re: 35 Octavia House, London, W10 5AE I have been advised that a non fire rated door and screen has been erected next to the above flat's entrance door which has separated off part of the balcony which has created a private storage area. Can you please advise if the relevant permission was obtained for this structure to be erected as the balconies are not demised to leaseholders and also what this area is used for? Your urgent response on this matter would be appreciated. Yours sincerely, Jannie Pretorius Home Ownership officer | 2013-08-30 | Fully Completed | Jannie Pretorius | 2013-08-20 15:09 | 2013-10-19 15:11 | 2013-08-20 15:09 | 2013-09-09 11:28 | -60 | In target | 2013-08-20 15:09 | 2013-09-12 13:19 | Jannie Pretorius
SALTERS ROAD, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 11:11 | S217009940001 | SALTERS ROAD (1-28) | 225133 | Active | 12a | High | Flat Door | The Georgian wired fire rated glass in the vision panel of flat 16's entrance door has been replaced with a piece of clear glass, which does not appear to be marked as fire rated glass. | Can it please be confirmed that the clear glass in the vision panel of flat 16's entrance doors is fire rated glazing. If it is not then it should be replaced with a piece of fire rated glass immediately which has been correctly fitted. | Home Ownership | Samuel Anyanwu |  | Emailed lessee 23.11.15 | 2015-11-23 | Partially Completed | David Ward | 2015-11-02 11:11 | 2015-11-23 11:15 |  |  | 135 | 135 days overdue
SALTERS ROAD, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 11:16 | S217009940001 | SALTERS ROAD (1-28) | 225134 | Active | 12b | High | Flat Door | The flat entrance door of flat 22 has been changed within the last couple of years I am told, from the originally fitted fire rated door. | Can it please be confirmed that this flat entrance door is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s) If it is not then it should be replaced with FD 30s door complying with all the requirements of the Building Regulations. | Home Ownership | Samuel Anyanwu |  | emailed lessee 23.11.15 | 2015-11-23 | Partially Completed | David Ward | 2015-11-02 11:16 | 2015-11-23 11:17 |  |  | 135 | 135 days overdue
SHEFFIELD TERRACE(31-77 ODD NUMBERS) - 2015.06.03 | 2015-06-11 14:59 | S217007640001 | SHEFFIELD TERRACE ODDS (31-77) | 201142 | Completed | 12b | High | Flat Door | It is not known if the flat entrance door of 53 is not a self closing fire rated door, please see the letter sent to the TMO on the 28th November 2014. | Can it please be confirmed if the occupant has confirmed if the presently fitted flat entrance door is fire rated or not? If it is not when will this flat entrance door be replaced with a self closing 30 minute fire rated door, complying with all the requirements of the Building Regulations? | Home Ownership | Samuel Anyanwu | 2015-07-08 | Access provided finally on 10th March 2016 for Carl Stokes to assess. Flat dor is an FD30 - labelled & fitted with self-closer - COMPLIANT COMPLETED | 2016-03-14 | Fully Completed | David Ward | 2015-06-11 14:59 | 2015-07-02 15:18 | 2015-06-11 14:59 | 2016-03-15 16:32 | -21 | In target | 2015-06-11 14:59 | 2016-03-21 16:30 | Janice Wray
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:10 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215802 | Active | 12e | High | Flat Door | The door of flat 35A has been changed and is now a 6 indented panel door. | Please can it be confirmed that is flat entrance door is a self closing 30 minute fire rated door? | Home Ownership | Samuel Anyanwu |  | Emailed NHHG - they are unlikely to change the door given previous experiences | 2015-11-11 | Partially Completed | David Ward | 2015-09-09 17:10 | 2015-09-30 17:11 | 2015-09-09 17:10 | 2015-11-12 11:05 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:02 | S217010180014 | ST MARKS GROVE 13-48 | 203726 | Active | 12b | High | Flat Door | The door of flat 40 has been changed from the originally fitted flat entrance door. | Can it please be confirmed that this flat entrance door is a self closing 30 minute fire rated door complying with the requirements of the Building Regulations. | Home Ownership | Nazrul Islam |  | [REDACTED] 13 Maltings Place Fulmead Street e-mail: nislam@kctmo.org.uk London SW6 2BT Date: 14th July 2015 Our Reference Your Reference Please Contact TMO/LHS/NI/ 40 St Marks Grove Nazrul Islam Re: Front Door - FRA Review Dear [REDACTED] I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review. It is reported the flat entrance door of flat 40 has been changed from the original fire rated door. TMO's Fire Risk Assessor recommended that this flat's entrance door is checked to see if it is a self closing 30 minute fire rated door fitted with intumescent strips and cold smoke seals. (FD30s). If it is not then it should be replaced with FD30s door complying with all the requirements of the Building Regulations. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [REDACTED] Regards Nazrul Islam Home Ownership Officer | 2015-07-14 | Partially Completed | Nazrul Islam | 2015-06-29 10:02 | 2015-07-20 10:03 | 2015-06-29 10:02 | 2015-07-15 10:02 | -21 | In target | 2015-06-29 10:02 | 2015-08-04 15:35 | David Ward
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:31 | S217012770006 | TALBOT GROVE HOUSE | 177724 | Completed | 9 | Information Only | Miscellaneous | Flat 7 is unoccupied and being renovated, a new bathroom and kitchen has been fitted along with electrical wiring work undertaken within the dwelling and the installation of electrical hardwired domestic fire detection. | Are the TMO aware of the refurbishment of this flat? - leasehold flat | Home Ownership | Earle Harriott | 2015-02-26 | 26/2/15: Letter sent to the leaseholder dated 19/2/15, no further action. | 2015-02-26 | Fully Completed |  |  |  | 2015-01-12 11:31 | 2015-02-27 14:51
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:43 | S217005570001 | WALNUT TREE HOUSE | 103484 | Completed | 12c | High | Flat Door | There is a hole in the door frame of flat 19's entrance door where it looks like a pipe or cable has been removed. There is also a hole in the transom light area above the cupboard door next to this flats entrance door. | The hole in the flat entrance door from and in the transom light area over the cupboard door must be filled in using suitable fire rated materials. It may be easier to replace the whole boarded area in the transom light area above the cupboard door. This boarding must be 30 minute fire rated. | Home Ownership | David Ward |  | Letter before action sent by Legal | 2013-10-01 | Partially Completed | David Ward | 2013-08-23 11:43 | 2013-09-13 11:45 | 2013-08-23 11:43 | 2013-10-11 14:46 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:47 | S217005570001 | WALNUT TREE HOUSE | 103487 | Completed | 12f | High | Flat Door | The entrance door to flat 25 has been changed from the originally fitted door. | Can it be confirmed that this flat entrance door is a 30 minute fire rated door fitted with a self closing device. If not, then this door should be replaced with self closing 30 minute fire rated door, complying with all the requirements of the Building Regulations. | Home Ownership | David Ward |  | Letter before action sent by Legal. Door assessed by C Stokes on 31st Oct 2013 & confirmed as NON-COMPLIANT. Lessee provided with copy of assessor's report. Legal Services have written requesting confirmation of action taken to upgrade / replace door to achieve compliance - response required by 17th Jan 2014. | 2014-03-17 | Fully Completed | David Ward | 2013-08-23 11:47 | 2013-09-13 11:51 | 2013-08-23 11:47 | 2014-03-18 17:12 | -21 | In target | 2013-08-23 11:47 | 2014-03-24 17:10 | Janice Wray
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:51 | S217005570001 | WALNUT TREE HOUSE | 103488 | Active | 12f | High | Flat Door | The entrance doors to flat 29 has been changed from the originally fitted door. | Can it be confirmed that this flat entrance door is a 30 minute fire rated door fitted with a self closing device. If not, then this door should be replaced with self closing 30 minute fire rated door, complying with all the requirements of the Building Regulations. | Home Ownership | David Ward |  | Letter before action sent by Legal. Door assessed by C Stokes on 10th Oct 2013 & confirmed as NON-COMPLIANT. Lessee advised in writing. RBKC Legal Services have now written requesting confirmation of action to address this - response required by 17th Jan 2014. | 2013-10-01 | Partially Completed | David Ward | 2013-08-23 11:51 | 2013-09-13 11:53 | 2013-08-23 11:51 | 2014-01-03 11:06 | -21 | In target | 2013-08-23 11:51 | 2014-01-09 11:03 | Janice Wray
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:54 | S217005570001 | WALNUT TREE HOUSE | 103490 | Completed | 12f | High | Flat Door | The entrance door to flat 30 has been changed from the originally fitted door. | Can it be confirmed that this flat entrance door is a 30 minute fire rated door fitted with a self closing device. If not, then this doors should be replaced with self closing 30 minute fire rated doors, complying with all the requirements of the Building Regulations. | Home Ownership | David Ward |  | Letter before action sent by Legal. Door assessed by C Stokes on 8th Nov 2013 & confirmed as COMPLIANT. (Lessee given copy of report.) | 2013-11-09 | Fully Completed | David Ward | 2013-08-23 11:54 | 2013-09-13 11:55 | 2013-08-23 11:54 | 2014-01-08 14:42 | -21 | In target | 2013-08-23 11:54 | 2014-01-14 14:41 | Janice Wray
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:59 | S217005570001 | WALNUT TREE HOUSE | 103492 | Completed | 12h | Information Only | Flat Door | The following flat entrance doors are the original fire rated flat entrance doors, these are flush solid doors which appear to be fire rated. These are flats numbers 2, 16, 17, 19, 22, 27, 33 and 38. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. | Home Ownership | David Ward |  |  | 2013-10-10 | Fully Completed |  |  |  | 2013-08-23 11:59 | 2014-01-14 10:05 |  |  | 2013-08-23 11:59 | 2014-01-20 10:04 | Janice Wray
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:35 | S217012740010 | WHISTLER TOWER 1-61 | 102298 | Completed | 12b | High | Flat Door | The frame and entrance door, ie the whole door set to flat 57 has been changed from the originally fitted door and frame. | Can it be confirmed that this flat entrance door set is fire rated and that the door fitted with a self closing device? If this door set is not fire rated it should be replaced with a fire rated door set complying to the requirements of the Building Regulations. | Home Ownership | David Ward | 2013-09-06 | Letter before action sent by Legal Door assessed by C Stokes 24th Oct 2013 & confirmed as COMPLIANT | 2013-10-25 | Fully Completed | David Ward | 2013-08-16 15:35 | 2013-09-06 15:37 | 2013-08-16 15:35 | 2014-01-08 14:49 | -21 | In target | 2013-08-16 15:35 | 2014-01-14 14:44 | Janice Wray
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:38 | S217012740010 | WHISTLER TOWER 1-61 | 102303 | Completed | 12c (For information only) | Information Only | Flat Door | The entrance doors to flats 29 and 60 have been changed from the originally fitted doors, these doors have been checked and they appear to be fire rated doors. | No action is needed on this issue. | Home Ownership | David Ward |  | For information only - no action required | 2013-08-19 | Fully Completed |  |  |  | 2013-08-16 15:38 | 2013-08-20 09:47 |  |  | 2013-08-16 15:38 | 2013-08-23 15:51 | David Ward
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:35 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214788 | Active | 8c | Low | Miscellaneous | There is an old charcoal BBQ to the side of flat 22, on the external roof area, it is not known if this BBQ is being used or not, but it appears not to be. I believe that cooking on a BBQ on a flat balcony area is not allowed under the tenancy agreement. (LEASEHOLD) | I would recommend that this charcoal BBQ is removed from this area outside of flat 22. Nazrul Islam | Home Ownership | Nazrul Islam |  | property sub let - emailed lessee 24.11.15 | 2015-11-24 | Partially Completed | David Ward | 2015-09-03 16:35 | 2016-03-01 16:37 |  |  | 36 | 36 days overdue
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 15:02 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215961 | Completed | 9 | Information Only | Miscellaneous | Flat 24B appears to be having structural alterations undertaken within it, there were 9 sheets of plasterboard in the lobby area up to this flat and it can be seen that work is being undertaken within this dwelling. LEASEHOLD | Are the TMO aware that refurbishment work is being undertaken within this flat. | Home Ownership | Samuel Anyanwu |  | written to leaseholder with regards to these works | 2015-11-25 | Fully Completed |  |  |  | 2015-09-10 15:02 | 2015-11-26 12:07 |  |  | 2015-09-10 15:02 | 2015-11-20 18:38 | David Ward