## Fire Risk Assessment by Team Us
Fire Risk Assessment by Team / User
Total: 481
Risk Assessment | Process Start Date | Prop ref | Block | Process No | Proc Status | Iitem no | Priority | Category | Risk | Action | Team | Who | Action Due Date | Action taken | Comp date | Full or partial | Reporting User | Feedback Start Date | Feedback Due Date | Closure Start Date | Closure Due Date | Date Difference | In Target | Return Stage Startdate | Return Stage Duedate | Return User
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:21 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184129 | Completed | 12 | High | Responsive Item | There is a crack in the floor of the staircase landing at the ground floor level between flats 6 and 7. | I would recommend that this floor of the staircase landing is looked at by a qualified structural engineer and his recommendations on this issue are followed. | Responsive Repairs | Robert Speak | 2016-03-10 | Order 201555357 raised for RD | 2016-03-08 | Fully Completed | Janice Wray | 2015-02-17 15:21 | 2015-03-10 15:22 | 2015-02-17 15:21 | 2016-04-07 15:49 | -21 | In target | 2015-02-17 15:21 | 2016-04-07 12:52 | Janice Wray
1 BURNABY STREET - 2013.12.31 | 2013-12-31 13:54 | S217000510001 | BURNABY STREET (1) | 122145 | Completed | 1 | High | Communal Lighting | The light in the entrance hall lobby area does not appear to be working. | I would recommend that the light in the entrance hall/lobby area is checked by a competent electrician and repaired or replaced so that the light works. | Responsive Repairs | Alex Bosman | 2015-08-03 | resident of 1st floor FLAT WHO ADVVISED THAT THE LIGHT IN THE ENTRANCE HALL IS WORKING AND REFUSED TO ARRNAGE ACCESS. RESIDENT STATED NO WORKS ARE REQUIRED. | 2015-11-17 | Fully Completed | Maria Ares | 2013-12-31 13:54 | 2014-01-21 14:08 | 2013-12-31 13:54 | 2016-01-19 08:57 | -21 | In target | 2013-12-31 13:54 | 2016-01-25 08:57 | Janice Wray
1 BURNABY STREET - 2013.12.31 | 2013-12-31 14:09 | S217000510001 | BURNABY STREET (1) | 122147 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | completed - noted for possible future upgrade | 2015-11-17 | Fully Completed | Maria Ares | 2013-12-31 14:09 | 2014-06-29 14:11 | 2013-12-31 14:09 | 2015-11-23 16:22 | -180 | In target | 2013-12-31 14:09 | 2015-11-27 16:22 | Janice Wray
1 CLYDESDALE ROAD - 2015.01.06 | 2015-01-12 11:13 | S217008380001 | CLYDESDALE ROAD (1) | 177697 | Completed | 14 | High | Responsive Item | Part of the ceiling on the staircase landing, by flat 5 has been replaced. The original ceiling lining which appears to be a dense boarding material, in all likely hood fire rated was replaced with a piece of thin plywood. | I would recommend that this piece of plywood is removed and a boarding material of the same density and possibly fire rating as the original material is refitted. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Works order raised - 201529211 | 2015-09-22 | Fully Completed | Janice Wray | 2015-01-12 11:13 | 2015-02-02 11:14 | 2015-01-12 11:13 | 2015-09-28 18:21 | -21 | In target | 2015-01-12 11:13 | 2015-10-02 18:21 | Janice Wray
1 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 10:17 | S217001880001 | ELM PARK GARDENS (1) | 201006 | Completed | 12a | High | Responsive Item | The hinge of the external door to the basement plant/boiler room is broken and this door does not shut fully. | I would recommend that a new hinge is fitted to this external boiler/plant room door, so that this door shuts fully. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-11 10:17 | 2015-07-02 10:18 | 2015-06-11 10:17 | 2016-02-02 18:22 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:25 | S217009580001 | NURSERY LANE (1) | 142329 | Completed | 17c | Medium | Smoke Alarms | On the ceiling of the new office there is a domestic battery powered smoke detector, there are also 2 smoke detectors of the buildings fire alarm system. | This domestic smoke detector can be removed. | Responsive Repairs | Alex Bosman |  | removed battery smoke from office | 2015-11-17 | Fully Completed | Maria Ares | 2014-05-06 13:25 | 2014-07-05 13:27 | 2014-05-06 13:25 | 2015-11-18 12:31 | -60 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 10:10 | S217007560001 | PEMBRIDGE SQUARE (1) | 136573 | Completed | 12a | High | Miscellaneous | The external steps up to the buildings entrance door are slightly damaged. | I would recommend that these external steps are repaired so that persons do not trip or slip up or down them. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-03-26 10:10 | 2014-04-16 10:12 | 2014-03-26 10:10 | 2015-11-30 16:15 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 10:12 | S217007560001 | PEMBRIDGE SQUARE (1) | 136575 | Completed | 12b | High | Flat Door | The door handle of flat 5's entrance door has been removed, so there is now a hole straight through the door. | A new door handle should be fitted to the flat entrance door of flat 5 so that the door is a fire rate door with no hole through it. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-03-26 10:12 | 2014-04-16 10:13 | 2014-03-26 10:12 | 2015-11-30 16:14 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 10:13 | S217007560001 | PEMBRIDGE SQUARE (1) | 136576 | Completed | 12c | High | Responsive Item | The roof hatch, on the top floor level landing which gives access to the external flat roof area of this building is not secured locked shut. There is no edge protection for this external roof. | I would recommend that the roof hatch is secured locked shut to stop persons accessing the external roof area of this building. THIS IS NOT A FIRE EXIT | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-03-26 10:13 | 2014-04-16 10:59 | 2014-03-26 10:13 | 2015-11-30 16:10 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 10:59 | S217007560001 | PEMBRIDGE SQUARE (1) | 136592 | Completed | 14a | High | Responsive Item | The wall in the ground floor entrance hall is damaged where flat 5s letter box has been removed from the wall. | The wall in the ground floor entrance hall should be repaired with suitable fire rated materials. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-03-26 10:59 | 2014-04-16 11:00 | 2014-03-26 10:59 | 2015-11-30 16:07 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 11:00 | S217007560001 | PEMBRIDGE SQUARE (1) | 136593 | Completed | 14b | High | Responsive Item | 1There are covers missing from the electrical wiring ducts in the 2nd floor level electrical cupboard. It appears that work has been undertaken on wiring circuits and the covers not replaced afterwards. | I would recommend that covers are placed back on all of the electrical wiring ducts in the 2nd floor level electrical cupboard. | Responsive Repairs | Alex Bosman |  | Checked Trunking - in place. All works completed | 2015-11-20 | Fully Completed | Maria Ares | 2014-03-26 11:00 | 2014-04-16 11:02 | 2014-03-26 11:00 | 2015-11-23 13:00 | -21 | In target
1 ST HELENS GARDENS - 2014.03.06 | 2014-03-13 13:25 | S217010100001 | ST HELENS GARDENS (1) | 134457 | Completed | 3 | Information Only | Inspection Regime | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | completed - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2014-03-13 13:25 | 2015-11-23 14:15 |  |  | 2014-03-13 13:25 | 2015-11-29 14:15 | Janice Wray
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 11:56 | S217007860001 | GOLBORNE GARDENS 1-10 | 182818 | Completed | 14a | High | Responsive Item | Outside the ground floor electrical room at the base of the staircase some of the duct work is missing. This seems to have been caused after work by contractors who appear to installed cabling and have not replaced the cover or made good the duct work afterwards. | The ducting outside the ground floor electrical room at the base of the staircase should be repaired with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Order raised -201529213 | 2015-09-22 | Fully Completed | Janice Wray | 2015-02-10 11:56 | 2015-03-03 11:58 | 2015-02-10 11:56 | 2015-09-28 18:25 | -21 | In target | 2015-02-10 11:56 | 2015-10-02 18:25 | Janice Wray
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 11:59 | S217007860001 | GOLBORNE GARDENS 1-10 | 182822 | Completed | 14b | High | Responsive Item | There is a hole in the wall lining above the electrical room door where a cable has been pasted through the wall and the wall has not been made good. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham |  | Order raised | 2015-09-22 | Fully Completed | Janice Wray | 2015-02-10 11:59 | 2015-03-03 12:00 | 2015-02-10 11:59 | 2015-09-28 18:27 | -21 | In target | 2015-02-10 11:59 | 2015-10-02 18:27 | Janice Wray
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 12:02 | S217007860001 | GOLBORNE GARDENS 1-10 | 182825 | Completed | 14c | High | Responsive Item | A light unit has been fitted on the ceiling of the entrance hall area, by the staircase half landing, to fit this light unit part of a wall lining has been cut into. | I would recommend that the light unit is repositioned and that the wall lining is repaired used suitable fire rated materials. | Responsive Repairs | John Tatham |  | Order raised | 2015-11-10 | Fully Completed | Janice Wray | 2015-02-10 12:02 | 2015-03-03 12:04 | 2015-02-10 12:02 | 2015-11-11 21:34 | -21 | In target | 2015-02-10 12:02 | 2015-11-17 21:33 | Janice Wray
10 ASHBURNHAM ROAD - 2013.09.30 | 2013-10-10 15:33 | S217000190004 | ASHBURNHAM ROAD (10) | 110155 | Completed | 3 | Low | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357138 | 2014-04-07 | Fully Completed | Michael Lyons | 2013-10-10 15:33 | 2014-04-08 15:36 | 2013-10-10 15:33 | 2014-05-07 20:00 | -180 | In target
10 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 11:19 | S217001880012 | ELM PARK GARDENS (10) | 200416 | Active | 14 | High | Responsive Item | The wall and ceiling linings of the internal lift motor room on the fourth floor level had numerous holes in them. (The upper level of the third floor flats are also at this floor level.) | These holes in the wall and ceiling lining should be filled covered over with a suitable fire rated material to maintain the fire rating of the structure of the building. There is sleeping accommodation on the other side of these walls. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham
10 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 11:21 | S217001880012 | ELM PARK GARDENS (10) | 200418 | Completed | 14b | Medium | Responsive Item | By the rear exit door to the garden area there is bare floor boards on the floor where it appears that the flooring has been removed and not replaced. | I would recommend that the area by the rear exit door has a new floor surface provided for it. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm fully complete | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-08 11:21 | 2015-08-07 11:22 | 2015-06-08 11:21 | 2016-02-02 18:25 | -60 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:01 | S217009620002 | OXFORD GARDENS (109) | 197392 | Completed | 12a | High | Responsive Item | The lock has been removed from the set of double fire doors by flats 1 and 2 at the base of the stairs and the hole not filled in. | Where the lock has been removed from the set of double fire doors by flats 1 and 2 at the base of the stairs and the hole should be filled in or covered by a suitable fire rated material so the fire compartmentation is maintained. | Responsive Repairs | John Tatham | 2015-06-15 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-05-16 09:01 | 2015-06-06 09:02 | 2015-05-16 09:01 | 2016-02-23 19:30 | -21 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:03 | S217009620002 | OXFORD GARDENS (109) | 197393 | Completed | 12b | Medium | Responsive Item | The left hand leaf of the double fire doors set by flats 1 and 2 at the base of the stairs has a bolt fitted on it, this could hinder the opening of the doors if the bolt is engaged. | I would recommend that this bolt is removed. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completed | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-16 09:03 | 2015-07-15 09:04 | 2015-05-16 09:03 | 2016-02-02 18:27 | -60 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:05 | S217009620003 | OXFORD GARDENS (109A) | 197394 | Completed | 12 | Information Only | Responsive Item | The lower right hand side pane of glass in the door of house number 1 of 109A is broken. | I would recommend that this pane of glass in the door is replaced. | Responsive Repairs | John Tatham | 2015-11-16 | RD confirm completion | 2016-03-05 | Fully Completed |  |  |  | 2015-05-16 09:05 | 2016-03-07 13:22
11 CHEPSTOW CRESCENT- 2015.3.17 | 2015-03-20 12:30 | S217007050001 | CHEPSTOW CRESCENT (11) | 189062 | Completed | 12 | High | Responsive Item | The fire rated double doors separating the entrance hall/lobby area and the staircase do not shut in line with each other correctly. | I would recommend that these double swing double doors are inspected and checked and that the hinges are adjusted so that these doors close in line with each other. | Responsive Repairs | John Tatham |  | Works order raised -201529207 | 2015-12-24 | Fully Completed | Janice Wray | 2015-03-20 12:30 | 2015-04-10 12:32 | 2015-03-20 12:30 | 2015-12-29 15:00 | -21 | In target | 2015-03-20 12:30 | 2015-12-31 15:00 | Janice Wray
11 CHEPSTOW CRESCENT- 2015.3.17 | 2015-03-20 12:33 | S217007050001 | CHEPSTOW CRESCENT (11) | 189063 | Completed | 14 | Medium | Responsive Item | There is a hole in the door frame of the electrical cupboard/room where a cable has been pasted through and a repair not been made good. There has been an attempt to fill in this hole but the work is not very good. | I would recommend that this hole is re-filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Works order raised | 2015-09-22 | Fully Completed | Janice Wray | 2015-03-20 12:33 | 2015-05-19 12:34 | 2015-03-20 12:33 | 2015-09-28 18:14 | -60 | In target | 2015-03-20 12:33 | 2015-10-02 18:14 | Janice Wray
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 10:55 | S217009467707 | MORGAN ROAD ODD (1-11) | 102421 | Completed | 1b | Medium | Responsive Item | At the base of the staircase by the entrance door of this building the cover plate is missing from an electrical junction box. | I would recommend that a new cover plate is fitted over the front of this electrical junction box. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357145 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 10:55 | 2013-10-18 10:57 | 2013-08-19 10:55 | 2014-05-02 10:29 | -60 | In target
11-18 GOLBORNE GARDENS - 2015.02.05 | 2015-02-10 12:24 | S217008850002 | GOLBORNE GARDENS 11-18 | 182838 | Completed | 8 | High | Responsive Item | The floor surface of the steps of the staircase between the ground and first floor levels is damaged. | The floor surface of the steps of the staircase between the ground and first floor levels should be repaired or replaced so that they are not a trip hazard. | Responsive Repairs | John Tatham |  | Order raised | 2015-09-22 | Fully Completed | Janice Wray | 2015-02-10 12:24 | 2015-03-03 12:26 | 2015-02-10 12:24 | 2015-09-28 18:28 | -21 | In target | 2015-02-10 12:24 | 2015-10-02 18:28 | Janice Wray
1-18 BURLEIGH HOUSE - 2015.05.06 | 2015-05-12 10:16 | S217010080009 | BURLEIGH HOUSE 1-18 | 196492 | Completed | 14 | High | Responsive Item | In the side wall of the electrical room/ cupboard there is a hole in the wall lining where cables have been pasted through the wall and the duct work not finished off correctly. | This hole in the wall linings should be filled in with suitable fire rated materials to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm complete | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-12 10:16 | 2015-06-02 10:17 | 2015-05-12 10:16 | 2016-02-02 18:30 | -21 | In target
1-18 DARTREY WALK - 2014.3.12 | 2014-04-10 15:44 | S217012740004 | DARTREY WALK 1-18 | 139375 | Completed | 16 | High | Responsive Item | The sign indicating that a dry rising main outlet is located in the cupboard of Dartrey Tower is missing. | I would recommend that a new dry riser sign is displayed on this cupboard door so that the LFB know that an outlet of the dry rising main is located in this cupboard. | Responsive Repairs | Michael Lyons |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-04-10 15:44 | 2014-05-01 16:01 | 2014-04-10 15:44 | 2015-12-14 16:12 | -21 | In target
12 RUSSELL GARDENS - 2014.6.11 | 2014-06-30 15:46 | S217006670002 | RUSSELL GARDENS (12) | 151046 | Completed | 3 | Medium | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Michael Lyons |  |  | 2015-12-02 | Fully Completed | Janice Wray | 2014-06-30 15:46 | 2014-08-29 15:48 | 2014-06-30 15:46 | 2015-12-03 19:57 | -60 | In target
1-26 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 08:51 | S217000830003 | CHELSEA MANOR COURT 1-26 | 207286 | Completed | 14a | High | Responsive Item | Above each of the ground floor level electrical room/cupboard doors there are cable holes in the door frame and in the wall lining where cables have been passed through the door frame and the wall lining and making good has not been undertaken. | These holes in the door frames and the wall linings should be filled in with a suitable fire rated materials to maintain the fire rating of the structural elements of this building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-17 08:51 | 2015-08-07 08:52 | 2015-07-17 08:51 | 2016-02-02 18:32 | -21 | In target
1-26 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 08:53 | S217000830003 | CHELSEA MANOR COURT 1-26 | 207287 | Active | 14b | Medium | Responsive Item | On each landing level of each staircase light fitting have been replaced, the new light fittings are smaller than the old ones. Where the old light fittings have been removed there are holes in the ceiling lining which have not been in filled/repaired. | These holes in the ceiling linings should be filled in/repaired with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:38 | S217012740001 | BERENGER WALK 1-28 | 139335 | Completed | 12a | High | Responsive Item | A piece of chip board has been screwed over the area where the meters can be viewed next to flat 28 Berenger Walk. It is assumed that the area under this chip board is damaged. | I would recommend that this piece of chip board is removed and the area underneath it inspected, if the fire rated meter viewing glazing is damaged or missing these should be replaced. Likewise if any timber cladding is damaged this should be replaced. | Responsive Repairs | Alex Bosman |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-04-10 14:38 | 2014-05-01 14:42 | 2014-04-10 14:38 | 2015-12-14 16:10 | -21 | In target
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:44 | S217012740001 | BERENGER WALK 1-28 | 139344 | Completed | 12c | High | Responsive Item | The fire rated glass covering the meter viewing panels of Flat 4 Blantyre Walk and Flat 20 Berenger Walk are damaged with holes in the glass or badly cracked. | I would recommend that a new piece of fire rated glass is inserted in these two meters viewing areas. | Responsive Repairs | Alex Bosman |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-04-10 14:44 | 2014-05-01 14:45 | 2014-04-10 14:44 | 2015-12-14 16:11 | -21 | In target
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:46 | S217012740001 | BERENGER WALK 1-28 | 139345 | Completed | 14a | High | Responsive Item | The cover is missing from the duct work on the external area outside the electrical cupboards by Whistler Tower. The covers are also missing from all of the electrical boards within the cupboards. It is assumed that contractors have been working in this area. | The covers should be replaced on the duct work and on the electrical boards. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all the structural elements of the buildings remain fire rated. | Responsive Repairs | Alex Bosman |  | REFIXED MISSING TRUNKING LID TO OUTSIDE INTAKE ON 1ST FLOOR . | 2015-11-17 | Fully Completed | Maria Ares | 2014-04-10 14:46 | 2014-05-01 14:47 | 2014-04-10 14:46 | 2015-11-18 12:44 | -21 | In target
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:48 | S217012740001 | BERENGER WALK 1-28 | 139346 | Completed | 14b | High | Responsive Item | There is a hole through the wall lining of the staircase enclosure of Berenger Tower where a large diameter black electrical cable has been passed through the wall and the hole not made good. | The hole in this wall lining should be in filled with a suitable fire rated material so that the structural elements of the buildings remain fire rated. I would recommend that in future checks are carried out after contractors have undertaken work in this building. | Responsive Repairs | Alex Bosman |  |  | 2015-12-02 | Fully Completed | Janice Wray | 2014-04-10 14:48 | 2014-05-01 14:50 | 2014-04-10 14:48 | 2015-12-03 20:19 | -21 | In target
13 BURNABY STREET - 2013.12.31 | 2013-12-31 14:26 | S217000510003 | BURNABY STREET (13) | 122159 | Completed | 1 | High | Communal Lighting | The light switches in the entrance hall lobby area are not working correctly, the push switches only allow the lights to be on for approximately 10 seconds. | I would recommend that the light switches are checked by a competent electrician and repaired or replaced so that the lights remain on for a reasonable length of time. | Responsive Repairs | Alex Bosman | 2016-02-16 | RMA confirmed all works complete | 2016-02-16 | Fully Completed | Maria Ares | 2013-12-31 14:26 | 2014-01-21 14:27 | 2013-12-31 14:26 | 2016-02-17 10:09 | -21 | In target
13 BURNABY STREET - 2013.12.31 | 2013-12-31 14:27 | S217000510003 | BURNABY STREET (13) | 122160 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | completed - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2013-12-31 14:27 | 2015-11-23 17:13 |  |  | 2013-12-31 14:27 | 2015-11-27 17:13 | Janice Wray
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:30 | S217009210005 | LANCASTER ROAD (130) | 102672 | Completed | 14 | Medium | Responsive Item | There are holes in the wall linings where cables have been past through and a repair not made good at high level in the basement electrical cupboard. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357149 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-08-19 16:30 | 2013-10-18 16:31 | 2013-08-19 16:30 | 2014-05-02 12:26 | -60 | In target
140 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:50 | S217002110014 | FINBOROUGH ROAD (140) | 194209 | Completed | 12a | High | Responsive Item | The fire rated door of the lower ground floor electrical room/cupboard door could not be secured locked shut, this door was unlocked and open when I arrived at this premises. | The gerda lock on this lower ground floor electrical room/cupboard door should be repaired or replaced so that this fire door can be secured locked shut. | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2015-04-27 09:50 | 2015-05-18 09:52 | 2015-04-27 09:50 | 2015-11-25 20:40 | -21 | In target
140 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:52 | S217002110014 | FINBOROUGH ROAD (140) | 194210 | Completed | 12b | High | Responsive Item | The top hinge on the fire door at the base of the stairs next to the electrical room is damaged. This means that this fire | This hinge should be replaced immediately so that this fire door can close fully onto its stops and the compartmentation of the protected staircase is maintained. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-04-27 09:52 | 2015-05-18 09:54 | 2015-04-27 09:52 | 2015-11-27 20:00 | -21 | In target
140 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:56 | S217002110014 | FINBOROUGH ROAD (140) | 194212 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining to the top left hand side of the lower ground floor level electrical cupboard/room where a cable has been pasted through and a repair not been made good. | I would recommend that this hole is filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-12-03 | Fully Completed | Janice Wray | 2015-04-27 09:56 | 2015-05-18 09:58 | 2015-04-27 09:56 | 2015-12-04 16:37 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:54 | S217012040001 | LEXHAM GARDENS (140) | 102531 | Completed | 8e | Medium | Responsive Item | The carpet on the 3rd floor level landing is damaged and could be a trip hazard. | I would recommend that the carpet on the landings and the staircase of this building is looked at especially the 3rd floor level landing area and any repairs are undertaken as required so there is not a trip hazard from any damaged areas of carpet. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357155 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 13:54 | 2013-10-18 13:55 | 2013-08-19 13:54 | 2014-05-02 10:56 | -60 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:08 | S217012040001 | LEXHAM GARDENS (140) | 102654 | Completed | 12c | High | Responsive Item | The entrance doors to flats 5 and 7 have been changed from the originally fitted doors and there is up to a 2 inch gap at the base of flat 5's door. | Can it be confirmed these two flats entrance doors are 30 minute fire rated doors fitted with a self closing devices capable of shutting the doors fully on to their stops. | Responsive Repairs | Michael Lyons | 2014-05-15 | Can this be passed to the FRA consultant Assessed by C Stokes on 13th May - Door of flat 7 changed recently - appears to be an FD30 doo - check records to ensure. Flat 5 requires replacement self-closing FD30 door to be fitted asap. | 2016-03-07 | Fully Completed | Michael Lyons | 2013-08-19 16:08 | 2013-09-09 16:11 | 2013-08-19 16:08 | 2016-03-08 13:29 | -21 | In target | 2013-08-19 16:08 | 2016-03-14 13:29 | Janice Wray
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:11 | S217012040001 | LEXHAM GARDENS (140) | 102656 | Completed | 12d | Medium | Responsive Item | The door to the basement level room with the gas meters in is damaged and cannot be closed fully nor can it be locked shut | The door to this basement level room should be repaired or replaced so that it can be shut fully and secured locked shut. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357155 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 16:11 | 2013-10-18 16:12 | 2013-08-19 16:11 | 2014-05-02 11:14 | -60 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:13 | S217012040001 | LEXHAM GARDENS (140) | 102657 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining opposite flat 9's entrance door were it appears that a box has been ripped off the wall and now the plaster is damaged and the is a hole. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357155 | 2014-04-18 | Fully Completed | Michael Lyons | 2013-08-19 16:13 | 2013-09-09 16:14 | 2013-08-19 16:13 | 2014-05-02 11:30 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:15 | S217012040001 | LEXHAM GARDENS (140) | 102660 | Completed | 16 | High | Responsive Item | There are escape exit signs displayed on each landing of this building stating "Use Roof for Fire Escape" indicating that the residents are expected to leave this building in the event of an emergency by climbing over the roof of this 5 storey building. Having first climbed up a pull down ladder and accessing the roof via a velux type window. I am assuming that the TMO are not expecting the residents of this building to climb over the roof of this building as a means of escape route and use the pull down ladder to access the open roof area. | I would therefore recommend that all these signs are removed immediately. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357155 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 16:15 | 2013-09-09 16:16 | 2013-08-19 16:15 | 2014-05-02 11:39 | -21 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:17 | S217012740003 | UPPER BERENGER WALK 1-42 | 139406 | Completed | 12a | High | Responsive Item | The double doors to the electrical cupboard adjacent to Berenger Tower on Upper Berenger Walk are damaged. | These doors should be repaired or replaced, with the lock checked to make certain it works correctly, so that the electrical components in the cupboard are protected. | Responsive Repairs | Michael Lyons |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-04-10 16:17 | 2014-05-01 16:19 | 2014-04-10 16:17 | 2015-11-30 17:27 | -21 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:24 | S217012740003 | UPPER BERENGER WALK 1-42 | 139414 | Completed | 14 | High | Responsive Item | There are areas of the timber cladding damaged near the supply meters viewing windows of: Flat 10 of Upper Berenger Walk. Flat 15 of Upper Berenger Walk. Flat 22 of Upper Berenger Walk. Flat 26 of Upper Berenger Walk. | This damaged timber cladding near to the supply meter viewing windows of these flats should be replaced so that the external structure of the building is not compromised. | Responsive Repairs | Michael Lyons |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-04-10 16:24 | 2014-05-01 16:26 | 2014-04-10 16:24 | 2015-11-27 21:40 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:10 | S217010567701 | LONGLANDS COURT (1-48) | 103172 | Completed | 1d | High | Responsive Item | The light outside the lift motor room above the staircase of flats 13 to 24 is not working. | I would recommend that the light unit is check to see why it is not working and repaired if necessary so that it works correctly and illuminates this area outside the lift motor room. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357160 | 2014-04-15 | Fully Completed | Michael Lyons | 2013-08-21 16:10 | 2013-09-11 16:12 | 2013-08-21 16:10 | 2014-05-06 13:18 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:12 | S217010567701 | LONGLANDS COURT (1-48) | 103174 | Completed | 1e | High | Responsive Item | The light unit inside the ground floor level electrical cupboard by flats 25 and 26 is hanging off the ceiling by its cable and is not working. | I would recommend that this light unit is check to see why it is not working and fixed back up on to the ceiling also repaired or replaced as necessary so that it works correctly. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357160 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-21 16:12 | 2013-09-11 16:14 | 2013-08-21 16:12 | 2014-05-06 14:17 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:21 | S217010567701 | LONGLANDS COURT (1-48) | 103182 | Completed | 12c | Medium | Responsive Item | On the 2nd floor level half landing below flats 17 and 18 the door/flap to opening of the rubbish chute was damaged and did not shut fully. | This door/flap to the rubbish chute opening should be repaired or replaced so that it shuts fully. | Responsive Repairs | Jackie Gaikwad | 2014-06-30 | Site job number 201357160 all rubbish shute works are being contracted out for completion w/e 30/6/14, all surrounding prep works have been completed RD confirm completion | 2016-02-01 | Fully Completed | Michael Lyons | 2013-08-21 16:21 | 2013-10-20 16:23 | 2013-08-21 16:21 | 2016-02-02 18:33 | -60 | In target | 2013-08-21 16:21 | 2014-05-14 15:39 | Janice Wray
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:23 | S217010567701 | LONGLANDS COURT (1-48) | 103185 | Completed | 14a | High | Responsive Item | There are numerous holes in the wall and ceiling linings at the roof space level where cables have been pasted through walls and door frames and a repair not made good. | The whole of the roof space level should be checked for holes in the wall and ceiling linings. Most of these holes are in the wall linings above the doors or in the door frames, these holes should be filled in with a suitable fire rated material depending on their location. This is to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357160 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-21 16:23 | 2013-09-11 16:24 | 2013-08-21 16:23 | 2014-05-06 14:18 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:25 | S217010567701 | LONGLANDS COURT (1-48) | 103186 | Completed | 14b | High | Responsive Item | There is a hole in the end wall lining at ceiling level of the ground floor level electrical room opposite flat 25. This is where a cable has been pasted through the wall and a repair has not been made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357160 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-21 16:25 | 2013-09-11 16:26 | 2013-08-21 16:25 | 2014-05-06 14:19 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:48 | S217010567701 | LONGLANDS COURT (1-48) | 103201 | Completed | 12b | Medium | Responsive Item | At the roof space level there is a metal door in the central section of the roof space in the separating wall which was in the open position. | This metal door in the separating wall should be kept shut at all times with a sign on each side of it stating " fire door keep shut" | Responsive Repairs | Jackie Gaikwad |  | Done Site job number 201357160 | 2014-04-07 | Fully Completed | Michael Lyons | 2013-08-21 16:48 | 2013-10-20 16:51 | 2013-08-21 16:48 | 2014-05-06 14:20 | -60 | In target
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:16 | S217008650004 | EDENHAM WAY 15-50 | 207075 | Active | 1b | High | Responsive Item | The lights were not working in the roof level water tank room at the time of this assessment. | I would recommend that the lights in water tank room are checked and repaired or replaced so that they work correctly. | Responsive Repairs | John Tatham |  |  |  |  | Cyril Morris | 2015-07-16 09:16 | 2015-08-06 09:17 |  |  | 244 | 244 days overdue
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:29 | S217008650004 | EDENHAM WAY 15-50 | 207082 | Completed | 14 | Low | Responsive Item | It was noticed that the brick thresholds are missing from below the service riser ducts in the 1st and 2nd floor level lift lobby areas. | I would recommend that the brick thresholds should be replaced below these riser ducts on these lift lobby areas. | Responsive Repairs | John Tatham | 2016-01-12 | RD confirm completion - order number 201553706 | 2016-03-05 | Fully Completed | Janice Wray | 2015-07-16 09:29 | 2016-01-12 09:30 | 2015-07-16 09:29 | 2016-03-07 13:29 | -180 | In target
1-52 UPPER BLANTYRE WALK - 2014.3..12 | 2014-04-11 09:19 | S217012740013 | UPPER BLANTYRE WALK 1-45 | 139461 | Completed | 12d | Information Only | Flat Door | This flat entrance door had been changed from the originally fitted fire rated flat entrance doors. This entrance door appear not to be fire rated. Flat 7 Upper Blantyre Walk- tenanted Assessor confirms that this door does not require upgrade or replacement at this stage. | Assessor recommends that this flat entrance door must comply with the requirements of the current Building Regulations when it is next replaced | Responsive Repairs | Michael Lyons | 2014-10-08 | RD confirm completion - 21553711 | 2016-03-05 | Fully Completed |  |  |  | 2014-04-11 09:19 | 2016-03-07 13:41
1-52 UPPER WHISTLER WALK - 2014.3..12 | 2014-04-11 09:09 | S217012740009 | UPPER WHISTLER WALK 1-52 | 139453 | Completed | 12c | High | Responsive Item | The fire rated glass covering the electrical meter of flat 6 Upper Whistler Walk is completely missing, so there is a hole into the flat from the walkway. | I would recommend that a new piece of fire rated glass is inserted in the opening in the wall of this flat. Where the glazing is missing. | Responsive Repairs | Michael Lyons |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-04-11 09:09 | 2014-05-02 09:12 | 2014-04-11 09:09 | 2015-12-14 16:14 | -21 | In target
16 AND 17 PENZANCE STREET - 2015.08.13 | 2015-09-02 14:59 | S217009670005 | PENZANCE STREET 16/17 A-H | 214592 | Completed | 12 | High | Responsive Item | There are gaps around the door frame of the electrical cupboard/room in number 16 where the door frame is not fixed or sealed to the brick work fully. | I would recommend that this door frame is fixed and seal correctly to the brickwork so that there are no gaps between the door frame and the brick work. Any materials used to infill any gaps must be fire rated. | Responsive Repairs | Alan Brooks | 2015-09-23 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-02 14:59 | 2015-09-23 15:04 | 2015-09-02 14:59 | 2016-02-23 19:42 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:06 | S217002110007 | FINBOROUGH ROAD (169) | 194364 | Completed | 14a | High | Responsive Item | The material in the transom area above the ground floor electrical cupboard/room door is not fire rated, it appears to be a piece of thin plywood. | This transom light area above this door should be filled in with a suitable fire rated material to maintain the compartmentation and fire rated structure of the building. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-04-27 16:06 | 2015-05-18 16:08 | 2015-04-27 16:06 | 2015-11-27 19:54 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:08 | S217002110007 | FINBOROUGH ROAD (169) | 194365 | Completed | 14b | High | Responsive Item | There is vent in the wall of the ground floor electrical cupboard/room onto the entrance hall/lobby area, this is a low level vent which is damaged. | I would recommend that this damaged vent is removed and the hole is in filled with brick work or a suitable fire rated material is filled over the vent hole. This is so that the fire rating of the wall, separating the electrical area to the entrance hall is maintained fire rated and also that of the structure of the building is maintained. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-04-27 16:08 | 2015-05-18 16:09 | 2015-04-27 16:08 | 2015-11-27 19:57 | -21 | In target
19 DANVERS STREET -2015.10.08 | 2015-10-16 09:01 | S217001420002 | DANVERS STREET (19) | 222234 | Completed | 12 | High | Responsive Item | The letter box flap is missing from the entrance door of flat C. TENANTED | A new letter box flap should be fitted to this flats entrance door or alternatively a whole new letter box and flap could be fitted. | Responsive Repairs | Alan Brooks | 2015-11-06 | RD confirm completion - order number 201553724 | 2016-03-05 | Fully Completed | Janice Wray | 2015-10-16 09:01 | 2015-11-06 09:02 | 2015-10-16 09:01 | 2016-03-07 13:45 | -21 | In target
2 RADDINGTON ROAD -2014.3.6 | 2014-03-26 11:20 | S217009860001 | RADDINGTON ROAD (2) | 136604 | Completed | 3 | Medium | Responsive Item | The buildings front door does not shut fully, it appears to be jamming at the base of the door. | I would recommend that the buildings front entrance door is looked at and adjusted so that this door shuts fully and easily. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-26 11:20 | 2014-05-25 11:21 | 2014-03-26 11:20 | 2015-11-27 21:17 | -60 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:10 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102427 | Completed | 1a | High | Responsive Item | The light switch in the electrical room has no plastic cover on it and the wires are visible. | A new light switch cover or a new complete light switch should be fitted so that a person does not electrocute themselves when turning the light on or off. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357162 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 11:10 | 2013-09-09 11:16 | 2013-08-19 11:10 | 2014-05-02 10:30 | -21 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:33 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102435 | Completed | 1c | Medium | Responsive Item | There is a small diameter black electrical running from the wall mounted electrical socket in the electrical room into flat number 4. It is not known what this cable powers or is used for. | I would recommend that the use of this cable is checked out because the occupant would not have access to the electrical room if there are any problems with this cable. | Responsive Repairs | Jackie Gaikwad | 2013-09-27 | Block Job number 201357162 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-19 11:33 | 2013-09-09 11:37 | 2013-08-19 11:33 | 2014-05-02 10:46 | -21 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:47 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102440 | Completed | 3 | Medium | Responsive Item | The wooden door of one bin cupboard is hanging off where the hinge has broken. | I would recommend that the broken door is repaired or replace. | Responsive Repairs | Jackie Gaikwad | 2013-09-27 | Block Job number 201357162 | 2014-04-25 | Fully Completed | Michael Lyons | 2013-08-19 11:47 | 2013-10-18 11:48 | 2013-08-19 11:47 | 2014-05-02 10:47 | -60 | In target
24 STADIUM STREET - 2013.12.31 | 2013-12-31 14:39 | S217005190011 | STADIUM STREET (24) | 122172 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | completed - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2013-12-31 14:39 | 2015-11-23 17:15 |  |  | 2013-12-31 14:39 | 2015-11-27 17:15 | Janice Wray
26 BURNABY STREET, LONDON - 2014.04.13 | 2014-01-31 09:36 | S217000510011 | BURNABY STREET (26) | 127329 | Completed | 1 | Low | Responsive Item | There is no cover on the light unit at the base of the staircase, the lights in the entrance hall area and on the staircase are working. | I would recommend that a new light cover is fitted to the light at the base of the staircase. | Responsive Repairs | Alex Bosman | 2016-02-16 | RMA confirmed all works complete | 2016-02-16 | Fully Completed | Maria Ares | 2014-01-31 09:36 | 2014-07-30 09:38 | 2014-01-31 09:36 | 2016-02-17 10:15 | -180 | In target
26 BURNABY STREET, LONDON - 2014.04.13 | 2014-01-31 09:39 | S217000510011 | BURNABY STREET (26) | 127330 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman | 2015-06-01 | completed - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2014-01-31 09:39 | 2016-01-18 14:50 |  |  | 2014-01-31 09:39 | 2016-01-22 14:48 | Janice Wray
27 FERNSHAW ROAD - 2014.10.14 | 2014-10-14 16:30 | S217002100004 | FERNSHAW ROAD (27) | 165359 | Completed |  | Medium | Responsive Item | I believe that the domestic smoke detector presently located on the 1st floor level landing outside flats C and D of this premises could be removed, it is not working and this type of smoke detector is not suitable to be installed in the common parts of this premises. | Copies of the London Fire Brigade home fire safety leaflets were left in this premises so that the occupants of the flats have information on domestic smoke detectors and fire safety advice | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-10-14 16:30 | 2015-04-12 16:32 | 2014-10-14 16:30 | 2015-11-25 20:30 | -180 | In target
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:55 | S217001880015 | ELM PARK GARDENS (28) | 201422 | Active | 14 | High | Responsive Item | The floor boards outside the lift motor room have been removed and not put back correctly, there are holes and gaps now in this floor surface. This could affect the fire compartmentation and is also a trip hazard. | This floor should be laid back correctly and any gaps or missing pieces of floor board replaced. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all work has been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:56 | S217001880015 | ELM PARK GARDENS (28) | 201423 | Active | 17 | Medium | Responsive Item | There is a battery operated domestic type, BS 5839 Part 6 smoke detector/sounder fitted on the third floor landing wall outside flat 8's entrance door. | I would recommend that this wall mounted battery operated domestic type, BS 5839 Part 6 smoke detector/sounder is removed. | Responsive Repairs | John Tatham
29 CHEPSTOW CRESCENT - 2015.03.17 | 2015-03-25 08:52 | S217007050002 | CHEPSTOW CRESCENT (29) | 189727 | Completed | 3 | High | Responsive Item | The self closing device fitted to this buildings main/front entrance doors does not shut this door fully, therefore allowing any persons to access the building as this door is not secured locked shut. | I would recommend that the self closing device fitted to this buildings main/front entrance doors is adjusted/repaired or replaced so that is shuts this door fully and the lock engages into the keep. Thus securing the buildings entrance door locked shut. | Responsive Repairs | John Tatham |  | works order raised | 2015-09-22 | Fully Completed | Janice Wray | 2015-03-25 08:52 | 2015-04-15 08:55 | 2015-03-25 08:52 | 2015-09-28 18:18 | -21 | In target | 2015-03-25 08:52 | 2015-10-02 18:17 | Janice Wray
29 CHEPSTOW CRESCENT - 2015.03.17 | 2015-03-25 08:55 | S217007050002 | CHEPSTOW CRESCENT (29) | 189728 | Completed | 12 | High | Responsive Item | The fire rated double doors separating the entrance hall/lobby area and the staircase do not shut in line with each other correctly. | I would recommend that these double swing double doors are inspected and checked and that the hinges are adjusted so that these doors close in line with each other. | Responsive Repairs | John Tatham |  | Works order raised | 2015-12-24 | Fully Completed | Janice Wray | 2015-03-25 08:55 | 2015-04-15 09:04 | 2015-03-25 08:55 | 2015-12-29 15:02 | -21 | In target | 2015-03-25 08:55 | 2015-12-31 15:01 | Janice Wray
29 CHEPSTOW CRESCENT - 2015.03.17 | 2015-03-25 09:04 | S217007050002 | CHEPSTOW CRESCENT (29) | 189729 | Completed | 14 | Medium | Responsive Item | There is a hole in the door frame, the top left hand corner, of the electrical cupboard/room where a cable has been pasted through and a repair not been made good. I would recommend that this hole is filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Order raised | 2015-09-22 | Fully Completed | Janice Wray | 2015-03-25 09:04 | 2015-05-24 09:07 | 2015-03-25 09:04 | 2015-09-28 18:19 | -60 | In target | 2015-03-25 09:04 | 2015-10-02 18:19 | Janice Wray
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:37 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215994 | Completed | 12 | High | Responsive Item | The entrance doors of flat 29 (TENANT) has been changed from the originally fitted fire rated door, this flat entrance door does not appear now to be fire rated. Order Number 201459788 | Can it please be confirmed if the flat entrance door of flat 29 (fitted on order number 201459788) is a self closing 30 minute fire rated door? | Responsive Repairs | Alan Brooks | 2015-10-01 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-10 15:37 | 2015-10-01 15:40 | 2015-09-10 15:37 | 2016-02-23 19:45 | -21 | In target
319 (329, 331 & 333) LADBROKE GROVE - 2015.04.22 | 2015-05-01 09:32 | S217009120041 | LADBROKE GROVE 319 A-J + | 195003 | Completed | 3 | Low | Responsive Item | There is not a steel shut off plate built into the base of the refuse chute, in the bin room. These shut off plates are fitted so that the refuse chute can be isolated from the bin room. | I would recommend that a steel shut off plate is inserted at the base of the refuse chute in the bin room so that the refuse chute can be isolated from the bin room. | Responsive Repairs | John Tatham |  | Order -201529221 | 2015-11-26 | Fully Completed | Janice Wray | 2015-05-01 09:32 | 2015-10-28 09:34 | 2015-05-01 09:32 | 2015-11-27 19:03 | -180 | In target | 2015-05-01 09:32 | 2015-12-03 19:03 | Janice Wray
32 ST CHARLES SQUARE - 2015.04.20 | 2015-04-27 14:54 | S217010080001 | ST CHARLES SQUARE (32) | 194318 | Completed | 12c | High | Responsive Item | The right hand side fire door of the double door set separating the entrance lobby from the staircase was damaged and does not close fully, so the means of escape route is not protected. | The right hand side fire door of the double door set separating the entrance lobby from the staircase should be repaired or replaced so that it closes fully. | Responsive Repairs | John Tatham | 2015-05-15 | 201526252 RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-04-27 14:54 | 2015-05-18 14:58 | 2015-04-27 14:54 | 2016-02-23 19:49 | -21 | In target | 2015-04-27 14:54 | 2016-02-29 19:48 | Janice Wray
33 ARUNDEL GARDENS - 2015.05.11 | 2015-05-16 08:49 | S217007990001 | ARUNDEL GARDENS (33) | 197388 | Active | 17 | High | Responsive Item | There is a battery operated domestic smoke detector/sounder fitted on the 2nd floor level staircase ceiling outside of flat 3's entrance door. There appears to be no battery in this domestic smoke detector and the cover is hanging off. | I would recommend that this domestic smoke detector is removed. | Responsive Repairs | John Tatham
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:36 | S217009120011 | LADBROKE GROVE (339) | 196452 | Completed | 12 | High | Responsive Item | The door of the electrical/cupboard of staircase 1 to 4 was not locked because the gerda lock appears to be damaged. | I would recommend that the door lock of this electrical room/cupboard is repaired or replaced so that this door can be kept locked shut. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-12 09:36 | 2015-06-02 09:37 | 2015-05-12 09:36 | 2016-02-02 18:35 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:37 | S217009120011 | LADBROKE GROVE (339) | 196453 | Completed | 14a | High | Responsive Item | To the upper left hand side of the electrical room/cupboard fire door in the staircase of flats 5 to 8 there is a cable hole in the wall lining where a cable has been pasted through the wall and a repair has not made good. This cable goes into the resident's storage area, again where there is another holes in the wall lining. | These holes in the wall linings should be filled in with suitable fire rated materials to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-12 09:37 | 2015-06-02 09:38 | 2015-05-12 09:37 | 2016-02-02 18:40 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:39 | S217009120011 | LADBROKE GROVE (339) | 196457 | Completed | 14b | High | Responsive Item | In the lobby area by the bin room there is a hole in the wall lining where a cable has been passed through the wall and a repair has not made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-12 09:39 | 2015-06-02 09:40 | 2015-05-12 09:39 | 2016-02-02 18:42 | -21 | In target
34 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:38 | S217001880016 | ELM PARK GARDENS (34) | 201413 | Active | 17 | Medium | Responsive Item | There is a battery operated domestic type, BS 5839 Part 6 smoke detector/sounder fitted on the third floor landing wall outside flat 8's entrance door. | I would recommend that this wall mounted battery operated domestic type, BS 5839 Part 6 smoke detector/sounder is removed. | Responsive Repairs | John Tatham
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:27 | S217009620005 | OXFORD GARDENS (34) | 103057 | Completed | 1b | Medium | Responsive Item | The lights in the ventilation unit room off the roof level lift motor room are not working. | I would recommend that an electrician checks these lights and changes the bulbs or repairs them so that they work correctly. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357242 | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-21 11:27 | 2013-10-20 11:28 | 2013-08-21 11:27 | 2014-05-06 12:34 | -60 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:38 | S217009620005 | OXFORD GARDENS (34) | 103063 | Completed | 12 | High | Responsive Item | The architrave around the door frame of the resident's storage room on the 5th floor level is missing and there are gaps between the door frame and the brickwork. | The gaps around this door frame should be filled in and architrave fitted around this door frame. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357242 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-21 11:38 | 2013-09-11 11:39 | 2013-08-21 11:38 | 2014-05-06 12:34 | -21 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:39 | S217009620005 | OXFORD GARDENS (34) | 103064 | Completed | 14 | High | Responsive Item | There is part of the rear wall of the 3rd floor level electrical cupboard missing, you can see into a residents storage cupboard at the rear of this electrical cupboard. | I would recommend that this wall is built back up so that the electrical cupboard and the residents storage cupboard are separated. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good and remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357242 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-21 11:39 | 2013-09-11 11:40 | 2013-08-21 11:39 | 2014-05-06 12:35 | -21 | In target
347 WESTBOURNE PARK ROAD - 2015.1.23 | 2015-01-30 12:00 | S217010570002 | WESTBOURNE PARK ROAD (347) | 181041 | Completed | 3 | High | Responsive Item | The self closing devise fitted to shut the gate on the staircase landing does not work correctly and shut the gate. The self closing device helps to restricts access to the building to residents and invited guests only and could reduce arson attacks. | The self closing devise fitted to the gate on the staircase landing of this building should be adjusted or repaired/replaced so that it closes the gate fully onto its stops and the gate locks shut. This will ensure the security of the staircase and therefore restrict access to authorised persons only to the flats. | Responsive Repairs | John Tatham |  | 201529239 | 2015-09-22 | Fully Completed | Janice Wray | 2015-01-30 12:00 | 2015-02-20 12:04 | 2015-01-30 12:00 | 2015-09-28 18:44 | -21 | In target | 2015-01-30 12:00 | 2015-10-02 18:44 | Janice Wray
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:37 | S217001880004 | ELM PARK GARDENS (35) | 201239 | Completed | 12b | High | Responsive Item | At the basement level where the electrical meters are located the materials used to box in the electrical meters is not fire rated and the doors of these cupboards are not lockable. | To comply with the requirements of the Building regulations the cupboards used to box in the electrical meters etc must be constructed of 30 minute fire rated materials and have locks on the doors so that they can be secured locked shut. Alternatively self closing devices can be fitted to any fire rated doors. | Responsive Repairs | John Tatham | 2015-07-13 | RD confirm completion - order number 201553790 | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-12 10:37 | 2015-07-03 10:38 | 2015-06-12 10:37 | 2016-03-07 13:48 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:48 | S217001880004 | ELM PARK GARDENS (35) | 201252 | Completed | 14 | Medium | Responsive Item | In the roof level lift and water tank rooms the wall lining of the lift motor room has been damaged. | I would recommend that this damaged wall lining is repaired. | Responsive Repairs | John Tatham | 2015-08-11 | RD confirm completion - order 201553799 | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-12 10:48 | 2015-08-11 10:49 | 2015-06-12 10:48 | 2016-03-07 13:53 | -60 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 11:47 | S217009700001 | PORTOBELLO ROAD (375) | 201073 | Completed | 12a | Medium | Responsive Item | The flat entrance door of flat 32 is damaged. (Tenanted property) | I would recommend that this flat entrance door is repaired or replaced. If it is replaced the new door should be a self closing 30 minute fire rated door complying with all of the requirements of the Building Regulations. | Responsive Repairs | John Tatham | 2015-08-31 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-06-11 11:47 | 2015-08-10 11:57 | 2015-06-11 11:47 | 2016-02-23 20:01 | -60 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 11:58 | S217009700001 | PORTOBELLO ROAD (375) | 201077 | Completed | 12b | Medium | Responsive Item | The hopper to the refuse chute on the 1st floor level above the entrance door to flat 12 is damaged and does not shut fully. | I would recommend that this refuse chute opening/hopper is repaired or replaced so that it shuts fully. | Responsive Repairs | John Tatham | 2015-06-11 | RD confirm completion - order 201553814 | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-11 11:58 | 2015-08-10 12:02 | 2015-06-11 11:58 | 2016-03-07 13:55 | -60 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:04 | S217009700001 | PORTOBELLO ROAD (375) | 201084 | Completed | 14 | High | Responsive Item | A vent is missing in the wall outside flat 19 on the balcony and the hole has been filled with newspaper and cardboard. | All the combustible material should be removed from this vent outside flat 19 and a proper cover refitted to it. Response | Responsive Repairs | John Tatham | 2016-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-11 12:04 | 2015-07-02 12:06 | 2015-06-11 12:04 | 2016-02-02 18:49 | -21 | In target
39 STONELEIGH STREET - 2014.03.06 | 2014-03-13 13:19 | S217010260003 | STONELEIGH STREET (39) | 134453 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | complete - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2014-03-13 13:19 | 2015-11-23 14:14 |  |  | 2014-03-13 13:19 | 2015-11-29 14:13 | Janice Wray
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:03 | S217007860010 | ADAIR ROAD | 201178 | Completed | 12a | High | Responsive Item | The gerda lock fitted to the lower ground floor level duct door between studios 13 and 14 has had something jammed into the lock opening. This loch cannot now be opened. | I would recommend that this gerda lock is repaired or replaced so that it can be opened correctly. | Responsive Repairs | John Tatham | 2015-07-02 | RD confirm completion - order 201553825 | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-11 16:03 | 2015-07-02 16:05 | 2015-06-11 16:03 | 2016-03-07 13:57 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:46 | S217008860001 | HESKETH PLACE (4) | 102583 | Completed | 12c | Medium | Responsive Item | Some of the linoleum floor tiles inside the front entrance door of this building are damaged and others are coming away from the floor. This could be a trip hazard. | I would recommend that floor tiles inside the buildings front entrance door are stuck back down or replace if missing so that the floor surface is not uneven. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357244 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-19 14:46 | 2013-10-18 14:47 | 2013-08-19 14:46 | 2014-05-02 10:57 | -60 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:48 | S217008860001 | HESKETH PLACE (4) | 102585 | Completed | 12d | Medium | Responsive Item | One of the upright rails of the staircase is missing on the ground floor near flat 3. | This upright rail of the staircase on the ground floor by flat 3 should be replaced. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357244 | 2014-04-23 | Fully Completed | Michael Lyons | 2013-08-19 14:48 | 2013-10-18 14:49 | 2013-08-19 14:48 | 2014-05-02 10:58 | -60 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:49 | S217008860001 | HESKETH PLACE (4) | 102590 | Completed | 14a | High | Responsive Item | There are holes in the wall and ceiling linings outside flats 5 and 8 entrance doors where cables and pipes have been pasted through and a repair not made good. | These holes in the wall and ceiling linings should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357244 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-19 14:49 | 2013-09-09 14:51 | 2013-08-19 14:49 | 2014-05-02 10:58 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:52 | S217008860001 | HESKETH PLACE (4) | 102598 | Completed | 14b | High | Responsive Item | There are pieces of duct covering missing where contractors have removed the duct work covers and not replaced them. | All missing pieces of duct work covering should be replaced. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357244 | 2014-04-22 | Fully Completed | Michael Lyons | 2013-08-19 14:52 | 2013-09-09 14:53 | 2013-08-19 14:52 | 2014-05-02 11:09 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:53 | S217008860001 | HESKETH PLACE (4) | 102601 | Active | 14c | High | Responsive Item | There is a large bunch of cables hanging down from the side of this building, these cables have not been secured correctly and they are pulling the conduit away from the wall.. | I would recommend that this large bunch of cables that are hanging down from the side of the building are re-fixed back on to the wall and also the conduit. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Site job number 201357244 Awaiting a tower erection, scaffold erected and cables temporally attached to the building. | 2014-06-13 | Partially Completed | Michael Lyons | 2013-08-19 14:53 | 2013-09-09 14:54 | 2013-08-19 14:53 | 2014-06-18 14:26 | -21 | In target | 2013-08-19 14:53 | 2014-06-24 15:27 | Janice Wray
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:55 | S217008860001 | HESKETH PLACE (4) | 102605 | Completed | 14d | Medium | Responsive Item | Cover plates have been removed in the staircase enclosure of this building from risers etc it is assumed to access cables and pipes, some of these cover plates have not been replaced correctly. | I would recommend that any of the cover plates that are not securely or correctly fitted are refitted or secured correctly. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357244 | 2014-03-28 | Fully Completed | Michael Lyons | 2013-08-19 14:55 | 2013-10-18 14:56 | 2013-08-19 14:55 | 2014-05-02 11:10 | -60 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:03 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106570 | Completed | 1 | High | Responsive Item | In the cupboard under the staircase at the lower ground floor level there are electrical wires protruding from the wall where it appears that the light unit fitted here has been removed. Shelving has been fitted in this cupboard. | Can it be confirmed that the electrical wires protruding from the wall in the lower ground floor level cupboard are not live. I would recommend that these wires are suitably contained and tied up. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357250 not sivend secured | 2014-04-04 | Fully Completed | Michael Lyons | 2013-09-18 12:03 | 2013-10-09 12:37 | 2013-09-18 12:03 | 2014-05-07 20:11 | -21 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:01 | S217010567702 | LONGLANDS COURT (49-81) | 103129 | Completed | 12a | Medium | Responsive Item | On the first and third floor levels the door/flap to opening of the rubbish chute was damaged and did not shut fully. | These doors/flaps to the rubbish chute openings should be repaired or replaced so that they shut fully. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357276 | 2014-03-28 | Fully Completed | Michael Lyons | 2013-08-21 15:01 | 2013-10-20 15:02 | 2013-08-21 15:01 | 2014-05-06 12:49 | -60 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:04 | S217010567702 | LONGLANDS COURT (49-81) | 103133 | Completed | 12b | Medium | Responsive Item | The self closing device on the door to the staircase on the fifth floor level is damaged and the door does not close fully. This appears to have been caused by the fitting of a smoke seal to this door, which is an external door. | I would recommend that the self closing device fitted to the door on the 5th floor level is repaired or replaced so that door is closed fully on to its stops. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357256 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-21 15:04 | 2013-10-20 15:06 | 2013-08-21 15:04 | 2014-05-06 13:15 | -60 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:06 | S217010567702 | LONGLANDS COURT (49-81) | 103135 | Completed | 14 | High | Responsive Item | There are holes in the wall lining over the ground floor electrical cupboard/room door where cables have been passed through and a repair has not been made good. These holes in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357256 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-21 15:06 | 2013-09-11 15:07 | 2013-08-21 15:06 | 2014-05-06 13:17 | -21 | In target
5 BURNABY STREET - 2013.12.31 | 2013-12-31 14:17 | S217000510002 | BURNABY STREET (5) | 122152 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | complete - noted for possible future upgrade | 2015-11-17 | Fully Completed | Maria Ares | 2013-12-31 14:17 | 2014-06-29 14:18 | 2013-12-31 14:17 | 2015-11-23 17:12 | -180 | In target | 2013-12-31 14:17 | 2015-11-27 17:11 | Janice Wray
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:12 | S217001880002 | ELM PARK GARDENS (5) | 102396 | Completed | 12 | High | Responsive Item | The self closing device fitted to the refuse chute room fire door on the staircase half landing 3rd to 4th floor level in the staircase of flats 21 to 40 was not working correctly therefore not shutting the door automatically fully onto its stops. | I would recommend that the self closing device fitted to this refuse chute room door is inspected and either adjusted or replaced so that the door is capable of being automatically shut fully on to its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357260 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-19 10:12 | 2013-09-09 10:23 | 2013-08-19 10:12 | 2014-05-02 10:24 | -21 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:23 | S217001880002 | ELM PARK GARDENS (5) | 102405 | Completed | 14 | High | Responsive Item | In the ground floor level riser cupboard between flats 1 and 2 parts of the floor is missing, it appears that electrical work has been undertaken in this cupboard. | I would recommend that the floor of this riser cupboard is repaired/re-laid. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357304 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-19 10:23 | 2013-09-09 10:25 | 2013-08-19 10:23 | 2014-05-02 10:24 | -21 | In target
51 - 80 EDENHAM WAY - 2015.06.16 | 2015-06-25 15:59 | S217008650002 | EDENHAM WAY (51-80) | 203412 | Completed | 1b | High | Responsive Item | The lights were not working in the roof level lift motor room at the time of this assessment. | I would recommend that the lights in lift motor room are checked and repaired or replaced so that they work correctly. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on 201552547 | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-25 15:59 | 2015-07-16 16:00 | 2015-06-25 15:59 | 2016-02-17 10:58 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:06 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204199 | Active | 1 | High | Responsive Item | None of the lights were working in the roof level lift and water tank rooms. | These lights should be checked and repaired or replaced so that they are in full working order. | Responsive Repairs | John Tatham |  |  |  |  | Cyril Morris | 2015-07-01 09:06 | 2015-07-22 09:08 |  |  | 259 | 259 days overdue
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:21 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204203 | Completed | 12a | Medium | Responsive Item | The door to the room/cupboard containing the gas meters is off its hinges, this maybe because the dry powder fire extinguisher has been hung on it. | I would recommend that this gas meter room/ cupboard door is repaired or replaced so that the door does not fall out when unlocked. | Responsive Repairs | John Tatham | 2015-08-30 | RD confirm completion- order 201553825 201553837 | 2016-03-05 | Fully Completed | Janice Wray | 2015-07-01 09:21 | 2015-08-30 09:22 | 2015-07-01 09:21 | 2016-03-07 14:01 | -60 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:24 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204206 | Completed | 14 | High | Responsive Item | There is a large hole in the basement ceiling which goes up into the ground floor level entrance hall area to the left hand side of the lift. It appears that a cable has been passed through this ceiling/floor and a repair not made good. | This hole in the ceiling/floor lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-01 09:24 | 2015-07-22 09:26 | 2015-07-01 09:24 | 2016-02-02 18:59 | -21 | In target
55 FARADAY ROAD - 2015.10.13 | 2015-10-22 12:19 | S217008710001 | FARADAY ROAD (55) | 223443 | Completed | 14 | High | Responsive Item | On the upper left hand side of the electrical room fire door there is a cable hole in the door frame where a cable has been pasted through the frame and a repair has not made good. Also part of the architrave of the door has been removed and not replaced I believe that this has been caused by a contractor installing electrical cables. | The hole in the door frame should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building and a new piece of architrave fitted around the door. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-11-12 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-10-22 12:19 | 2015-11-12 12:21 | 2015-10-22 12:19 | 2016-02-02 19:02 | -21 | In target
58 ELM PARK GARDENS - 2014.04.15 | 2014-04-22 13:48 | S217001880026 | ELM PARK GARDENS (58) | 140529 | Completed | 12 | Information Only | Responsive Item | The apartment entrance doors are not fitted with self closing devices, the entrance doors were fitted as part of the 2007/8 refurbishment and this refurbishment went through the Building Control process. | If in the future any apartment entrance doors are repaired or replace then a self closing device should be fitted to the apartment entrance door. So that it conforms to the requirements of the Building Regulations. The presently fitted entrance doors are fire rated and shut fully on to their stops. | Responsive Repairs | Michael Lyons |  |  | 2015-12-11 | Fully Completed |  |  |  | 2014-04-22 13:48 | 2015-12-14 09:14
6 ASHBURNHAM ROAD | 2013-12-31 14:32 | S217000190002 | ASHBURNHAM ROAD (6) | 122163 | Completed | 3 | Information Only | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Alex Bosman |  | complete - noted for possible future upgrade | 2015-11-17 | Fully Completed |  |  |  | 2013-12-31 14:32 | 2015-11-23 17:14 |  |  | 2013-12-31 14:32 | 2015-11-27 17:14 | Janice Wray
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:45 | S217009920001 | RUNCORN PLACE (6) | 102645 | Completed | 14 | Medium | Responsive Item | In the door frame of ground floor electrical cupboard there are 2 holes where cables have been removed and a repair has not made good. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357153 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-19 15:45 | 2013-10-18 15:46 | 2013-08-19 15:45 | 2014-05-02 11:11 | -60 | In target
6 STANLEY GARDENS - 2013.05.01 | 2013-08-15 10:32 | S217010240001 | STANLEY GARDENS (6) | 101927 | Completed | 12 | High | Responsive Item | Some of the linoleum floor tiles have come off or are coming away from the floor, especially in the stairs between the first and second floor levels. This could be a trip hazard. | I would recommend that a check is undertaken of the flooring on the landings, the stairs and in the entrance hall area and any loose or missing floor tiles are stuck back down or replace if missing. | Responsive Repairs | Jackie Gaikwad | 2013-09-05 | 201357263 | 2014-03-14 | Fully Completed | Michael Lyons | 2013-08-15 10:32 | 2013-09-05 10:33 | 2013-08-15 10:32 | 2014-04-30 11:17 | -21 | In target
60 SLAIDBURN STREET - 2014.10.14 | 2014-10-14 16:36 | S217004910001 | SLAIDBURN STREET (60) | 165362 | Completed | 14 | High | Responsive Item | There are holes in the wall lining of the wall between the cleaner's room and the corridor outside of this room, where pipes have been passed through the wall and a repair has not made. | These holes in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-12-03 | Fully Completed | Janice Wray | 2014-10-14 16:36 | 2014-11-04 16:38 | 2014-10-14 16:36 | 2015-12-04 16:53 | -21 | In target
62 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 13:23 | S217001880027 | ELM PARK GARDENS (62) | 200497 | Completed | 14 | High | Responsive Item | There are holes in the new electrical cupboard floor, located by the buildings rear exit door. | The floor of this cupboard should be fire rated and sealed completely to stop the passage of smoke and fire spread from the floor below to this floor level. | Responsive Repairs | John Tatham | 2015-06-29 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-08 13:23 | 2015-06-29 13:24 | 2015-06-08 13:23 | 2016-02-02 19:07 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 15:45 | S217002110008 | FINBOROUGH ROAD (62) | 102920 | Completed | 1a | High | Responsive Item | There are some covers missing from the light units in this building and some others are damaged. | All the light units in this building with the covers missing should have them replaced along with any damaged ones. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-20 15:45 | 2013-09-10 15:46 | 2013-08-20 15:45 | 2014-05-06 08:29 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 15:55 | S217002110008 | FINBOROUGH ROAD (62) | 102925 | Completed | 1c | High | Responsive Item | The lights in some of the refuse chute rooms worked while those in some other ones did not, some corridor lights were illuminated and others were not. | I would recommend that all of the lights in the corridors and in the refuse chute rooms are checked to see if they work correctly, could it be that some of these lights are on sensors or a timer and some are not. If this is the case the sequencing and timings should be adjusted so that there is consistency. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-20 15:55 | 2013-09-10 15:56 | 2013-08-20 15:55 | 2014-05-06 08:30 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 15:59 | S217002110008 | FINBOROUGH ROAD (62) | 102930 | Completed | 3b | High | Responsive Item | There is not a steel shut off plate built into the base of the left hand side refuse chute in the bin room, the right hand side one has one fitted. This is looking from the front of this building. The steel shut off plate is so that the refuse chute can be isolated from the bin room. | I would recommend that a steel shut off plate is inserted at the base of the left hand side refuse chute in the bin room so that the refuse chute can be isolated from the bin room. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-30 | Fully Completed | Michael Lyons | 2013-08-20 15:59 | 2013-09-10 16:00 | 2013-08-20 15:59 | 2014-05-06 08:31 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:04 | S217002110008 | FINBOROUGH ROAD (62) | 102935 | Completed | 8b | Medium | Responsive Item | There are at least three staircase or corridor window panes which are cracked or in one case 1 window is completely missing, the missing window is in a refuses chute room. | The cracked panes of glass in the windows should be placed along with the missing window. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 The glass is on order | 2014-06-06 | Fully Completed | Michael Lyons | 2013-08-20 16:04 | 2013-10-19 16:06 | 2013-08-20 16:04 | 2016-01-07 15:54 | -60 | In target | 2013-08-20 16:04 | 2014-05-10 08:18 | Janice Wray
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:07 | S217002110008 | FINBOROUGH ROAD (62) | 102936 | Completed | 1b | High | Responsive Item | There is a yellow electrical cable which runs from the lower ground floor electrical cupboard between flats 6 and 8, through the transom light area above this cupboard out through the louvered vents above the exit door and then clipped to and along the rear walls of the gardens of these flats. This cable has bulkhead lights attached to it but is cut as it passes over one of the garden gates. This yellow electrical cable is plugged into a 3 pin socket within the electrical cupboard so it is not a fixed external lighting system and because the cable is cut it does not work. | I would recommend that the reason for this cable and the lights is investigated and that they are removed. That is unless this is meant to be a permanent external lighting system and if this is the case it should be wired in correctly and cover the whole of the exterior rear walkway and just not part of it. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 This lighting system has been disabled | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-20 16:07 | 2013-09-10 16:08 | 2013-08-20 16:07 | 2014-05-06 08:33 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:08 | S217002110008 | FINBOROUGH ROAD (62) | 102937 | Completed | 12a | High | Responsive Item | The door, the door frame and the glazing in the transom light area above this door of the cleaners cupboard at the base of the right hand side staircase are damaged. | I would recommend that the whole door set of this cleaners cupboard is replaced with a 30 minute fire rated one. Or the individual components of the door set could be repaired back to a fire rated standard. | Responsive Repairs | Michael Lyons | 2014-06-30 | Block job number 201357265 The frame and door are on order RD confirm completion | 2016-02-22 | Fully Completed | Michael Lyons | 2013-08-20 16:08 | 2013-09-10 16:09 | 2013-08-20 16:08 | 2016-02-23 20:08 | -21 | In target | 2013-08-20 16:08 | 2014-05-10 08:19 | Janice Wray
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:10 | S217002110008 | FINBOROUGH ROAD (62) | 102938 | Completed | 12b | High | Responsive Item | The door frame of the cupboard at the base of the left hand side staircase is slightly damaged and a piece of non fire rated board has been inserted in the transom light area above this door. This cupboard is secured shut and presently empty. | If this cupboard remains completely empty no action is needed but if any storage is placed in this cupboard then the door frame and the transom light area must be reinstated back to be 30 minute fire rated. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-25 | Fully Completed | Michael Lyons | 2013-08-20 16:10 | 2013-09-10 16:11 | 2013-08-20 16:10 | 2014-05-06 08:35 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:11 | S217002110008 | FINBOROUGH ROAD (62) | 102940 | Completed | 12c | High | Responsive Item | All of the self closing devices fitted to the refuse chute room doors off the left hand side staircase and two of the staircase doors next to them do not close the fire doors fully onto their stops. | The self closing device fitted to these refuse chute room fire door should be adjusted, repaired or replaced so that the self closing device close the fire doors fully on to their stops. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-24 | Fully Completed | Michael Lyons | 2013-08-20 16:11 | 2013-09-10 16:12 | 2013-08-20 16:11 | 2014-05-06 08:36 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:12 | S217002110008 | FINBOROUGH ROAD (62) | 102941 | Completed | 12d | High | Responsive Item | The fire rated glazing in the corridor door by flats 9 and 10 is cracked, it is not known if this door is now a 30 minute fire rated door. | I would recommend that the glazing in this corridor door is checked to see if it is still fire rated if not it should be replaced with a new piece if possible so that the door is a self closing 30 minute fire rated door complying with all the requirements of the Building Regulations. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-20 16:12 | 2013-09-10 16:14 | 2013-08-20 16:12 | 2014-05-06 08:36 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:33 | S217002110008 | FINBOROUGH ROAD (62) | 102957 | Completed | 14a | High | Responsive Item | At the lower ground floor level in the wall from the staircase enclosure going into flat 11 there is what appears to be a vent hole being cut in the wall. This is a fire rated staircase and flats should not be vented into this area. | I would recommend that the reason for the cutting into the staircase wall brickwork is investigated and that the damaged area is repaired back to its original condition, so that fire rated of the structure of the building is maintained. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357265 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-20 16:33 | 2013-09-10 16:34 | 2013-08-20 16:33 | 2014-05-06 11:32 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:35 | S217002110008 | FINBOROUGH ROAD (62) | 102958 | Completed | 14b | High | Responsive Item | There is a hole in the door frame of the electrics cupboard at the lower ground floor level opposite where the damaged wall is in item 14a. | This hole in the door frame should be repaired/ filled in with a suitable fire rated material to maintain the fire rating of the door frame. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357265 | 2014-04-04 | Fully Completed | Michael Lyons | 2013-08-20 16:35 | 2013-09-10 16:41 | 2013-08-20 16:35 | 2014-05-06 11:32 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:41 | S217002110008 | FINBOROUGH ROAD (62) | 102961 | Completed | 14c | High | Responsive Item | There are holes in the corridor wall linings by flats 6 and 8 where pipes have been passed through the walls and repairs have not made good. T | hese holes in the wall linings should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357265 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-20 16:41 | 2013-09-10 16:43 | 2013-08-20 16:41 | 2014-05-06 11:33 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:17 | S217002110008 | FINBOROUGH ROAD (62) | 102948 | Completed | 12f | High | Responsive Item | The entrance door to flat 23 is damaged, there is a hole in the door and the transom light area has a piece of plywood screwed over it. This flat entrance door is now not fire rated. | This flat entrance door is now not fire rated because of the damaged to the door, this door should be replaced with a self closing 30 minute fire rated door and the transom light area also confirmed as being fire rated. The whole door set should comply with all the requirements of the Building Regulations. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357265 C Stokes unable to obtan access despite 3 attempts. Tennated door has been replaced and presume it is FD30 - TMO should have paperwork | 2014-05-30 | Fully Completed | Michael Lyons | 2013-08-20 16:17 | 2013-09-10 16:20 | 2013-08-20 16:17 | 2014-08-01 12:16 | -21 | In target | 2013-08-20 16:17 | 2014-08-07 12:14 | Janice Wray
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:43 | S217002110008 | FINBOROUGH ROAD (62) | 102964 | Completed | 14d | High | Responsive Item | There is a hole in the wall lining outside flat 45's entrance door. | This hole in the wall lining should be repaired with a suitable fire rated material t | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357265 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-20 16:43 | 2013-09-10 16:44 | 2013-08-20 16:43 | 2014-05-06 12:32 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:48 | S217002110008 | FINBOROUGH ROAD (62) | 102968 | Completed | 16 | High | Responsive Item | Some of the "Push Bar to Open" signs on the lower ground floor final exit doors are missing. | A "Push Bar to Open" signs should be displayed on each of the lower ground floor final exit door where at push bar to open device is fitted. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357265 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-20 16:48 | 2013-09-10 16:49 | 2013-08-20 16:48 | 2014-05-06 12:32 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 14:46 | S217002110002 | FINBOROUGH ROAD (63) | 189142 | Completed | 1 | High | Responsive Item | Above the flat entrance door of flat 6 there is a large bunch of electrical cables, some with copper wire exposed taped to a pipe. It is not known what these electrical cables are for. | I would recommend that the reason for these electrical cables is investigated and if they are needed then they are correctly enclosed and fixed to the corridor walls or if they are not required that they are removed. | Responsive Repairs | John Tatham |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2015-03-20 14:46 | 2015-04-10 14:51 | 2015-03-20 14:46 | 2015-12-14 09:18 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:09 | S217002110002 | FINBOROUGH ROAD (63) | 189158 | Completed | 12a | High | Responsive Item | There are presently only rising butt hinges fitted on the 1st and 2nd floor level refuse chute room fire doors, there are no self closing devices fitted to these two fire doors. | I would recommend that suitable over head self closing devices are fitted to the two refuse chute room fire doors so that these doors are closed automatically and fully on to the door stops. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-03-20 15:09 | 2015-04-10 15:10 | 2015-03-20 15:09 | 2015-12-02 11:27 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:11 | S217002110002 | FINBOROUGH ROAD (63) | 189159 | Completed | 12b | High | Responsive Item | It appears that the boarded transom light area of the two refuse chute room doors is not fire rated boarding, these appear to be pieces of plywood. | This boarding in the transom light areas of the 2 refuse chute rooms, on the 1st and 2nd floor level staircase landings should be replaced with fire rated boarding to maintain the fire rating of the protected staircase. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-03-20 15:11 | 2015-04-10 15:12 | 2015-03-20 15:11 | 2015-11-27 19:43 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:13 | S217002110002 | FINBOROUGH ROAD (63) | 189160 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining of the lower ground floor level electrical room, to the top right hand side of the doors. This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-03-20 15:13 | 2015-04-10 15:14 | 2015-03-20 15:13 | 2015-12-02 11:29 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:25 | S217002110003 | FINBOROUGH ROAD (65) | 189122 | Completed | 12a | High | Responsive Item | There are presently only rising butt hinges fitted on the 1st and 2nd floor level refuse chute room fire doors, there are no self closing devices fitted to these two fire doors. | I would recommend that suitable over head self closing devices are fitted to the two refuse chute room fire doors so that these doors are closed automatically and fully on to the door stops. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-03-20 14:25 | 2015-04-10 14:26 | 2015-03-20 14:25 | 2015-12-02 11:37 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:27 | S217002110003 | FINBOROUGH ROAD (65) | 189123 | Completed | 12b | High | Responsive Item | The boarded transom light area of the resident's storage cupboard next to flat 10's entrance door has holes drilled through it. This transom light area is now not fire rated. | This boarding in the transom light area of the resident's storage cupboard next to flat 10's entrance door must be replaced with a piece of fire rated boarding to maintain the fire rating of the internal corridor. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-03-20 14:27 | 2015-04-10 14:28 | 2015-03-20 14:27 | 2015-11-27 19:45 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:29 | S217002110003 | FINBOROUGH ROAD (65) | 189124 | Completed | 12c | High | Responsive Item | It appears that the boarded transom light area of the two refuse chute room doors is not fire rated boarding, these appear to be pieces of plywood. | This boarding in the transom light areas of the 2 refuse chute rooms, on the 1st and 2nd floor level staircase landings should be replaced with fire rated boarding to maintain the fire rating of the protected staircase. T | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-03-20 14:29 | 2015-04-10 14:30 | 2015-03-20 14:29 | 2015-11-27 19:47 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:31 | S217002110003 | FINBOROUGH ROAD (65) | 189126 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining of the lower ground floor level electrical room where a brick is missing. . | This brick should be replaced, the hole filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-03-20 14:31 | 2015-04-10 14:32 | 2015-03-20 14:31 | 2015-12-02 11:39 | -21 | In target
66 OXFORD GARDENS - 2015.05.06 | 2015-05-16 08:52 | S217009620007 | OXFORD GARDENS (66) | 197389 | Completed | 17 | High | Responsive Item | There is a battery operated domestic smoke detector/sounder fitted on the 2nd floor level staircase ceiling. It is not known who fitted this domestic smoke detector in this location, who is undertaking any weekly testing it? Or even if it works at all. | I would recommend that this domestic smoke detector is removed. Fitting domestic type smoke detectors/ sounders in a staircase enclosure of an apartment building, the common parts, does not meet the requirements of the Building Regulations. | Responsive Repairs | John Tatham | 2015-06-06 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-16 08:52 | 2015-06-06 08:54 | 2015-05-16 08:52 | 2016-02-02 19:23 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 13:20 | S217001880006 | ELM PARK GARDENS (67) | 102498 | Completed | 14a | High |  | There are holes in the wall linings from the ground floor electrical cupboard, next to the porter's room into the porter's room, one is hidden by the clock on the wall. This is where electrical cables have been passed through the walls by contractors and the holes not made good. | I would recommend that these holes in the wall linings are filled in using a suitable fire rated material. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all fire stopping etc has been completed. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357267 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-19 13:20 | 2013-09-09 13:37 | 2013-08-19 13:20 | 2014-05-02 10:54 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 13:37 | S217001880006 | ELM PARK GARDENS (67) | 102510 | Completed | 14b | High | Responsive Item | There are holes in the ceiling linings in both of the cupboard/access rooms up to the roof level where new light fittings have been installed and the original holes in the ceilings not made good/filled in. | I would recommend that these holes in the ceiling linings are filled in using a suitable fire rated material. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all fire stopping etc has been completed. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357267 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-19 13:37 | 2013-09-09 13:41 | 2013-08-19 13:37 | 2014-05-02 10:54 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:38 | S217001880006 | ELM PARK GARDENS (67) | 102464 | Completed | 12a | High | Responsive Item | The door handle on the double doors from the flat/lift lobby area of flats 37 to 39 is missing and there is now a hole through these fire doors. | A new handle should be fitted to these fire doors so that there is not a hole through the doors | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357269 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-19 12:38 | 2013-09-09 12:42 | 2013-08-19 12:38 | 2014-05-02 10:50 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:42 | S217001880006 | ELM PARK GARDENS (67) | 102465 | Completed | 12b | High | Responsive Item | The refuse chute door/flap opening is damaged on the 2nd to 3rd floor level in the staircase of flats 1 to 20, this flap does not now shut fully. | The door/flap opening of the rubbish chute should be repaired or replaced so that it shuts fully. | Responsive Repairs | Jackie Gaikwad | 2014-07-31 | Site job number 201357267 all rubbis chutes will be dealt with by an external contractor by 30/06 RD confirm completion | 2016-02-01 | Fully Completed | Michael Lyons | 2013-08-19 12:42 | 2013-09-09 13:19 | 2013-08-19 12:42 | 2016-02-02 19:26 | -21 | In target | 2013-08-19 12:42 | 2014-05-14 15:31 | Janice Wray
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:14 | S217010200001 | ST QUINTIN AVENUE (69) | 199064 | Active | 1b | High | Responsive Item | There are bundles of cables hanging down beside the flat entrance doors of flats 3 and 10. It is not known what these cables are for. | I would recommend that this hanging cables are connected up to whatever device that there are for and not left hanging down from the ceilings. | Responsive Repairs | John Tatham |  |  |  |  | Cyril Morris | 2015-05-28 11:14 | 2015-06-18 11:15 |  |  | 293 | 293 days overdue
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:20 | S217010200001 | ST QUINTIN AVENUE (69) | 199069 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining above flat 8's entrance door where an electrical cable has been pasted through the wall and a repair not made good. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham | 2015-06-18 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-28 11:20 | 2015-06-18 11:21 | 2015-05-28 11:20 | 2016-02-02 19:27 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:21 | S217001880003 | ELM PARK GARDENS (7) | 102454 | Completed | 12b | High | Responsive Item | The double doors of the 2nd floor flat/lift lobby area to staircase of flats 26 to 28 grounds and does not close fully or is held in the open position. | I would recommend that these doors are adjusted so that the self closing devices fitted to them can close the doors automatically and fully on to their stops. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357269 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-19 12:21 | 2013-09-09 12:23 | 2013-08-19 12:21 | 2014-05-02 10:48 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:24 | S217001880003 | ELM PARK GARDENS (7) | 102455 | Completed | 12c | High | Responsive Item | The refuse chute door/flap opening is damaged on the 5th to 6th floor level in the staircase of flats 21 to 40, this flap does not now shut fully | The door/flap opening of the rubbish chute should be repaired or replaced so that it shuts fully. | Responsive Repairs | Jackie Gaikwad | 2014-07-31 | Site job number 201357267 all refuse chutes will be dealt with by an external contractor, all additional prep works have been completed 201553908 RD confirm completed | 2016-03-05 | Fully Completed | Michael Lyons | 2013-08-19 12:24 | 2013-09-09 12:25 | 2013-08-19 12:24 | 2016-03-07 16:16 | -21 | In target | 2013-08-19 12:24 | 2014-05-14 15:30 | Janice Wray
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:26 | S217001880003 | ELM PARK GARDENS (7) | 102456 | Completed | 14 | High | Responsive Item | There are holes in the ceiling linings in both of the cupboard/access rooms up to the roof level where new light fittings have been installed and the original holes in the ceilings not made good/filled in. The ceiling by flats 38 to 40 is the worst one. | I would recommend that these holes in the ceiling linings are filled in using a suitable fire rated material. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all fire stopping etc has been completed. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357269 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-19 12:26 | 2013-09-09 12:27 | 2013-08-19 12:26 | 2014-05-02 10:49 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:02 | S217010350001 | TAVISTOCK ROAD (70-80) | 104375 | Completed | 1c | High | Responsive Item | The light unit in the 2nd floor level electrical cupboard is not working. | I would recommend that this light unit is tested by an electrician and either repaired or replaced so that it works correctly. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357270 | 2014-03-28 | Fully Completed | Michael Lyons | 2013-09-02 12:02 | 2013-09-23 12:03 | 2013-09-02 12:02 | 2014-05-07 20:01 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:33 | S217010350001 | TAVISTOCK ROAD (70-80) | 104390 | Completed | 1d | High | Responsive Item | 1d High The light unit in the potting shed is hanging off the ceiling and is not working. | I would recommend that this light unit is tested by an electrician and either repaired or replaced that it works correctly and then re-fixed back to the ceiling. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357270 | 2014-03-28 | Fully Completed | Michael Lyons | 2013-09-02 12:33 | 2013-09-23 12:34 | 2013-09-02 12:33 | 2014-05-07 20:02 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:34 | S217010350001 | TAVISTOCK ROAD (70-80) | 104391 | Completed | 1e | High | Responsive Item | The light unit in the bin room is damaged and is not working. | I would recommend that this light unit is tested by an electrician and either repaired or replaced that it works correctly. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357270 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-09-02 12:34 | 2013-09-23 12:35 | 2013-09-02 12:34 | 2014-05-07 20:02 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 13:20 | S217010350001 | TAVISTOCK ROAD (70-80) | 104422 | Completed | 14a | High | Responsive Item | There are numerous holes in the wall and ceiling linings of this building where the contractors have passed cables etc through the walls and ceilings and have not made good afterwards. In the entrance hall lobby area there are holes in the ceiling where new light units have been installed. | All the holes in the wall and ceiling linings should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that a full check of the building is undertaken before the contractors leave site. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357270 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-09-02 13:20 | 2013-09-23 13:21 | 2013-09-02 13:20 | 2014-05-07 20:04 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 13:22 | S217010350001 | TAVISTOCK ROAD (70-80) | 104424 | Completed | 14b | High | Responsive Item | There are large holes in the wall and ceiling linings in the roof space and in the externally accessed boiler room where new pipes have been fitted for the buildings heating system. | These holes in the wall and ceiling lining should be repaired/filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357270 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-09-02 13:22 | 2013-09-23 13:23 | 2013-09-02 13:22 | 2014-05-07 20:04 | -21 | In target
79 - 94 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 08:59 | S217000830006 | CHELSEA MANOR COURT 79-94 | 207290 | Completed | 14a | High | Responsive Item | Above each of the ground floor level electrical room/cupboard doors there are cable holes in the door frame and in the wall linings, some at high level where cables have been passed through the door frame and the wall lining and making good has not been undertaken. | These holes in the door frames and the wall linings should be filled in with a suitable fire rated materials to maintain the fire rating of the structural elements of this building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-08-07 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-17 08:59 | 2015-08-07 09:00 | 2015-07-17 08:59 | 2016-02-02 19:31 | -21 | In target
79 - 94 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 09:01 | S217000830006 | CHELSEA MANOR COURT 79-94 | 207291 | Completed | 14b | Medium | Responsive Item | On each landing level of each staircase light fitting have been replaced, the new light fittings are smaller than the old ones. Where the old light fittings have been removed there are holes in the ceiling lining which have not been in filled/repaired. | These holes in the ceiling linings should be filled in/repaired with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-09-15 | confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-17 09:01 | 2015-09-15 09:02 | 2015-07-17 09:01 | 2016-02-02 19:33 | -60 | In target
8 ASHBURNHAM ROAD - 2013.9.30 | 2013-10-10 15:17 | S217000190003 | ASHBURNHAM ROAD (8) | 110140 | Completed | 1 | High | Responsive Item | One of the 2 push in light switches in the entrance hall/lobby area of this building is broken and does not work. | I would recommend that this push in light switch is replaced with a new one so that the light switch turns the ceiling light on. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357271 | 2014-04-17 | Fully Completed | Michael Lyons | 2013-10-10 15:17 | 2013-10-31 15:19 | 2013-10-10 15:17 | 2014-05-07 19:58 | -21 | In target
8 ASHBURNHAM ROAD - 2013.9.30 | 2013-10-10 15:19 | S217000190003 | ASHBURNHAM ROAD (8) | 110142 | Completed |  | Low | Responsive Item | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357324 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-10-10 15:19 | 2014-04-08 15:20 | 2013-10-10 15:19 | 2014-05-07 19:58 | -180 | In target
8 DAMER TERRACE - 2014.08.14 | 2014-08-22 12:04 | S217001400005 | DAMER TERRACE (8) | 158513 | Completed | 1b | Medium | Responsive Item | The external light by the building's entrance door was not working at the time of this assessment. According to the occupants a TMO contractor came to look at this light and said that the electrical wire/supply to it had been cut. | I would recommend that the external light is repaired or replaced so that it works correctly. | Responsive Repairs | Michael Lyons |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-08-22 12:04 | 2014-10-21 12:05 | 2014-08-22 12:04 | 2015-12-14 09:08 | -60 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:58 | S217002110009 | FINBOROUGH ROAD (80) | 122193 | Completed | 14 | High | Responsive Item | There are holes in the ceiling lining of the first floor landing where a new light fitting has been installed and the old securing holes of the old light unit have not been filled in. | These holes in the ceiling lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2013-12-31 14:58 | 2014-01-21 15:00 | 2013-12-31 14:58 | 2015-11-27 19:59 | -21 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 15:00 | S217002110009 | FINBOROUGH ROAD (80) | 122194 | Completed | 15 | High | Emergency Lighting | The covers of two of the emergency lighting units currently installed in the building are dirty, thus affecting the level of illuminating from the bulb and you cannot see the charger indicator light clearly. | I would recommend that the covers of the 2 older emergency lighting units are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of the lights. | Responsive Repairs | Alex Bosman |  | INSPECTED LIGHTS AND FOUND ALL TO BE IN GOOD ORDER | 2015-11-17 | Fully Completed | Maria Ares | 2013-12-31 15:00 | 2014-01-21 15:01 | 2013-12-31 15:00 | 2015-11-18 13:19 | -21 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:04 | S217010567703 | LONGLANDS COURT (82-87) | 103427 | Completed | 14a | High | Responsive Item | There are holes in the wall lining over the lower ground floor electrical room door and a brick is missing, where cables have been passed through and a repair has not been made good. | These holes in the wall lining should be filled in with a suitable fire rated material and the brick replaced to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357272 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-23 10:04 | 2013-09-13 10:06 | 2013-08-23 10:04 | 2014-05-06 14:45 | -21 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:06 | S217010567703 | LONGLANDS COURT (82-87) | 103429 | Completed | 14b | High | Responsive Item | There is a hole in the lower ground floor level electrical room door frame, where a cable has been passed through and a repair has not been made good. | This hole in the electrical room door frame should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357272 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-23 10:06 | 2013-09-13 10:07 | 2013-08-23 10:06 | 2014-05-06 14:47 | -21 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:17 | S217010567704 | LONGLANDS COURT (88-93) | 103106 | Completed | 1a | High | Responsive Item | The lights do not appear to be working in the lower ground floor resident's storage area between the electrical room and the bin store internal door. | I would recommend that the lights in this area are checked and repaired or replaced so that there is artificial light in this enclosed lower ground floor level area. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357275 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-21 14:17 | 2013-09-11 14:18 | 2013-08-21 14:17 | 2014-05-06 12:46 | -21 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:19 | S217010567704 | LONGLANDS COURT (88-93) | 103108 | Completed | 3 | High | Responsive Item | The fire fighter entry over ride devicefitted to the entrance door of this building did not function and release the locking device on the door and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride device fitted to the entrance door of this building should be repaired or replaced so that it releases the locking device fitted to the buildings entrance door. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357275 Working | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-21 14:19 | 2013-09-11 14:21 | 2013-08-21 14:19 | 2014-05-06 12:46 | -21 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:41 | S217010567704 | LONGLANDS COURT (88-93) | 103116 | Completed | 14 | High | Responsive Item | There are holes in the wall lining over the lower ground floor electrical room door where cables have been passed through and a repair has not been made good. | These holes in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | 201529236 | 2015-09-22 | Fully Completed | Janice Wray | 2013-08-21 14:41 | 2013-09-11 14:42 | 2013-08-21 14:41 | 2015-09-28 18:35 | -21 | In target | 2013-08-21 14:41 | 2015-10-02 18:34 | Janice Wray
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:04 | S217001880008 | ELM PARK GARDENS (93) | 102485 | Completed | 12a | High | Responsive Item | The self closing device fitted to the refuse chute room fire door on the staircase half landing 2nd to 3rd floor level in the staircase of flats 1 to 20 was not working correctly therefore not shutting the door automatically fully onto its stops. | I would recommend that the self closing device fitted to this refuse chute room door is inspected and either adjusted or replaced so that the door is capable of being automatically shut fully on to its stops. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357277 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-19 13:04 | 2013-09-09 13:06 | 2013-08-19 13:04 | 2014-05-02 10:51 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:06 | S217001880008 | ELM PARK GARDENS (93) | 102486 | Completed | 12b | High | Responsive Item | The double doors of the 6th floor flat/lift lobby area to staircase of flats 18 to 20 grounds and does not close fully or is held in the open position. | I would recommend that these doors are adjusted so that the self closing devices fitted to them can close the doors automatically and fully on to their stops. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357277 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-19 13:06 | 2013-09-09 13:07 | 2013-08-19 13:06 | 2014-05-02 10:53 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:08 | S217001880008 | ELM PARK GARDENS (93) | 102488 | Completed | 12c | High | Responsive Item | The refuse chute door/flap openings are damaged in the right hand side staircase, flats 21 to 40 on the half landings above the 2nd, 3rd and 4th floor levels, these flaps do not now shut fully. | These door/flap openings of the rubbish chute should be repaired or replaced so that they shut fully. | Responsive Repairs | Jackie Gaikwad | 2014-07-31 | Site job number 201357277 All refuse chutes will be dealt with by an external contractor by 31/07, all prep works have been carried out Order 201553917. RD confirm completion | 2016-03-05 | Fully Completed | Michael Lyons | 2013-08-19 13:08 | 2013-09-09 13:09 | 2013-08-19 13:08 | 2016-03-07 16:20 | -21 | In target | 2013-08-19 13:08 | 2014-05-14 15:32 | Janice Wray
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 14:57 | S217009120002 | LADBROKE GROVE (94) | 101764 | Completed | 12b | High | Flat Door | The entrance door to flat 4 appears to have been changed from the originally door fitted and the area to the right of the door has been boarded up. | Can it be confirmed the entrance door to this flat is a 30 minute fire rated door fitted with a self closing devices capable of shutting the door fully on to its stops. Can it also be confirmed if the boarding to the right of the entrance door is 30 minute fire rated? If it is not or the screen it is coving is not it must be replaced with 30 minute fire rated materials immediately. | Responsive Repairs | Jackie Gaikwad | 2013-09-04 | Assessed by Carl Stokes on 23rd Jan 2014 - door COMPLIANT but unable to confirm whether side screen compliant so recommendation to add extra lining panel (fire -rated supalux or equivalent) referred to Response Repairs Manager. Works completed - fire-rated boarding installed. | 2015-02-24 | Fully Completed | Janice Wray | 2013-08-14 14:57 | 2013-09-04 15:03 | 2013-08-14 14:57 | 2015-03-05 15:46 | -21 | In target | 2013-08-14 14:57 | 2014-02-03 13:17 | Janice Wray
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:29 | S217010567705 | LONGLANDS COURT (94-102) | 103377 | Completed | 12a | Medium | Responsive Item | The door to the bin room is old and it is not known if this is a fire rated door, it does not have a self closing device fitted to it. | I would recommend that a new self closing 30 minute fire rated door is fitted to the lower ground floor level bin room. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357281 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-22 16:29 | 2013-10-21 16:31 | 2013-08-22 16:29 | 2014-05-06 14:23 | -60 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:32 | S217010567705 | LONGLANDS COURT (94-102) | 103378 | Completed | 14 | High | Responsive Item | The transom light area of the central corridor door at the lower ground floor level by the electrical room at the base of the right hand side staircase is not fire rated. This is because there are gaps and holes in the boarding where cables and ducts have been passed through it. | This transom light area over the central corridor doors at the lower ground floor level by the electrical room should be replaced with 30 minute fire rated boarding fully sealed. The base of this staircase should be fully fire protected. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357281 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-22 16:32 | 2013-09-12 16:33 | 2013-08-22 16:32 | 2014-05-06 14:44 | -21 | In target
96 - 98 BLENHEIM CRESCENT - 2015.06.16 | 2015-06-26 13:00 | S217008160001 | BLENHEIM CRESCENT (96) | 203599 | Completed | 14 | High | Responsive Item | In the door frame of ground floor electrical room of number 96 there is a hole where a cables has been removed and a repair has not made good. This hole could allow the passage of smoke and down grades the fabric of the building's structure. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-08-14 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-06-26 13:00 | 2015-07-17 13:01 | 2015-06-26 13:00 | 2016-02-23 20:13 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 09:29 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214834 | Completed | 1 | High | Responsive Item | On the 2nd floor levels in the lift lobby areas the covers of the wall mounted electrical boxes have the padlocks missing or the locks on the boxes are damaged. This means that these electrical cables etc inside the boxes are not secure. | I would recommend that all the wall mounted electrical boxes in the 2nd floor levels lift lobby areas are fitted with locks or padlocks so that they are secure. | Responsive Repairs | Alan Brooks | 2015-09-25 | Order 201553930. RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-04 09:29 | 2015-09-25 09:31 | 2015-09-04 09:29 | 2016-03-07 16:23 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 09:31 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214835 | Completed | 3 | High | Responsive Item | The fire fighter entry over ride device fitted to the entrance gate by flat 101 did not function and release the locking device and open the gate. | The fire fighter entry over ride device fitted to the entrance gate by flat 101 should be repaired or replaced so that it releases the locking device fitted to the door. | Responsive Repairs | Alan Brooks | 2016-02-16 | S&M tested; confirmed all working 27.1.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2015-09-04 09:31 | 2015-09-25 09:32 | 2015-09-04 09:31 | 2016-02-17 10:59 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 09:35 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214839 | Completed | 12a | High | Responsive Item | Nearly all of the fire rated self closing doors on the refuse chute rooms or at the head of the staircases have damaged self closing devices or hinges. Therefore these doors will not close fully of shut automatically. | I would recommend that all of the fire rated self closing doors on the refuse chute rooms or at the head of the staircases are checked to see if they are functioning correctly. If they are not then the self closing devices or the hinges should be either adjusted, repaired or replaced so that the doors are capable of being automatically shut fully on to their stops. | Responsive Repairs | Alan Brooks | 2015-08-25 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-04 09:35 | 2015-09-25 11:26 | 2015-09-04 09:35 | 2016-02-23 20:15 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 11:26 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214892 | Completed | 12b | High | Responsive Item | There is clear glass in some of the staircase fire doors at the 2nd floor level and in some of the refuse chute room doors is fire rated glazing. This glass in not marked as fire rated glazing. | Can it be confirmed by the contractor or a TMO surveyor that the clear glazing in some of the glazed areas of the fire doors in this building is fire rated glass. If it is not fire rated glazing then this clear glass should be replaced with fire rated glassing so that the integrity of the protected staircase enclosure is maintained. | Responsive Repairs | Alan Brooks | 2015-09-25 | Order 201553822. RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-04 11:26 | 2015-09-25 11:28 | 2015-09-04 11:26 | 2016-03-07 16:25 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 11:28 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214893 | Completed | 12c | Medium | Responsive Item | The letter box is damaged and the flap missing from flat 211's entrance door. TENANTED FLAT | I would recommend that a new letter box is fitted to this door. | Responsive Repairs | Alan Brooks | 2015-11-03 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-04 11:28 | 2015-11-03 11:29 | 2015-09-04 11:28 | 2016-02-23 20:17 | -60 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:04 | S217007970002 | ADAIR TOWER | 133534 | Completed | 12a | High | Responsive Item | The occupants of flat 42 have fitted a security camera outside their flat entrance door with the cable of the camera passing through the door frame. There is now a hole through this door frame. | I would recommend that the hole through the door frame of this flat entrance door is sealed up with a fire rated material so that the fire rating and protection to the flat/lift lobby area is maintained. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 11:04 | 2014-03-28 11:06 | 2014-03-07 11:04 | 2015-11-12 15:59 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:07 | S217007970002 | ADAIR TOWER | 133538 | Completed | 12b | High | Responsive Item | The fire rated glass in the following fire doors or side screens next to flat entrance doors is cracked or damaged. 1. Roof level by the dry riser outlet. 2. Side screen of flat 1 3. Side screen of flat 14 | These damaged pieces of fire rated glazing should be replaced with new fire rated glazing. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-07 11:07 | 2014-03-28 11:08 | 2014-03-07 11:07 | 2015-11-27 20:38 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:09 | S217007970002 | ADAIR TOWER | 133541 | Completed | 12c | High | Responsive Item | On floor levels 4 and 13 the hoppers/flaps to rubbish chutes are damaged and do not shut fully | The hoppers/flaps to the rubbish chutes openings on these levels should be repaired or replaced so that they shut fully. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 11:09 | 2014-03-28 11:09 | 2014-03-07 11:09 | 2015-11-12 16:01 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:12 | S217007970002 | ADAIR TOWER | 133545 | Completed | 12e | Low | Responsive Item | The flap is missing from the letter box of flat 10 and the letter box is damaged, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that a new letter box and flap is fitted to the flat entrance door of flat 10 so that the compartmentation of the protected staircase is maintained. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-07 11:12 | 2014-09-03 11:13 | 2014-03-07 11:12 | 2015-11-27 20:40 | -180 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:15 | S217007970002 | ADAIR TOWER | 133548 | Completed | 12g | Information Only | Flat Door | Flat 38 is presently a void area and has been secured by the use of a steel door over the flat entrance door by the TMO. | If a new flat entrance door is fitted to this flat it should be a self closing 30 minute fire rated door. | Responsive Repairs | Alex Bosman | 2014-09-15 | complete - works to be completed during void works | 2015-11-17 | Fully Completed |  |  |  | 2014-03-07 11:15 | 2016-01-18 14:55 |  |  | 2014-03-07 11:15 | 2016-01-22 14:54 | Janice Wray
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:16 | S217007970002 | ADAIR TOWER | 133549 | Completed | 16a | High | Responsive Item | The "Push Bar to Open" signs on the ground floor final exit door at the base of the staircase is missing. | A "Push Bar to Open" signs should be displayed on the ground floor final exit door of the protected staircase. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 11:16 | 2014-03-28 11:18 | 2014-03-07 11:16 | 2015-11-12 16:03 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:18 | S217007970002 | ADAIR TOWER | 133551 | Completed | 16b | High | Signage | The floor number sign is missing from the flat/lift lobby area of floor level 3. | A new floor number sign should be fitted to the wall opposite the lifts on this floor level. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-07 11:18 | 2014-03-28 11:23 | 2014-03-07 11:18 | 2015-11-27 20:41 | -21 | In target
ADELAIDE HOUSE - 2015.02.26 | 2015-03-27 08:34 | S217012270004 | ADELAIDE HOUSE | 190113 | Completed | 14 | High | Responsive Item | There is a brick missing from the wall above the electrical room door where a cable has been passed through the wall and the wall has not been made good. | This brick and the hole should be filled in with suitable fire rated materials to maintain the fire rating of the structure of this building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | hole bricked up, 0.5m2 201526204 | 2015-09-16 | Fully Completed | Janice Wray | 2015-03-27 08:34 | 2015-04-17 08:35 | 2015-03-27 08:34 | 2015-09-21 16:27 | -21 | In target
AGNES HOUSE - 2014.08.14 | 2014-08-20 10:47 | S217010050010 | AGNES HOUSE | 158167 | Completed | 12b | High | Flat Door | The flat entrance door to flat 8 has been changed from the originally fitted fire rated door, the presently fitted flat entrance door has a piece of clear glass in it and there is a gap at the head of the door, between the door and the door frame. This is a tenanted flat. | I would recommend that the occupier of this flat is asked to confirm with documentation that the flat entrance door is a self closing 30 minute fire rated door with cold smoke seals etc complying with the requirements of the Building Regulations? Did we fit this? | Responsive Repairs | Michael Lyons |  | new FC30 door perko, smoke seals fitted, 201526219 | 2015-09-16 | Fully Completed | Janice Wray | 2014-08-20 10:47 | 2014-09-10 10:49 | 2014-08-20 10:47 | 2015-09-21 16:51 | -21 | In target
AGNES HOUSE - 2014.08.14 | 2014-08-20 10:55 | S217010050010 | AGNES HOUSE | 158172 | Completed | 12c | High | Flat Door | The flat entrance door to flat 8 has been changed from the originally fitted fire rated door, the presently fitted flat entrance door has a piece of clear glass in it and there is a gap at the head of the door, between the door and the door frame. This is a tenanted flat. | This flat door is badly fitted with a gap between the door and door frame at the top of the door. This door should be repaired by a competent person or a new door fitted, Please also see item 12b | Responsive Repairs | Michael Lyons | 2014-09-26 | 201553833 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-08-20 10:55 | 2014-09-10 10:57 | 2014-08-20 10:55 | 2016-03-07 16:32 | -21 | In target
ALLOM HOUSE - 2014.4/10 | 2014-04-11 10:53 | S217008370002 | ALLOM HOUSE | 139523 | Completed |  | High | Flat Door | The glazing in the transom light above the entrance door of flat 18 does not appear to be fire rated | Can this glazing be checked by a suitably qualified contractor to ascertain if it is fire rated.If not, can it be replaced with a suitable fire rated material so that the integrity of the protected staircase is maintained | Responsive Repairs | Michael Lyons |  | Works order raised - 201526221 | 2015-12-11 | Fully Completed | Janice Wray | 2014-04-11 10:53 | 2014-05-02 11:00 | 2014-04-11 10:53 | 2015-12-14 15:59 | -21 | In target | 2014-04-11 10:53 | 2015-12-18 15:58 | Janice Wray
ALLOM HOUSE - 2015.04.20 | 2015-04-27 16:47 | S217008370002 | ALLOM HOUSE | 194386 | Completed | 12b | High | Responsive Item | The letter box flap is missing from the entrance door of flat 8, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that this letter box flap is replaced or a new letter box fitted. | Responsive Repairs | John Tatham |  | Completed | 2015-09-16 | Fully Completed | Janice Wray | 2015-04-27 16:47 | 2015-05-18 16:48 | 2015-04-27 16:47 | 2015-09-21 16:54 | -21 | In target
ALLOM HOUSE - 2015.04.20 | 2015-04-27 16:49 | S217008370002 | ALLOM HOUSE | 194388 | Completed | 12C | High | Responsive Item | The refuse chute hoppers/flap will not shut fully on the refuse chute openings on the staircase half landings above flats 19 and 20, also above flats 37 and 38. | I would recommend that these hopper/flap openings of the rubbish chute are inspected and then repaired or replaced so that they shut fully. | Responsive Repairs | John Tatham |  | 201526221 await start date | 2015-11-11 | Fully Completed | Janice Wray | 2015-04-27 16:49 | 2015-05-18 16:52 | 2015-04-27 16:49 | 2015-11-12 16:08 | -21 | In target | 2015-04-27 16:49 | 2015-11-18 16:08 | Janice Wray
ALLOM HOUSE - 2015.04.20 | 2015-04-27 16:54 | S217008370002 | ALLOM HOUSE | 194393 | Completed | 14a | High | Responsive Item | The cover plate of the duct/service riser on the staircase half landing above flats 29 and 30 has been removed and not put back correctly. | I would recommend that this cover plate is fixed back correctly. | Responsive Repairs | John Tatham |  | Works order raised - 201526221 | 2015-11-11 | Fully Completed | Janice Wray | 2015-04-27 16:54 | 2015-05-18 16:55 | 2015-04-27 16:54 | 2015-11-12 16:10 | -21 | In target | 2015-04-27 16:54 | 2015-11-18 16:09 | Janice Wray
ANCHOR HOUSE -2015.02.28 | 2015-02-03 11:08 | S217012760008 | ANCHOR HOUSE | 181539 | Completed | 14 | Medium | Responsive Item | There is hole in the wall lining above the right hand side of the electrical room/cupboard door where a cable has been removed. | I would recommend that this hole is in filled with a suitable fire rated material so that the fire rating of the structure of the building is maintained. I would recommend that in future checks are carried out after contractors have undertaken work in this building. | Responsive Repairs | John Tatham |  |  | 2015-09-22 | Fully Completed | Janice Wray | 2015-02-03 11:08 | 2015-04-04 11:11 | 2015-02-03 11:08 | 2015-09-28 17:47 | -60 | In target
APOLLO HOUSE - 2015.01.28 | 2015-02-03 11:33 | S217012760010 | APOLLO HOUSE | 181560 | Completed | 12a | High | Responsive Item | The flat entrance door of flat 16 is damaged, there is a hole straight through the door where the lock has been removed and the letter box is completely missing so again there is a large hole straight through this door. | A new lock and letter box should be fitted to this flat entrance door or a new self closing 30 minute fire rated door (FD30s) could be fitted, complying with the requirements of the Building Regulations. | Responsive Repairs | John Tatham |  | Surveys carried out 22 & 23/10/15 with work to commence on site 26/10/15 | 2015-10-27 | Fully Completed | Janice Wray | 2015-02-03 11:33 | 2015-02-24 11:34 | 2015-02-03 11:33 | 2015-10-28 14:50 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-01 16:49 | S217008190003 | APPLEFORD HOUSE 1-12 | 204389 | Completed | 1 | High | Responsive Item | The lights at the end of this building under flats 3 and 4 at the lower ground floor level were not working. | I would recommend that the lights in this area of the building are checked then repaired or replaced so that they are working correctly. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on201552551 | 2016-02-16 | Fully Completed | Maria Ares | 2015-07-01 16:49 | 2015-07-22 16:50 | 2015-07-01 16:49 | 2016-02-17 11:00 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-01 16:51 | S217008190003 | APPLEFORD HOUSE 1-12 | 204391 | Completed | 3a | High | Responsive Item | The fire fighter entry over ride device fitted to the entrance door of the staircase of flats 1 to 8 at the lower ground floor level did not function and release the locking device and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | This fire fighter entry over ride device should be repaired or replaced so that it releases the locking device fitted to this door. | Responsive Repairs | John Tatham | 2016-02-16 | S&M tested; confirmed all working 27.1.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2015-07-01 16:51 | 2015-07-22 16:52 | 2015-07-01 16:51 | 2016-02-17 11:01 | -21 | In target
ARCHER HOUSE - 2015.02.26 | 2015-03-27 11:38 | S217012270001 | ARCHER HOUSE | 190174 | Completed | 14a | High | Responsive Item | To the upper left hand side of the under staircase electrical cupboard door of the staircase of flats 1 to 8 there is a hole in the wall linings where cable have been passed through the wall and a repair has not made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in this building. | Responsive Repairs | John Tatham |  | Works order raised - 201526225 | 2015-09-22 | Fully Completed | Janice Wray | 2015-03-27 11:38 | 2015-04-17 11:39 | 2015-03-27 11:38 | 2015-09-28 17:50 | -21 | In target | 2015-03-27 11:38 | 2015-10-02 17:50 | Janice Wray
ARCHER HOUSE - 2015.02.26 | 2015-03-27 11:40 | S217012270001 | ARCHER HOUSE | 190177 | Completed | 14b | Medium | Responsive Item | There appears to be an air brick in the compartment wall between the bin storage area and the electrical room of the staircase of flats 1 to 8 that could allow the passage of flames and smoke between the 2 areas. | This wall between the bin area and the electrical room/cupboard should be made a minimum of 30 minutes fire rated so fire separating these 2 areas. | Responsive Repairs | John Tatham |  | Works order raised - 201526225 | 2015-09-23 | Fully Completed | Janice Wray | 2015-03-27 11:40 | 2015-05-26 11:41 | 2015-03-27 11:40 | 2015-09-28 17:52 | -60 | In target | 2015-03-27 11:40 | 2015-10-02 17:51 | Janice Wray
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:37 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101951 | Completed | 8c | Low | Responsive Item | The doors of the single riser cupboards on the 13th and 16th floor levels can not be opened.. | I would recommend that the locks fitted to these cupboard doors are repaired or replaced so that the doors can be opened. | Responsive Repairs | Jackie Gaikwad | 2013-10-31 | 201357271 | 2014-03-20 | Fully Completed | Michael Lyons | 2013-08-15 11:37 | 2014-02-11 11:38 | 2013-08-15 11:37 | 2014-04-30 11:20 | -180 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:43 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101957 | Completed | 12a (tenants doors) | High | Flat Door | The entrance doors to flat 15 has been changed after this flat entrance door was damaged in an incident, the TMO is aware of these incidents and a temporary entrance door was installed until new replacement door could be fitted. This temporary flat entrance door is not fire rated and does not have a self closing device fitted to it. | I would recommend that this temporary flat entrance door is replaced immediately with self closing certified 30 minute fire rated doors complying to all the requirements of the Building Regulations. | Responsive Repairs | Jackie Gaikwad | 2013-09-04 | This needs to be passed to the FRA as the door needs to be assessed. Referred to Carl Stokes to contact tenant and arrangemet assessment - 1st May 2014 Door & sidescreen assessed by C Stokes 13th May - sidescreen compliant but door still a temporary door non_compliant - needs to be replaced with A SELF-CLOSING FD 30 asap 201553845 - RD confirm completion | 2016-03-05 | Fully Completed | Michael Lyons | 2013-08-15 11:43 | 2013-09-05 11:47 | 2013-08-15 11:43 | 2016-03-07 16:39 | -21 | In target | 2013-08-15 11:43 | 2016-03-12 16:34 | Janice Wray
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 12:06 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101977 | Completed | 12c | High | Responsive Item | The flat/lift lobby area to staircase door on the 4th floor level is damaged and does not close fully. | This 4th floor level flat/lift lobby area to staircase door should be repaired or replaced so that the door is a full fire rated door and that it closes fully on to its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-05 | 201357138 RD Job number job completed | 2014-04-21 | Fully Completed | Michael Lyons | 2013-08-15 12:06 | 2013-09-05 12:08 | 2013-08-15 12:06 | 2014-05-01 09:04 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 12:08 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101978 | Completed | 12f | High | Responsive Item | The self closing devices fitted to the flat/lift lobby area fire doors on to the staircase on the 1stand 2nd floor levels need adjusting or replacing so that they shut the fire doors fully. | The self closing device on these fire doors should be adjusted, repaired or replaced so that the door shuts fully onto their stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-05 | Job number 201357271 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-15 12:08 | 2013-09-05 12:53 | 2013-08-15 12:08 | 2014-05-02 09:57 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 12:53 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101994 | Completed | 14 | High | Responsive Item | There are holes in the boarding or the boarding is missing above the riser cupboard doors on the 1st floor level where contractors have passed cables through these areas and not made good. | I would recommend that the missing pieces of boarding are replaced and any holes are filled in with a suitable material above the doors of these 1st floor level cupboard doors. | Responsive Repairs | Jackie Gaikwad | 2013-09-05 | Job Number 201357272 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-15 12:53 | 2013-09-05 12:55 | 2013-08-15 12:53 | 2014-05-02 09:58 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 12:58 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101998 | Completed | 16 | Medium | Miscellaneous | The floor level and flat numbers signs are missing from the staircase landings on floor levels, 1, 2 and 4. Also the sign on the flat/lift lobby area of the 14th floor level is damaged These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that the floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-10-04 | 201357287 Block Job number | 2014-04-30 | Fully Completed | Michael Lyons | 2013-08-15 12:58 | 2013-10-14 13:00 | 2013-08-15 12:58 | 2014-05-02 10:00 | -60 | In target
ASTON HOUSE - 2015.02.2015 | 2015-03-27 11:55 | S217012270002 | ASTON HOUSE | 190193 | Completed | 14 | High | Responsive Item | To the upper left hand side of each under staircase cupboards door there are holes in the wall linings where cable have been passed through the wall and a repair has not made good. | These holes in the wall linings should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Works order raised - 201529203 | 2015-09-22 | Fully Completed | Janice Wray | 2015-03-27 11:55 | 2015-04-17 11:56 | 2015-03-27 11:55 | 2015-09-28 17:54 | -21 | In target | 2015-03-27 11:55 | 2015-10-02 17:54 | Janice Wray
BALFOUR HOUSE - 2015.07.27 | 2015-09-02 11:41 | S217010080004 | BALFOUR HOUSE 1-8 | 214490 | Completed | 12a | High | Responsive Item | The flat entrance door to flat 4 is damaged and the letter box is hanging off the door. | I would recommend that a new self closing 30 minute fire rated door, complying with all the requirements of the Building Regulations is fitted. | Responsive Repairs | Alan Brooks | 2015-09-23 | order 201553853 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-02 11:41 | 2015-09-23 11:43 | 2015-09-02 11:41 | 2016-03-07 16:50 | -21 | In target
BALFOUR HOUSE - 2015.07.27 | 2015-09-02 12:10 | S217010080002 | BALFOUR HOUSE | 214509 | Completed | 12e | Medium | Responsive Item | A flat entrance door fitted to flat 5 has a cat flap in it, the present tenant does not own a cat, this cat flap was put in this flat door by the previous occupant I believe. | I would recommend that a new self closing 30 minute fire rated door, fitted with cold smoke seals and intumescent strips and complying with all the requirements of the Building Regulations is fitted as the cat flap in this door makes it not fire rated. | Responsive Repairs | Alan Brooks | 2015-11-02 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-02 12:10 | 2015-11-01 12:16 | 2015-09-02 12:10 | 2016-02-23 20:19 | -60 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 14:05 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 171953 | Completed | 1a | Medium | Miscellaneous | The covers of some of the lighting units in the buildings are dirty, thus affecting the level of illuminating from the bulb. | I would recommend that the covers of the lighting units in the buildings are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircases and on the balconies. | Responsive Repairs | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2014-11-28 14:05 | 2015-01-27 14:07 | 2014-11-28 14:05 | 2015-11-18 13:42 | -60 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:32 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172040 | Completed | 19c | High | Dry or Wet Riser | Some of the padlocks securing/locking the boxes housing the water main and the dry riser outlets in the Baseline area at the lower ground floor level are missing or not Fire Brigade (FB) padlocks. | The boxes housing the water main and the dry riser outlets should be checked and any found not secured or without FB padlocks fitted to them should be fitted with and secured with FB padlocks only. As the Baseline area is a secure area vandalism of the installed fixed fire system is not a problem. Could FB padlocks please be fitted to all riser inlet / outlets please | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-11-28 15:32 | 2014-12-19 15:34 | 2014-11-28 15:32 | 2015-11-12 16:21 | -21 | In target
BARLOW HOUSE - 2014.4.7 | 2014-04-11 10:01 | S217010470001 | BARLOW HOUSE | 139485 | Completed |  | High | Responsive Item | The glazing in the transom lights above the entrance door to flats 26,28 and 29 does not appear to be fire rated. | These should be checked by a suitably qualified contractor to ascertain if the glazing is fire rated. If not, it should be replaced with a suitable fire rated material so that the integrity of the protected staicase is maintained | Responsive Repairs | Michael Lyons |  | RD state "the glazing doors and frame have been all upgraded when fitted by contractor, we are unable to get a copy of the spec. " | 2015-09-22 | Fully Completed | Janice Wray | 2014-04-11 10:01 | 2014-05-02 10:05 | 2014-04-11 10:01 | 2015-09-28 18:04 | -21 | In target | 2014-04-11 10:01 | 2015-10-02 18:04 | Janice Wray
BARLOW HOUSE - 2014.4.7 | 2014-04-11 10:14 | S217010470001 | BARLOW HOUSE | 139493 | Completed |  | High | Flat Door | The entrance doors to flats 10,26,28 & 29 have been changed from the original fitted door | Can it be confirmed that these doors are 30 minute fire rated doors fitted with a self closing device, capable of shutting the door fully on to its stops? If you require Carl Stokes to return to access these flats, can you please refer this back to H&S | Responsive Repairs | Michael Lyons |  | Flat 10 no access. Flat 26/28/29 doors are FC30 with multi lock systems and perkos, ( so are unable to have smoke seals fitted) | 2015-09-22 | Fully Completed | Janice Wray | 2014-04-11 10:14 | 2014-05-02 10:18 | 2014-04-11 10:14 | 2015-09-28 18:05 | -21 | In target | 2014-04-11 10:14 | 2015-10-02 18:05 | Janice Wray
BARLOW HOUSE - 2015.04.20 | 2015-04-27 15:47 | S217010470001 | BARLOW HOUSE | 194352 | Completed | 12c | High | Responsive Item | The letter box flap is missing from the entrance door of flat 30, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that this letter box flap is replaced or a new letter box fitted. | Responsive Repairs | John Tatham |  | Letter box renewed - COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-04-27 15:47 | 2015-05-18 15:48 | 2015-04-27 15:47 | 2015-09-21 16:56 | -21 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:22 | S217012740002 | BERENGER TOWER 1-51 | 102374 | Completed | 8c | Medium | Responsive Item | There is no lock fitted to the single riser cupboard door on the 6th flat/lift lobby area. | A lock should be fitted to this riser cupboard door. | Responsive Repairs | Jackie Gaikwad | 2013-09-27 | Block Job number 201357290 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-08-19 09:22 | 2013-10-18 09:32 | 2013-08-19 09:22 | 2014-05-02 10:17 | -60 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:32 | S217012740002 | BERENGER TOWER 1-51 | 102376 | Completed | 8d | Low | Responsive Item | The double doors of the riser cupboards on the 5th and 11th floor level flat/lift lobby areas and the single doors on the 3rdand 17th floor levels will not open. | I would recommend that the locks fitted to these cupboard doors are repaired or replaced so that the doors open easily. | Responsive Repairs | Jackie Gaikwad | 2014-02-03 | Block Job number 201357290 | 2014-03-27 | Fully Completed | Michael Lyons | 2013-08-19 09:32 | 2014-02-15 09:34 | 2013-08-19 09:32 | 2014-05-02 10:18 | -180 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:45 | S217012740002 | BERENGER TOWER 1-51 | 102384 | Completed | 12e | High | Responsive Item | The self closing device fitted to the flat/lift lobby area fire doors on to the staircase on floor levels 10 and 15 need adjusting or replacing so that they shut the fire doors fully. | The self closing devices on these two fire doors should be adjusted, repaired or replaced so that the door shuts fully onto its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357290 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-19 09:45 | 2013-09-09 09:46 | 2013-08-19 09:45 | 2014-05-02 10:19 | -21 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:46 | S217012740002 | BERENGER TOWER 1-51 | 102385 | Completed | 14 | High | Responsive Item | There is part of a brick missing in the 1st floor staircase wall, where a cable has been passed through the back wall of the electrical cupboard which opens out on to walkway. | A replacement brick should be inserted in this wall so that this hole in the wall lining is filled in. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad | 2013-09-09 | Block Job number 201357290 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-08-19 09:46 | 2013-09-09 09:47 | 2013-08-19 09:46 | 2014-05-02 10:20 | -21 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:48 | S217012740002 | BERENGER TOWER 1-51 | 102386 | Completed | 16 | Medium | Responsive Item | The floor level and flat numbers signs are missing from the staircase landing on the 1st, 2nd 3rd, 4th, 6th, 8th, 9th, 14th, 15th and 16th floor levels. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that a floor level and flat numbers signs are provided for these staircase landing floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-16 | Block Job number 201357290 Awaiting some signage, to be delivered 02/05/14 201553860 - RD confirm completion | 2016-03-05 | Fully Completed | Michael Lyons | 2013-08-19 09:48 | 2013-10-18 09:49 | 2013-08-19 09:48 | 2016-03-07 16:54 | -60 | In target | 2013-08-19 09:48 | 2014-05-10 07:45 | Janice Wray
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:30 | S217012740014 | BLANTYRE TOWER 1-65 | 102167 | Completed | 12b | High | Responsive Item | The self closing devices fitted to the flat/lift lobby area fire doors on to the staircase on the 5th and 15th floor levels need adjusting or replacing so that they shut the fire doors fully. | The self closing device on these fire doors should be adjusted, repaired or replaced so that the doors shut fully onto their stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Job number 201357294 | 2014-04-23 | Fully Completed | Michael Lyons | 2013-08-16 07:30 | 2013-09-06 07:32 | 2013-08-16 07:30 | 2014-05-02 10:01 | -21 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:36 | S217012740014 | BLANTYRE TOWER 1-65 | 102168 | Completed | 16 | Medium | Miscellaneous | The floor level and flat numbers signs are missing from the staircase landings on floor levels, 1, 4, 5, 6, 10 and 14. Also the sign on the flat/lift lobby area of the 14th floor level is also missing. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that the floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357294 | 2014-04-25 | Fully Completed | Michael Lyons | 2013-08-16 07:36 | 2013-10-15 07:39 | 2013-08-16 07:36 | 2014-05-02 10:02 | -60 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 14:56 | S217009090001 | BLECHYNDEN HOUSE | 142406 | Completed | 14 | High | Responsive Item | There are holes in the ceiling linings of the ground floor electrical room where pipes and cables have been pasted through and a repair not made good. | These holes in the ceiling should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Alex Bosman |  |  | 2015-12-03 | Fully Completed | Janice Wray | 2014-05-06 14:56 | 2014-05-27 14:58 | 2014-05-06 14:56 | 2015-12-04 17:15 | -21 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:52 | S217008190001 | BOSWORTH HOUSE | 184211 | Completed | 14a | High | Responsive Item | There is a hole in the wall lining near the door of the third floor level plant room. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham |  | 201529205, hole filled with fire cement COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-02-18 09:52 | 2015-03-11 09:54 | 2015-02-18 09:52 | 2015-09-21 16:58 | -21 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:54 | S217008190001 | BOSWORTH HOUSE | 184212 | Completed | 14b | High | Responsive Item | Part of the duct work/covers are missing on the 2nd floor level below the 3rd floor level plant room, by the staircase to balcony door. | I would recommend that the covers are replaced on this duct work. This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham |  | duct cover re-fixed COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-02-18 09:54 | 2015-03-11 09:56 | 2015-02-18 09:54 | 2015-09-21 17:00 | -21 | In target
BOWLING GREEN HOUSE, APOLLO PLACE, LONDON SW10 0DN - 2015.1.6 | 2015-01-30 13:22 | S217012760011 | BOWLING GREEN HOUSE | 181064 | Completed | 1 | High | Responsive Item | At the time of this assessment the lights on the 2nd floor level balcony were not all working, according to a resident this has been reported to the TMO helpline. | Can it be please be confirmed that the lights not working on the 2nd floor level balcony have been reported and that work is in hand to repair or replace these lights? If not I would recommend that these lights not working are repaired, bulbs changed etc as soon as possible. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-01-30 13:22 | 2015-02-20 13:24 | 2015-01-30 13:22 | 2015-12-02 11:44 | -21 | In target
BOWLING GREEN HOUSE, APOLLO PLACE, LONDON SW10 0DN - 2015.1.6 | 2015-01-30 13:30 | S217012760011 | BOWLING GREEN HOUSE | 181068 | Completed | 14 | High | Responsive Item | On the wall near to flat 3 a cover plate has been removed and fitted back very badly, there are cables coming from under this cover plate and these are then fixed to the wall. | I would recommend that this cover plate is fixed to the wall correctly and fully so that there are no gaps around the edge of the plate or between the plate and the wall. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2015-01-30 13:30 | 2015-02-20 13:31 | 2015-01-30 13:30 | 2015-12-02 11:45 | -21 | In target
BRICKBARN CLOSE - 2015.05.05 | 2015-05-12 14:04 | S217002990005 | BRICKBARN CLOSE | 196617 | Completed | 12 | High | Responsive Item | The door from the roof level cold water tank room above the staircase of flats 9 to16 is in pieces with bits of it laying on the floor of the water tank room and on the external roof. | I would recommend that a new door is fitted from this cold water tank room to the external roof area and that all the old pieces of door and any other waste are removed from the external roof and this water tank room. | Responsive Repairs | John Tatham | 2015-06-19 | 201554166 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-05-12 14:04 | 2015-06-02 14:05 | 2015-05-12 14:04 | 2016-03-07 16:57 | -21 | In target
BRICKBARN CLOSE - 2015.05.05 | 2015-05-12 14:06 | S217002990005 | BRICKBARN CLOSE | 196620 | Completed | 14 | High | Responsive Item | Above the door of the electrical cupboard/ room of the staircase of flats 1 to 8 there are two holes in the wall linings where a cable has been passed through the wall and a repair has not made good. | These holes in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-06-02 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-12 14:06 | 2015-06-02 14:07 | 2015-05-12 14:06 | 2016-02-02 19:34 | -21 | In target
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:09 | S217010820001 | BRUCE HOUSE | 214306 | Completed | 12b | Low | Responsive Item | In the 2nd floor level staircase half landing floor surface of flats 25 to 36 there is a hole in the floor surface where a pipe passes through the landing floor. The area around the pipe hole has not been filled in etc. | The floor surface in the staircase of flats 25 to 36 at the 2nd floor level should be repaired so as not to be a trip hazard where the hole is located. | Responsive Repairs | Alan Brooks | 2016-02-28 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-01 12:09 | 2016-02-28 12:23 | 2015-09-01 12:09 | 2016-02-02 19:36 | -180 | In target
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:27 | S217010820001 | BRUCE HOUSE | 214309 | Completed | 14 | Medium | Responsive Item | There is a hole in the wall lining of the ground floor electrical room, left hand side of the door, in the staircase of flats 25 to 36 where an electrical cable has been passed through the wall and a repair has not made good. | This hole in the wall lining should be repaired with a suitable fire rated material so that the fire rating of the room/cupboard onto the staircase is maintained fire rated and also that of the buildings structure. | Responsive Repairs | Alan Brooks | 2015-10-31 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-01 12:27 | 2015-10-31 12:30 | 2015-09-01 12:27 | 2016-02-02 19:37 | -60 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:46 | S217000980001 | BRUNEL HOUSE | 181575 | Completed | 14a | High | Responsive Item | There are two holes in the wall above the ground floor level electrical cupboard/room where electrical cables have been passed through the wall and the holes not made good. | I would recommend that these holes in the wall lining are in filled with a suitable fire rated material to maintain the compartmentation and structural fabric of this building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2015-02-03 11:46 | 2015-02-24 11:47 | 2015-02-03 11:46 | 2015-11-25 20:01 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:48 | S217000980001 | BRUNEL HOUSE | 181578 | Completed | 14b | High | Responsive Item | On each staircase half landing there are holes in the wall linings at high level where electrical cables have been passed through the wall and the holes not made good. | I would recommend that these holes in the wall lining are in filled with a suitable fire rated material to maintain the compartmentation and structural fabric of this building. | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2015-02-03 11:48 | 2015-02-24 11:49 | 2015-02-03 11:48 | 2015-11-25 20:02 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:50 | S217000980001 | BRUNEL HOUSE | 181579 | Completed | 14c | High | Responsive Item | The cover plates of the service duct have been removed from the staircase wall and have not been fitted back fully. | I would recommend that these duct cover plates are fitted back correctly. | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2015-02-03 11:50 | 2015-02-24 11:51 | 2015-02-03 11:50 | 2015-11-25 20:04 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:52 | S217000980001 | BRUNEL HOUSE | 181581 | Completed | 14d | High | Responsive Item | On the wall by flats 1 and 2 cover plates have been removed and not fitted back correctly. | I would recommend that these cover plates are fitted back correctly. | Responsive Repairs | John Tatham |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2015-02-03 11:52 | 2015-02-24 11:53 | 2015-02-03 11:52 | 2015-11-25 20:05 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:16 | S217010650001 | BURGESS FIELDS | 104212 | Completed | 1b | High | Responsive Item | The light unit outside the roof level lift motor room is damaged and not working as well as two other units in other roof areas. | I would recommend that these light units are tested by an electrician to see if they work correctly and if needed that they are repaired or replaced so that they illuminate the roof space areas. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357296 | 2014-03-31 | Fully Completed | Michael Lyons | 2013-08-30 14:16 | 2013-09-20 14:17 | 2013-08-30 14:16 | 2014-05-07 20:06 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:27 | S217010650001 | BURGESS FIELDS | 104222 | Completed | 12a | High | Responsive Item | In the roof space the frame of one of the fire break doors is damaged, therefore not providing a fire break in the roof area. | The door frame of the damaged door in the roof space should be repaired so that the roof level fire breaks are maintained. | Responsive Repairs | Jackie Gaikwad | 2015-09-22 | Site job number 201357296 elements of this job have been completed, we are just awaiting a section of frame RD confirm completion | 2016-02-22 | Fully Completed | Michael Lyons | 2013-08-30 14:27 | 2013-09-20 14:41 | 2013-08-30 14:27 | 2016-02-23 20:23 | -21 | In target | 2013-08-30 14:27 | 2014-05-14 15:46 | Janice Wray
BURGESSFIELD-2013.06.20 | 2013-08-30 14:41 | S217010650001 | BURGESS FIELDS | 104228 | Completed | 12b | High | Responsive Item | The self closing devices fitted to the ground floor office door, the lower ground floor level door from the corridor going to the electrics room and 1st floor level guest bedroom door do not close the fire doors fully onto its stops. | The self closing devices fitted to these fire doors should be adjusted, repaired or replaced so that the self closing devices close the fire doors fully on to their stops. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357296 | 2014-04-04 | Fully Completed | Michael Lyons | 2013-08-30 14:41 | 2013-09-20 14:42 | 2013-08-30 14:41 | 2014-05-07 20:08 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:43 | S217010650001 | BURGESS FIELDS | 104229 | Completed | 14a | High | Responsive Item | There are holes in the wall linings of the lower ground floor lobby area by the WC and the electrical intake room where cables have been past through and a repair not made good. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357296 | 2014-04-07 | Fully Completed | Michael Lyons | 2013-08-30 14:43 | 2013-09-20 14:44 | 2013-08-30 14:43 | 2014-05-07 20:08 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:45 | S217010650001 | BURGESS FIELDS | 104230 | Completed | 14b | High | Responsive Item | There are large holes in the wall and ceiling linings in the roof space and in the externally accessed boiler room where new pipes have been fitted for the buildings heating system. | These holes in the wall and ceiling lining should be repaired/filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357296 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-30 14:45 | 2013-09-20 14:46 | 2013-08-30 14:45 | 2014-05-07 20:09 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:46 | S217010650001 | BURGESS FIELDS | 104231 | Completed | 16a | High | Responsive Item | There is presently no external escape signage provided at the lower ground floor level at the front of the building showing the way to the rear garden area. | Escape signage should be suitably displayed externally at the lower ground floor level at the front of the building showing the way to the rear garden area. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357296 | 2014-04-15 | Fully Completed | Michael Lyons | 2013-08-30 14:46 | 2013-09-20 14:48 | 2013-08-30 14:46 | 2014-05-07 20:09 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:30 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134511 | Active | 1b | High | Responsive Item | The light units in 2 of the 4 residents storage areas located in the wire mesh cages off the 3rd floor corridor are damaged, hanging off the ceilings or have no light bulbs in them. | I would recommend that these light fittings are repaired, replaced or new bulbs are placed in them so that the lights work correctly. | Responsive Repairs | Alex Bosman |  |  |  |  | Lee Amos | 2014-03-13 15:30 | 2014-04-03 15:32 |  |  | 734 | 734 days overdue
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:34 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134515 | Completed | 3a | High | Responsive Item | The fire fighter entry over ride device fitted to the entrance door at the head of the ramp did not work correctly and release the locking device on the door nor did the ones near to flats, 1 and 10 Camelford Walk and 20 Upper Camelford Walk. All the other doors fitted with over ride switches worked correctly. | The fire fighter entry over ride devices fitted to these entrance doors should be repaired or replaced so that they releases the locking device fitted to the entrance doors. These over ride devices allows the Fire and Rescue Service to access the staircase/walkway etc in an emergency without the use of a key. | Responsive Repairs | Alex Bosman |  | All checked by Rob Regan and working fine on 07/10/15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-03-13 15:34 | 2014-04-03 15:36 | 2014-03-13 15:34 | 2015-11-20 11:30 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:36 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134516 | Completed | 3b | High | Responsive Item | The steel shut off plate built into the base of the refuse chute located near to the boiler room, is damaged. The steel shut off plate is so that the refuse chute can be isolated from the bin room. | I would recommend that this steel shut off plate is repaired or replaced so that the refuse chute can be isolated from the bin room. | Responsive Repairs | Alex Bosman |  | 201526236 Surveys carried out 22 & 23/10/15 with work to commence on site 26/10/15 | 2015-11-10 | Fully Completed | Janice Wray | 2014-03-13 15:36 | 2014-04-03 15:38 | 2014-03-13 15:36 | 2015-11-11 21:05 | -21 | In target | 2014-03-13 15:36 | 2015-11-17 21:04 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:42 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134520 | Completed | 8c | High | Responsive Item | Some of the covering of the electrical trunking is missing by the entrance door of flat 9 of Camelford Walk. | I would recommend that the missing covering of the electrical trunking is replaced. | Responsive Repairs | Alex Bosman |  | LGSR issued 05/11/15 | 2015-11-20 | Fully Completed | Maria Ares | 2014-03-13 15:42 | 2014-04-03 15:43 | 2014-03-13 15:42 | 2015-11-23 13:14 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:46 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134522 | Completed | 14 | High | Responsive Item | There are bricks missing from wall of the electrical cupboard in the staircase on the third floor level between flats 20 and 22 of Upper Camelford Walk. | The missing bricks should be replaced in the wall of this electrical cupboard. NOTE- THIS APPLIES TO BOTH BLOCKS | Responsive Repairs | Alex Bosman |  | 201526236 Surveys carried out 22 & 23/10/15 with work to commence on site 26/10/15 | 2015-12-24 | Fully Completed | Janice Wray | 2014-03-13 15:46 | 2014-04-03 15:51 | 2014-03-13 15:46 | 2015-12-29 14:59 | -21 | In target | 2014-03-13 15:46 | 2015-12-31 14:59 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:53 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134534 | Completed | 16b | High | Signage | The "Push Bar to Open" signs is missing on the 2nd door of the alternative exit route from the boiler room. | A "Push Bar to Open" signs should be displayed on this exit | Responsive Repairs | Michael Lyons |  | COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2014-03-13 15:53 | 2014-04-03 15:54 | 2014-03-13 15:53 | 2015-09-21 17:09 | -21 | In target | 2014-03-13 15:53 | 2015-09-25 17:09 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:57 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134539 | Completed | 18 | High | Fire Extinguisher | There are carbon dioxide fire extinguishers located in some of the electrical cupboards of this building. There is no signage on the outside of the cupboard doors indicating that there are fire extinguishers located inside the cupboards. There is no access to these cupboards unless you have a special key for the high grade security locks fitted to them. | RECOMMENDED ACTION I would recommend that the carbon dioxide fire extinguishers located inside the small electrical cupboards off the staircases are removed. The extinguisher in the ground floor level cupboard was last serviced in November 2011 according to the RGE contractors label on it. Alternative Action (Alternatively if TMO choose to keep these fire extinguishers in the electrical cupboards they must be serviced and a sign displayed on the outer face of each electrical cupboard indicating that there is a carbon dioxide portable fire extinguisher located inside the cupboard. ) Alex | Responsive Repairs | Alex Bosman |  | AP confirmed service complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-03-13 15:57 | 2014-04-03 15:58 | 2014-03-13 15:57 | 2015-12-15 11:03 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:07 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127456 | Completed | 12 | High | Responsive Item | The inner door of the pedestrian exit in the corner located by the vehicle ramp is damaged. | This door should be repaired or replaced so that it can be opened and closed easily and not ground. | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-01-31 13:07 | 2014-02-21 13:08 | 2014-01-31 13:07 | 2015-11-25 20:25 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:16 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127463 | Completed | 16a | High | Signage | There is exit signage displayed indicating that both of the exit doors from the lobby area of the corner pedestrian exit are means of escape routes. The right hand door leads to an enclosed space. | The exit signage indicating that the right hand side door from the lobby area of the corner pedestrian exit by the ramp should be removed immediately as this door leads to an enclosed space. This is nor a designated exit route. | Responsive Repairs | Alex Bosman |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2014-01-31 13:16 | 2014-02-21 13:17 | 2014-01-31 13:16 | 2015-12-02 11:24 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:19 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127466 | Completed | 16b | High | Miscellaneous | The corner pedestrian exit by the ramp (at the front of the car park) is so close to the ramp and the pedestrian gate on the ramp that this exit is not required to be an emergency means of escape route. Also if you use this route, the gate in the railings at the head of the steps is locked shut, so any person will have to climb over the railings to get to a place of ultimate safety. | For this corner exit to be an emergency exit route the gate in the railings must be kept unlocked or a suitable opening device fitted to it that does not require a key to open it. RECOMMENDED ACTION Please remove all signage indicating that this corner exit route is an emergency means of escape route. | Responsive Repairs | Alex Bosman |  |  | 2015-12-01 | Fully Completed | Janice Wray | 2014-01-31 13:19 | 2014-02-21 13:21 | 2014-01-31 13:19 | 2015-12-02 11:25 | -21 | In target
CARTON HOUSE - 2014.4.22 | 2014-05-14 10:55 | S217010050007 | CARTON HOUSE | 143663 | Completed | 1a | High | Responsive Item | Two of the lights in the roof space area, above flat 47 are not working. | I would recommend that a contractor is asked to check out/test the lights in the roof space area to see if they work correctly and repair or replace them if they do not. Work has been undertaken in this roof space area. | Responsive Repairs | Michael Lyons |  | Works order raised | 2015-11-24 | Fully Completed | Janice Wray | 2014-05-14 10:55 | 2014-06-04 11:21 | 2014-05-14 10:55 | 2015-11-25 19:27 | -21 | In target | 2014-05-14 10:55 | 2015-12-01 19:26 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:21 | S217010050007 | CARTON HOUSE | 143677 | Completed | 1b | Medium | Responsive Item | The covers of some of the lighting units located on the external roof area and in the roof space area of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units located at the roof level of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | Responsive Repairs | Michael Lyons |  | Works order raised | 2015-11-24 | Fully Completed | Janice Wray | 2014-05-14 11:21 | 2014-07-13 11:22 | 2014-05-14 11:21 | 2015-11-25 19:29 | -60 | In target | 2014-05-14 11:21 | 2015-12-01 19:29 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:23 | S217010050007 | CARTON HOUSE | 143678 | Completed | 8 | High | Responsive Item | There has been work undertaken in the roof space area of this building, there are areas of roof insulation missing or insulation piled up in heaps as well as parts of the walkway missing. | I would recommend that the missing parts of the walkway in the enclosed roof space area are replaced. The insulation should be re-laid or replaced where it is missing. I would recommend that in future checks are carried out after contractors have undertaken work in this building. | Responsive Repairs | Michael Lyons |  | Works order raised -201526239 | 2015-11-10 | Fully Completed | Janice Wray | 2014-05-14 11:23 | 2014-06-04 11:24 | 2014-05-14 11:23 | 2015-11-11 21:16 | -21 | In target | 2014-05-14 11:23 | 2015-11-17 21:16 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:55 | S217010050007 | CARTON HOUSE | 143694 | Completed | 16a | High | Signage | After the redecoration/refurbishment work in this building signs were displayed on each floor level by the lifts and on each staircase landing giving the floor level number and the flats located on that floor level. One or all 3 of these signs on floor levels, 5, 7 and 8 and damaged, missing or defaced. These signs are to aid to the emergency services. | I would recommend that new signs are displayed, these signs should be similar to the signs displayed on the other floor levels and give the same information. These signs should be in a large font and permanently fixed to the walls in the same positions as the ones on the other floor levels. | Responsive Repairs | Michael Lyons |  | Works order raised - now Completed | 2015-10-02 | Fully Completed | Janice Wray | 2014-05-14 11:55 | 2014-06-04 11:56 | 2014-05-14 11:55 | 2015-10-07 12:52 | -21 | In target | 2014-05-14 11:55 | 2015-10-13 12:52 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:57 | S217010050007 | CARTON HOUSE | 143695 | Completed | 16b | High | Signage | There is no sign displayed in the ground floor level entrance lobby area informing the emergency services which flats are located on which floor level. | I would recommend that a sign is displayed in the ground floor level entrance lobby area showing which flat numbers are located on which floor level. This sign should be permanently fixed to the wall by the lifts and in a large font. | Responsive Repairs | Michael Lyons |  | Works order raised - Completed | 2015-10-02 | Fully Completed | Janice Wray | 2014-05-14 11:57 | 2014-06-04 11:58 | 2014-05-14 11:57 | 2015-10-07 12:54 | -21 | In target | 2014-05-14 11:57 | 2015-10-13 12:54 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:58 | S217010050007 | CARTON HOUSE | 143696 | Completed | 16c | High | Signage | The "Push Bar to Open" signs are missing on each of the exit doors at the base of the staircases at the ground floor level. | A "Push Bar to Open" signs should be displayed on each of the ground floor final exit doors at the base of each staircase. | Responsive Repairs | Michael Lyons |  | Sign installed | 2015-09-16 | Fully Completed | Janice Wray | 2014-05-14 11:58 | 2014-06-04 12:01 | 2014-05-14 11:58 | 2015-09-21 17:11 | -21 | In target
CHELSEA MANOR COURT FLATS 27 TO 76 - 2015.07.07 | 2015-09-01 09:44 | S217000830004 | CHELSEA MANOR COURT 27-54 | 214227 | Completed | 14a | High | Responsive Item | Above the ground floor level electrical room/cupboard doors by flats 55 and 62 there are cable holes in the door frame and in the wall lining where cables have been passed through the door frame and the wall lining and making good has not been undertaken. | These holes in the door frames and the wall linings should be filled in with a suitable fire rated materials to maintain the fire rating of the structural elements of this building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-09-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-01 09:44 | 2015-09-22 09:45 | 2015-09-01 09:44 | 2016-02-02 19:39 | -21 | In target
CHELSEA MANOR COURT FLATS 27 TO 76 - 2015.07.07 | 2015-09-01 09:45 | S217000830004 | CHELSEA MANOR COURT 27-54 | 214228 | Completed | 14b | Medium | Responsive Item | On each landing level of each staircase the light fitting have been replaced, the new light fittings are smaller than the old ones. Where the old light fittings have been removed there are holes in the ceiling lining which have not been in filled/repaired. | These holes in the ceiling linings should be filled in/repaired with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-10-31 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-01 09:45 | 2015-10-31 09:47 | 2015-09-01 09:45 | 2016-02-02 19:40 | -60 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:17 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102325 | Completed | 8e | Low | Responsive Item | The riser cupboard on the 5th floor level with the double doors is open and I could not secure it shut. | I would recommend that the lock fitted to this cupboard door is repaired or replaced so that the doors can be secured shut. | Responsive Repairs | Jackie Gaikwad | 2013-02-01 | Block Job number 201357298 | 2014-03-27 | Fully Completed | Michael Lyons | 2013-08-16 16:17 | 2014-02-12 16:20 | 2013-08-16 16:17 | 2014-05-02 10:22 | -180 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:41 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102339 | Completed | 12c | High | Flat Door | The entrance door to flat 12 is damaged with one panel boarded over. | Can it be confirmed that this flat entrance door is still a fire rated door? If it is not it should be replaced with a fire rated door complying to the requirements of the Building Regulations. T | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Can this be passed to the FRA as it needs clarification as to teh door status This door was inspected by C Stokes on 13th May - door still has one damaged panel (bottom lhs of door) so door not currently compliant. Options are to replace the damaged panel or install replacement self-closing FD30 door. I will send a copy of the photo by e-mail to help you decide which way to proceed with this. Janice 201554216 - RD confirm completion | 2016-03-07 | Fully Completed | Michael Lyons | 2013-08-16 16:41 | 2013-09-06 16:43 | 2013-08-16 16:41 | 2016-03-08 13:34 | -21 | In target | 2013-08-16 16:41 | 2016-03-14 13:33 | Janice Wray
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:46 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102341 | Completed | 12e | High | Responsive Item | Some of the beading holding the fire rated glazed vision panels in the staircase fire doors on the 10th and 11th floor levels is loose or missing. | These two fire doors should be checked and any missing or loose beadings repaired. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357298 | 2014-04-24 | Fully Completed | Michael Lyons | 2013-08-16 16:46 | 2013-09-06 16:48 | 2013-08-16 16:46 | 2014-05-02 10:10 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:48 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102343 | Completed | 12f | High | Responsive Item | The self closing devices fitted to the flat/lift lobby area fire doors on to the staircase on the 1st, 2nd, 9th, 10th, 15th and 17th floor levels need adjusting or replacing so that they shut the fire doors fully. | The self closing device on these fire doors should be adjusted, repaired or replaced so that the door shuts fully onto their stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357298 | 2014-04-24 | Fully Completed | Michael Lyons | 2013-08-16 16:48 | 2013-09-06 16:49 | 2013-08-16 16:48 | 2014-05-02 10:10 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:53 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102347 | Completed | 14a | High | Responsive Item | The top right hand side fire rated glazed vision panel in the 15th floor level staircase fire door is cracked. | I would recommend that this damaged piece of fire rated glazing is replaced with a new piece. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357298 | 2014-04-15 | Fully Completed | Michael Lyons | 2013-08-16 16:53 | 2013-09-06 16:55 | 2013-08-16 16:53 | 2014-05-02 10:14 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:57 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102350 | Completed | 14b | High | Responsive Item | One piece of the fire rated glazed screen between the lift lobby area and the staircase on the ground floor level is cracked. | I would recommend that this damaged piece of fire rated glazing is replaced with a new piece. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357298 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-16 16:57 | 2013-09-06 16:58 | 2013-08-16 16:57 | 2014-05-02 10:14 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:59 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102352 | Completed | 14c | Medium | Responsive Item | One of the 5th floor level staircase external window is cracked and another one boarded up. | I would recommend that these damaged and boarded up windows are replaced with new pieces of glazing. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357298 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-16 16:59 | 2013-10-15 17:00 | 2013-08-16 16:59 | 2014-05-02 10:15 | -60 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 17:01 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102355 | Completed | 16 | Medium | Miscellaneous | The floor level and flat numbers signs are missing from the staircase landings on floor levels, 3, 4 and 17. Also the sign on the flat/lift lobby area of the 14th floor level. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that the floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357298 Awaiting additional landing 17 signs | 2014-05-28 | Fully Completed | Michael Lyons | 2013-08-16 17:01 | 2013-10-15 17:04 | 2013-08-16 17:01 | 2014-06-18 14:22 | -60 | In target | 2013-08-16 17:01 | 2014-05-21 16:23 | Michael Lyons
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 17:04 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102357 | Completed | 19 | High | Responsive Item | The hasp used for the padlock to secure the dry riser outlet box on the 18th floor level is broken. The dry riser outlet is now not secure and could be vandalised or damaged. | I would recommend that a new hasp and padlock is fitted to this dry riser outlet box so that the dry riser outlet is secured and therefore the fixed fire system is safe from vandalism or damage. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357298 | 2014-04-04 | Fully Completed | Michael Lyons | 2013-08-16 17:04 | 2013-09-06 17:07 | 2013-08-16 17:04 | 2014-05-02 10:16 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 13:37 | S217010570001 | CLYDESDALE HOUSE | 102842 | Completed | 14a | High | Responsive Item | There are holes in the side wall lining of the roof level lift motor room by the trap door, where electrical cables have been passed through the wall and repairs have not made good. | These holes in the wall linings should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357300 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-08-20 13:37 | 2013-09-10 13:40 | 2013-08-20 13:37 | 2014-05-02 12:32 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 13:45 | S217010570001 | CLYDESDALE HOUSE | 102847 | Completed | 14b | High | Responsive Item | There is a hole in the ceiling outside flat 10's entrance door. | This hole in the ceiling should be repaired. | Responsive Repairs | Jackie Gaikwad |  | Block Job number 201357300 | 2014-04-01 | Fully Completed | Michael Lyons | 2013-08-20 13:45 | 2013-09-10 13:54 | 2013-08-20 13:45 | 2014-05-02 12:32 | -21 | In target
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 09:47 | S217010050003 | COPPERFIELD HOUSE | 157979 | Completed | 1 | Information Only | Responsive Item | There was quite a bit of water in the ground floor level electrical cupboard/room under the staircase located by flats 13 and 14. Apparently it is very common for the area by the rear exit door of this staircase and by the electrical cupboard to be under water when it rains. | This cupboard does contain electrical components, these are wall mounted and above where the water rises to though. | Responsive Repairs | Michael Lyons | 2015-08-20 | 201554232 RD confirm completion | 2016-03-05 | Fully Completed |  |  |  | 2014-08-19 09:47 | 2016-03-07 17:08
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 09:53 | S217010050003 | COPPERFIELD HOUSE | 157989 | Completed | 12b | High | Flat Door | The flat entrance door to flat 6 has been changed from the original door, this is a tenanted flat. | Can it please be confirmed that this newly fitted flat entrance door and frame are certified 30 minute fire rated - is there any paperwork or do we need Carl to assess? Documentation to show this in case it is required by the enforcing authority of the FSO. Also is this new flat entrance door fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? If it is not then a self closing device etc must be fitted. | Responsive Repairs | Michael Lyons |  | no access 24/08,09/09, card left, 201526240 | 2015-11-10 | Fully Completed | Janice Wray | 2014-08-19 09:53 | 2014-09-09 09:56 | 2014-08-19 09:53 | 2015-11-11 21:25 | -21 | In target | 2014-08-19 09:53 | 2015-11-17 21:24 | Janice Wray
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:49 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103590 | Active | 12a | High | Responsive Item | The gate from the rear garden area is presently fitted with a mortice lock and a key is needed to open this gate. This needs to be replaced | Opening device on gate must be replaces so that the gate can be opened without the need for a key. This could be a thumb turn device or just a normal door handle but will need to be protected by a shield of some description for security reasons so that the gate cannot be opened from the footpath side. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357301 awaiting the welding of the shield |  | Partially Completed | Michael Lyons | 2013-08-23 15:49 | 2013-09-13 16:05 | 2013-08-23 15:49 | 2014-05-07 20:13 | -21 | In target | 2013-08-23 15:49 | 2014-05-14 15:45 | John Tatham
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 13:39 | S217003310001 | CURRAN HOUSE | 200505 | Completed | 14a | High | Responsive Item | In the wall of the ground floor level electrical room/cupboard by flat 6 there is a hole in the wall. | The hole in this wall of this electrical room/ cupboard should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-06-29 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-08 13:39 | 2015-06-29 14:00 | 2015-06-08 13:39 | 2016-02-02 19:42 | -21 | In target
DARFIELD WAY FLATS 2 TO 27 - 2015.08.13 | 2015-09-02 14:51 | S217008566606 | DARFIELD WAY 2-9 | 214588 | Active | 14 | Information Only | Responsive Item | It appears that the porch areas where the staircase entrance doors have been installed are coming away from the original brickwork of the building. The TMO know of this as pinning work has been undertaken to tie the porches to the original brickwork. | This collapsing of the newer built brick porches should be monitored so that the staircase entrance/exit doors do not become jammed and not openable. | Responsive Repairs | Maria Walker | [7 empty] | 2015-09-02 14:51 | 2015-10-21 12:22
DARTREY TOWER - 2013.03.01 | 2013-08-20 15:42 | S217012740006 | DARTREY TOWER 1-49 | 102919 | Completed | 8c | Low | Responsive Item | The doors of both riser cupboards on the 10th floor level will not open along with the double doors on the 8th floor level flat/lift lobby area and the single door on the 5th and 9th floor levels. | I would recommend that the locks fitted to these cupboard doors are repaired or replaced so that the doors open easily. | Responsive Repairs | Jackie Gaikwad | 2014-02-03 | Block job number 201357301 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-20 15:42 | 2014-02-16 16:06 | 2013-08-20 15:42 | 2014-05-06 08:27 | -180 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:18 | S217012740006 | DARTREY TOWER 1-49 | 102949 | Completed | 14a | High | Responsive Item | The staircase window pane is cracked and damaged at the 4th floor level. | I would recommend that this window pane is replaced. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Block job number 201357301 And inspected | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-20 16:18 | 2013-09-10 16:20 | 2013-08-20 16:18 | 2014-05-06 09:14 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:23 | S217012740006 | DARTREY TOWER 1-49 | 102953 | Completed | 14b | High | Responsive Item | There are holes in the wall and ceiling linings where cables have been passed through the linings and the hole not filled in: 1. On the ground floor level by the electrical room door. 2. In the 1st floor staircase wall 3. On the 2nd floor level over the double cupboard 4. On the 17th floor level over the single cupboard | These holes in the wall and ceiling linings should be repaired/filled in with suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Block job number 201357301 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-20 16:23 | 2013-09-10 16:41 | 2013-08-20 16:23 | 2014-05-06 09:18 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:43 | S217012740006 | DARTREY TOWER 1-49 | 102963 | Completed | 16 | Medium | Signage | The floor level and flat numbers signs are missing from both the staircase landing and the flat/lift lobby area on floor level 9 and the staircase landing of floor level 16. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-18 | These audit of all signs and numbers has been carried out and all signs have been ordered, and will be fitted by 21/05 | 2014-05-30 | Fully Completed | Michael Lyons | 2013-08-20 16:43 | 2013-10-19 16:45 | 2013-08-20 16:43 | 2014-06-18 15:35 | -60 | In target | 2013-08-20 16:43 | 2014-05-14 15:37 | Michael Lyons
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:13 | S217012740006 | DARTREY TOWER 1-49 | 102943 | Completed | 12b | High | Responsive Item | The self closing device fitted to the flat/lift lobby area fire doors on to the staircase on the following floor levels needs adjusting or replacing so that it shuts the fire door fully. 5th Floor level 11th Floor level 13th Floor level | These self closing devices on these fire doors should be adjusted, repaired or replaced so that the door shuts fully onto its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Block job number 201357301 Not completed on the original jobs raised in 2013 | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-20 16:13 | 2013-09-10 16:16 | 2013-08-20 16:13 | 2014-05-06 09:51 | -21 | In target | 2013-08-20 16:13 | 2014-05-12 09:51 | Janice Wray
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:16 | S217012740006 | DARTREY TOWER 1-49 | 102946 | Completed | 12c | High | Responsive Item | The ground floor lift lobby exit door did not shut fully therefore engaging the locking mechanism of the door. | I would recommend that the self closing device fitted to this exit door is looked at and adjusted or replaced so that the door huts fully and the lock engages. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Block job number 201357301 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-08-20 16:16 | 2013-09-10 16:18 | 2013-08-20 16:16 | 2014-05-06 08:48 | -21 | In target
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:09 | S217012270003 | DENBIGH HOUSE | 189969 | Completed | 12b | High | Responsive Item | The hopper to refuse chute opening by flats 3 and 4 did not shut fully. | This refuse chute hopper should be repaired or replaced so that it shuts fully. | Responsive Repairs | John Tatham |  | Works order raised - 201526244 Surveys carried out 22 & 23/10/15 with work to commence on site 26/10/15 | 2015-10-27 | Fully Completed | Janice Wray | 2015-03-26 13:09 | 2015-04-16 13:10 | 2015-03-26 13:09 | 2015-10-28 15:19 | -21 | In target | 2015-03-26 13:09 | 2015-11-03 15:18 | Janice Wray
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:10 | S217012270003 | DENBIGH HOUSE | 189970 | Completed | 14a | High | Responsive Item | To the upper left hand side of the under staircase electrical cupboard door of the staircase of flats 1 to 8 there is a hole in the wall linings where cable have been passed through the wall and a repair has not made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in this building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  | Holes filled with fire retardent filler COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-03-26 13:10 | 2015-04-16 13:12 | 2015-03-26 13:10 | 2015-09-21 17:21 | -21 | In target
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:13 | S217012270003 | DENBIGH HOUSE | 189971 | Completed | 14b | Medium | Responsive Item | There appears to be an air brick in the compartment wall between the bin storage area and the electrical room of the staircase of flats 1 to 8 that could allow the passage of flames and smoke between the 2 areas. | This wall between the bin area and the electrical room/cupboard should be made a minimum of 30 minutes fire rated so fire separating these 2 areas. | Responsive Repairs | John Tatham |  | air brick removed and bricked up COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-03-26 13:13 | 2015-05-25 13:14 | 2015-03-26 13:13 | 2015-09-21 17:22 | -60 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:28 | S217010050004 | DOMBEY HOUSE | 158099 | Completed | 12a | High | Flat Door | The flat entrance door and frame to flat 4 was changed by the TMO in September 2013. | Can it please be confirmed that this TMO newly fitted flat entrance door and frame are certified 30 minute fire rated with the documentation to show this in case it is required by the enforcing authority of the FSO. Also is this new flat entrance door fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? If it is not then a self closing device etc must be fitted. Can it please be confirmed that | Responsive Repairs | Michael Lyons |  | Order 201526245 - the door will need to be replaced, this will be booked in for after 03/10/15 as the tenant is away. | 2015-11-10 | Fully Completed | Janice Wray | 2014-08-19 15:28 | 2014-09-09 15:30 | 2014-08-19 15:28 | 2015-11-11 21:31 | -21 | In target | 2014-08-19 15:28 | 2015-11-17 21:31 | Janice Wray
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:34 | S217010050004 | DOMBEY HOUSE | 158102 | Completed | 14a | Medium | Flat Door | The fire rated glazing in the vision panel of flat 23's flat entrance door is cracked. | The fire rated glazing in this vision panel of this flat entrance door should be replaced with another suitable fire rated piece of glazing. This is so that the integrity of the flat entrance door and the protected staircase is maintained. | Responsive Repairs | Michael Lyons |  | window reglazed GWC 1m2 COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2014-08-19 15:34 | 2014-10-18 15:35 | 2014-08-19 15:34 | 2015-09-21 17:24 | -60 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:38 | S217010050004 | DOMBEY HOUSE | 158104 | Completed | 14b | Medium | Responsive Item | There is a large hole in the external porch canopy outside the staircase to flats 19 to 24. | I would recommend that the hole in this porch canopy is repaired. | Responsive Repairs | Michael Lyons |  | no hole in canopy, no works needed COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2014-08-19 15:38 | 2014-10-18 15:39 | 2014-08-19 15:38 | 2015-09-21 17:26 | -60 | In target
DORRIT HOUSE - 2014.7.22 | 2014-08-01 16:47 | S217010050006 | DORRIT HOUSE | 155721 | Completed | 12 | High | Responsive Item | The flat entrance door to flat 18 has been changed from the originally fitted fire rated door. This flat entrance door is now not a fire rated door. | I would recommend that this flat entrance door is replaced with a new self closing 30 minute fire rated door complying with all the requirements of the Building Regulations. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-08-01 16:47 | 2014-08-22 16:48 | 2014-08-01 16:47 | 2015-11-27 21:21 | -21 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:33 | S217010470003 | EASTRY HOUSE | 196878 | Completed | 14 | High | Responsive Item | There is a hole in the wall lining of the ground floor level electrical cupboard/room where a cable has been pasted through the wall and the wall lining not made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-06-03 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-13 15:33 | 2015-06-03 15:34 | 2015-05-13 15:33 | 2016-02-02 19:50 | -21 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:35 | S217010470003 | EASTRY HOUSE | 196879 | Completed | 22a | High | Responsive Item | There is a vent pipe in the staircase wall at the 1st floor level from Walmer Road NHS Clinic/centre. This vent is through a blocked off window. A fire in the NHS occupied area of this building will take out the residential staircase as this vent does not have a fire dampener on it. | I would recommend that the Walmer Road NHS centre/clinic block off this vent or fit a fire dampener on the end of it so that a fire in the NHS occupancy does not make the staircase un-useable for the TMO occupants of this building. | Responsive Repairs | John Tatham | 2015-06-03 | 201553973 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-05-13 15:35 | 2015-06-03 15:36 | 2015-05-13 15:35 | 2016-03-07 17:12 | -21 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:26 | S217002186603 | ELM PARK HOUSE PARKING | 122255 | Completed | 16a | High | Signage | The presently displayed exit sign indicating that the end exit doors are a means of escape route should be removed and new arrowed exit signage displayed showing that the ramp is the only entrance/exit route from this car park. | Remove the exit sign indicating that the end exit doors are means of escape routes and fit new exit signage indicating the ramp as the only exit route. | Responsive Repairs | Alex Bosman | 2014-01-23 | Order 201542477 | 2016-03-13 | Fully Completed | Mainu Miah | 2014-01-02 09:26 | 2014-01-23 09:29 | 2014-01-02 09:26 | 2016-04-01 12:53 | -21 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:29 | S217002186603 | ELM PARK HOUSE PARKING | 122257 | Completed | 16b | High | Signage | Two of the fire action notices in this car park are presently on the floor. | The fire action notices presently located on the floor of this car park should be securely fitted to the walls. | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-01-02 09:29 | 2014-01-23 09:30 | 2014-01-02 09:29 | 2015-11-25 20:48 | -21 | In target
ELM PARK HOUSE CAR PARK | 2013-12-31 09:23 | S217002186603 | ELM PARK HOUSE PARKING | 122043 | Completed |  | High | Signage | As this car park is now full sprinklered I believe that all signage indicating that the two end pedestrian secondary exits are emergency exits should be removed. Please see the section titled "Any other relevant information on this premises" in the fire risk assessment for a full explanation of why these secondary exits are not needed. If there was a fire in the car park as you were driving into it you would drive back out again and if you saw a fire in the car park as a pedestrian you would not enter the car park. Now that this car park is fully sprinklered I believe that the two end exits should be classed as accommodation exits only. | Remove the presently installed exit signage indicating that the two end exits from this car park are emergency exits. | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2013-12-31 09:23 | 2014-01-21 09:27 | 2013-12-31 09:23 | 2015-11-25 20:46 | -21 | In target
ELM PARK HOUSE CAR PARK | 2013-12-31 09:30 | S217002186603 | ELM PARK HOUSE PARKING | 122046 | Completed |  | Medium | Emergency Lighting | The presently installed emergency lighting system in this car park is not to a recognised standard. Emergency lighting units appear to just be randomly fitted. | When possible I would recommend that new or additional emergency lighting units are installed in this car park to the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | Responsive Repairs | Alex Bosman |  | AP confirmed service of system complete condition report to follow for possible inclusion in future upgrade program. | 2015-12-14 | Fully Completed | Maria Ares | 2013-12-31 09:30 | 2014-03-01 09:31 | 2013-12-31 09:30 | 2015-12-15 11:19 | -60 | In target
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:31 | S217010050009 | ESTELLA HOUSE | 158192 | Completed | 12a | High | Responsive Item | The door of the ground floor electrical meter room of the staircase of flats 13 to 16 appears to be damaged and will not open. | The lock on this electrical meter room door should be repaired or replaced so that access to the room can be gained. If there are any items stored in this cupboard these should be removed. | Responsive Repairs | Michael Lyons |  | Works order raised -201526248 Surveys carried out 22 & 23/10/15 with work to commence on site 26/10/15 | 2015-10-27 | Fully Completed | Janice Wray | 2014-08-20 11:31 | 2014-09-10 11:32 | 2014-08-20 11:31 | 2015-10-28 15:25 | -21 | In target | 2014-08-20 11:31 | 2015-11-03 15:24 | Janice Wray
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:32 | S217010050009 | ESTELLA HOUSE | 158194 | Completed | 12b | High | Flat Door | The flat entrance door to flat 7 has been changed from the originally fitted fire rated flat entrance door. This is a tenanted dwelling. (Tenanted Dwelling) | Can it please be confirmed that this flat entrance door if fitted by the TMO or its contractors is a certified 30 minute fire rated with the documentation to show this in case it is required by the enforcing authority of the FSO. Also is this new flat entrance door fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? If this door was not fitted by the TMO or its contractors I would recommend that the occupier is asked to provide documentation showing that this door is a 30 minute fire rated door and that it is fitted with a self closing device capable of shutting the door fully onto its stops. | Responsive Repairs | Michael Lyons |  | Works order raised | 2015-11-18 | Fully Completed | Janice Wray | 2014-08-20 11:32 | 2014-09-10 11:34 | 2014-08-20 11:32 | 2015-11-19 20:13 | -21 | In target | 2014-08-20 11:32 | 2015-11-25 20:13 | Janice Wray
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:54 | S217008270002 | CAMBORNE MEWS (13-36) | 181054 | Completed | 12a | High | Responsive Item | A light fitting has been fitted on the door frame of flat 28, there is now a hole straight through this door frame and the light fitting does not have a bulb in it. | I would recommend that this light fitting is removed and that the hole straight through the flat entrance door, door frame is filled in suiting a suitable fire rated material. | Responsive Repairs | John Tatham |  | Works order raised -201526228 | 2015-12-02 | Fully Completed | Janice Wray | 2015-01-30 12:54 | 2015-02-20 12:55 | 2015-01-30 12:54 | 2015-12-03 19:33 | -21 | In target | 2015-01-30 12:54 | 2015-12-09 19:33 | Janice Wray
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:56 | S217008270002 | CAMBORNE MEWS (13-36) | 181055 | Completed | 12b | Medium | Responsive Item | The top hinge on the bin room door of flats 19 to 24 is broken and this door now does not shut fully. | This hinge should be replaced and the door adjusted so that the door shuts fully. The present situation where there is a hole straight through the flat entrance door means that this flat entrance door is not fulfilling the function of a fire rated door. | Responsive Repairs | John Tatham |  | re-fixed hinge COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-01-30 12:56 | 2015-03-31 12:57 | 2015-01-30 12:56 | 2015-09-21 17:04 | -60 | In target
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:57 | S217008270002 | CAMBORNE MEWS (13-36) | 181056 | Completed | 14 | Medium | Responsive Item | There is part of a brick missing from the ground floor level wall of the staircase entrance hall area of the staircase of flats 19 to 24. | I would recommend that this area of wall is looked at and a new brick inserted into the area where the current brick is half missing. | Responsive Repairs | John Tatham |  | replaced missing brick and pointing COMPLETED | 2015-09-16 | Fully Completed | Janice Wray | 2015-01-30 12:57 | 2015-03-31 12:58 | 2015-01-30 12:57 | 2015-09-21 17:05 | -60 | In target
FLORENCE HOUSE - 2014.08.14 | 2014-08-20 10:32 | S217010050012 | FLORENCE HOUSE | 158159 | Completed | 12 | High | Flat Door | The flat entrance door to flat 15 has been changed from the originally fitted fire rated flat entrance door. This is a tenanted dwelling and the presently fitted door is a six indented panelled door. | Can it please be confirmed that this flat entrance door if fitted by the TMO or its contractors is a certified 30 minute fire rated with the documentation to show this in case it is required by the enforcing authority of the FSO. Also is this new flat entrance door fitted with a self closing device and cold smoke seals etc to comply with the requirements of the Building Regulations? If this door was not fitted by the TMO or its contractors I would recommend that the occupier is asked to provide documentation showing that this door is a 30 minute fire rated door and that it is fitted with a self closing device capable of shutting the door fully onto its stops. | Responsive Repairs | Michael Lyons |  | no awswer 24/08, 27/08, 09/09,card left, 201526249 order - 201526249 | 2015-11-18 | Fully Completed | Janice Wray | 2014-08-20 10:32 | 2014-09-10 10:33 | 2014-08-20 10:32 | 2015-11-19 20:16 | -21 | In target | 2014-08-20 10:32 | 2015-11-25 20:15 | Janice Wray
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:11 | S217010470002 | FORELAND HOUSE | 196905 | Completed | 14a | High | Responsive Item | There is a hole in the wall lining to the right of flat 11's entrance door where a cable has been pasted through the wall and the brick has not been replaced/the wall lining not made good. | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-06-03 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-13 16:11 | 2015-06-03 16:14 | 2015-05-13 16:11 | 2016-02-02 19:53 | -21 | In target
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:15 | S217010470002 | FORELAND HOUSE | 196907 | Completed | 14b | High | Responsive Item | The cover plate of the cable duct outside of the ground floor level electrical room/ cupboard has been removed and not put back, it is now missing. | This cover plate should be replaced and fixed back correctly over the cable duct. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-06-03 | 201553986 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-05-13 16:15 | 2015-06-03 16:16 | 2015-05-13 16:15 | 2016-03-07 17:18 | -21 | In target
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:16 | S217010470002 | FORELAND HOUSE | 196909 | Completed | 14c | High | Responsive Item | The cover plate fixed over a cable duct on the 2nd floor level on the staircase landing has been removed and not secured them back again correctly and there is a large gap at the top of this cover plate now. | This cover plate should be re-fixed back correctly over the cable duct, to provide suitable fire stopping for the cable duct. | Responsive Repairs | John Tatham | 2015-06-03 | 201553995 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-05-13 16:16 | 2015-06-03 16:18 | 2015-05-13 16:16 | 2016-03-07 17:20 | -21 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:53 | S217008850003 | GADSDEN HOUSE | 185109 | Active | 12a | High | Responsive Item | The door of the basement area by flat 1 is damaged along the whole bottom edge and the hinge is also damaged so this door does not shut fully. | I do not think that this door can be repaired back to a fire rated door so I would recommend that a new 30 minute fire rated door fitted with intumescent strips and cold smoke seals is fitted in this location. | Responsive Repairs | John Tatham
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:54 | S217008850003 | GADSDEN HOUSE | 185110 | Completed | 12b | Medium | Responsive Item | The door frame of the electrical room/cupboard door at the basement level between flats 4 and 5 is damaged. | The architrave of this electrical room/cupboard door should be repaired. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 11:54 | 2015-04-25 11:55 | 2015-02-24 11:54 | 2015-11-27 20:55 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:56 | S217008850003 | GADSDEN HOUSE | 185111 | Completed | 12c | Medium | Responsive Item | The hopper to rubbish chute opening by flat 7 does not shut fully. | This hopper should be repaired or replaced so that it shuts fully. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 11:56 | 2015-04-25 11:58 | 2015-02-24 11:56 | 2015-11-27 20:56 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:58 | S217008850003 | GADSDEN HOUSE | 185114 | Completed | 12d | Low | Responsive Item | The covers of the TV boxes on the wall at the basement level between flats 4 and 5 are missing or damaged. | I would recommend that the covers of these TV boxes are replaced or mended so that they can be secured. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 11:58 | 2015-08-23 12:00 | 2015-02-24 11:58 | 2015-11-27 20:58 | -180 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:00 | S217008850003 | GADSDEN HOUSE | 185117 | Completed | 14a | Medium | Responsive Item | There is part of a row of block work missing from the wall at the base of the right hand side staircase, between flats 4 and 5 at the basement level, it appears that a cable has been installed here. | This block work should be replaced so that the fire rating of the wall, separating the basement area from the staircase is maintained and that of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 12:00 | 2015-04-25 12:01 | 2015-02-24 12:00 | 2015-11-27 20:59 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:05 | S217008850003 | GADSDEN HOUSE | 185125 | Completed | 14b | High | Responsive Item | There is a metal cover plate not fixed back correctly on the balcony wall between flats 19 and 20. | This metal inspection/cover plate should be re-fixed back correctly and securely to maintain the fire rated structure and provide suitable fire stopping for any cable duct. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 12:05 | 2015-03-17 12:07 | 2015-02-24 12:05 | 2015-11-27 21:00 | -21 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:07 | S217008850003 | GADSDEN HOUSE | 185127 | Completed | 14c | High | Responsive Item | There are cables hanging down at the ground floor level of the staircase between flats 4 and 5, these cables have been taped using masking tape to the ceiling. | These cables must be secured correctly to the wall or ceiling linings, they should now be in cased in metal conduit or on metal cable trays to comply with new wiring regulations requirements. | Responsive Repairs | John Tatham |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2015-02-24 12:07 | 2015-03-17 12:09 | 2015-02-24 12:07 | 2015-11-27 21:03 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:49 | S217012740008 | GREAVES TOWER 4-62 | 102344 | Completed | 16a | Medium | Responsive Item | The floor level and flat numbers signs are missing from the staircase landings on floor levels, 3, 7, 8, 9, 10, 11, 12, 13 and 14. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357304 | 2014-04-29 | Fully Completed | Michael Lyons | 2013-08-16 16:49 | 2013-10-15 16:52 | 2013-08-16 16:49 | 2014-05-02 10:13 | -60 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:53 | S217012740008 | GREAVES TOWER 4-62 | 102346 | Completed | 16b | Medium | Responsive Item | An exit sign has been displayed above the ground floor level staircase exit door and on the half landing above this door. There is only a single staircase in this building. | As there is only a single staircase in this building exit signage is not required, so for consistency reasons I would recommend that this 2 exit signs are removed as exit signage is not displayed elsewhere in this premises on the single staircase. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357304 | 2014-04-15 | Fully Completed | Michael Lyons | 2013-08-16 16:53 | 2013-10-15 16:54 | 2013-08-16 16:53 | 2014-05-02 10:23 | -60 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:47 | S217012740008 | GREAVES TOWER 4-62 | 102342 | Completed | 12c | High | Responsive Item | The self closing device fitted to the flat/lift lobby area fire doors on to the staircase on the 18th floor level needs adjusting or replacing so that it shuts the fire door fully. | The self closing device on this fire door should be adjusted, repaired or replaced so that the door shuts fully onto its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357304 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-08-16 16:47 | 2013-09-06 16:48 | 2013-08-16 16:47 | 2014-05-02 10:11 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:28 | S217012740008 | GREAVES TOWER 4-62 | 102336 | Completed | 8g | Low | Responsive Item | The doors of both riser cupboards on the 10th and 11th floor levels will not open along with the single doors of the cupboards on the 5th and 15h floor levels. | I would recommend that the locks fitted to these cupboard doors are repaired or replaced so that the doors can be opened. | Responsive Repairs | Jackie Gaikwad | 2014-02-14 | Block Job number 201357304 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-16 16:28 | 2014-02-12 16:30 | 2013-08-16 16:28 | 2014-05-02 10:23 | -180 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:32 | S217012740008 | GREAVES TOWER 4-62 | 102337 | Completed | 12a | High | Responsive Item | The two Georgian wired fire rated glazed vision panels in the flat entrance door of flat 9 have been removed and non fire rated stained glass inserted in place of the fire rated glazing. This door now appears not to have any fire rating to it. | I would recommend that this flat entrance door is checked to see that the glazing in it is fire rated glazing. If the glazing is not fire rated then the door should be replaced with a door complying with the requirements of the Building Regulations as the present door has been downgraded from the originally fitted door and is now of a lower structural standard. If a door is changed it must meet current Building Regulations requirements. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357304 | 2014-04-15 | Fully Completed | Michael Lyons | 2013-08-16 16:32 | 2013-09-06 16:33 | 2013-08-16 16:32 | 2014-05-02 10:08 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:15 | S217012740008 | GREAVES TOWER 4-62 | 102323 | Completed | 8a | High | Responsive Item | At the roof level the door to the area where the dry rising main outlet is located is damaged and is held shut by a piece of concrete slab leaned up against it. | I would recommend that this door is repaired or replaced and secured correctly with a lock that the Fire Service have a key for as the dry rising main is located within this area. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357304 | 2014-03-27 | Fully Completed | Michael Lyons | 2013-08-16 16:15 | 2013-09-06 16:16 | 2013-08-16 16:15 | 2014-05-02 10:07 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:29 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172141 | Completed | 1b | High | Responsive Item | At the time of this assessment the lighting was not working in the roof level room where the water tanks are located. | I would recommend that the lighting units in this roof level area are repaired or replaced so that they work correctly. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on 201552556 | 2016-02-16 | Fully Completed | Maria Ares | 2014-12-01 09:29 | 2014-12-22 09:30 | 2014-12-01 09:29 | 2016-02-17 11:02 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:22 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172163 | Completed | 12b | High | Responsive Item | The access door to the external roof from the internal corridor has had both of the "Gerda" locks removed from it, this door is now only secured by a normal latch type lock opened by a door handle. This door is now damaged and does not shut securely. | I would recommend that this door is repaired or replaced and that locks or a device is fitted to this roof door so that it can be secured fully and that the door does not flap in the wind and get damaged. | Responsive Repairs | John Tatham | 2014-12-22 | 201554098 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-01 10:22 | 2014-12-22 10:23 | 2014-12-01 10:22 | 2016-03-07 17:23 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172168 | Completed | 12d | High | Responsive Item | The fire door to the refuse chute room on the 14th floor level grounds and will not shut fully. | I would recommend that this door to the refuse chute room on the 14th floor level is repaired so that is does not ground and that the self closing device shuts the door fully onto its stops. | Responsive Repairs | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-01 10:25 | 2014-12-22 10:27 | 2014-12-01 10:25 | 2016-02-23 20:29 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:28 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172169 | Completed | 12e | High | Responsive Item | The fire door to the staircase from the lift lobby areas on the 2nd and 19th floor levels are damaged and do not shut fully. | I would recommend that these doors are repaired or replaced so that they shut fully. | Responsive Repairs | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-01 10:28 | 2014-12-22 10:28 | 2014-12-01 10:28 | 2016-02-23 20:33 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:29 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172170 | Completed | 12f | High | Responsive Item | On the 10th floor level the refuse chute hopper head is damaged - it's handle is missing and it does not shut fully | This hopper head to the rubbish chute on the 10th floor level should be repaired or replaced so that it shuts fully. | Responsive Repairs | John Tatham | 2014-12-22 | 201554019 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-01 10:29 | 2014-12-22 10:31 | 2014-12-01 10:29 | 2016-03-07 17:25 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:33 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172174 | Completed | 12h | High | Responsive Item | The door handle of the staircase door (separating lift lobby and staircase) is missing on the staircase side on the 13th floor level. | A new door handle should be fitted to this staircase door. | Responsive Repairs | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-12-01 10:33 | 2014-12-22 10:35 | 2014-12-01 10:33 | 2016-02-02 19:58 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:46 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172180 | Completed | 14b | High | Responsive Item | On the 2nd and the 15th floor levels the panels covering the cable ducts have been removed and not refitted correctly. One is held on with tape. | These covers should be fitted back correctly. . | Responsive Repairs | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-12-01 10:46 | 2014-12-22 10:47 | 2014-12-01 10:46 | 2016-02-02 20:01 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:25 | S217012770010 | GRENFELL WALK | 146388 | Completed | 1 | Medium | Communal Lighting | The covers of some of the lighting units located on the external balconies and staircases of Grenfell Walk are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of these lighting units are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | Responsive Repairs | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2014-06-02 12:25 | 2014-08-01 12:38 | 2014-06-02 12:25 | 2015-11-18 13:50 | -60 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:51 | S217012770010 | GRENFELL WALK | 146397 | Completed | 15a | High | Emergency Lighting | There are emergency lighting system/units installed on the balconies and the staircases of Upper Grenfell Walk. Where these emergency lighting units are installed though the positioning is haphazard. | I would recommend that emergency lighting units installed on the means of escape routes of Upper Grenfell Walk are checked against the requirements of British Standard 5266 Part 1 2011 and then additional units are installed where required. This will including the undertaking of the risk assessment section of the BS first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | Responsive Repairs | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade progra | 2015-12-14 | Fully Completed | Maria Ares | 2014-06-02 12:51 | 2014-06-23 12:54 | 2014-06-02 12:51 | 2015-12-15 11:23 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:54 | S217012770010 | GRENFELL WALK | 146398 | Completed | 15b | High | Emergency Lighting | There appear to be no emergency lighting system/units installed on the balconies and the staircases of Grenfell Walk, but it is hard to tell because the covers of the lights are dirty but the neon charging lights cannot be seen. | I would recommend that light units installed on the means of escape routes of Grenfell Walk are checked to see if they are also emergency lighting units. If they are not then no action is needed to install emergency lighting units but the light cover should be cleaned or replaced. If they are emergency lighting units then they should be tested and checked against the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. | Responsive Repairs | Alex Bosman |  | COMPLETE - INFORMATION ONLY AS EMERGENCY LIGHT TESTING IS NOT REQUIRED. | 2015-11-17 | Fully Completed | Maria Ares | 2014-06-02 12:54 | 2014-06-23 12:56 | 2014-06-02 12:54 | 2015-11-18 13:51 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 15:57 | S210008550002 | HARRIET HOUSE (1-20) | 197860 | Completed | 12 | High | Responsive Item | The door frames of both the ground floor electrical rooms/cupboards need to be re-fixed back to the brickwork. There are gaps between the frames and the brickwork. structure. | I would recommend that the frame of the ground floor electrical rooms/cupboards are re-fixed back to the brickwork with any gaps filled with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham | 2015-06-09 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-19 15:57 | 2015-06-09 16:00 | 2015-05-19 15:57 | 2016-02-02 20:04 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:01 | S210008550002 | HARRIET HOUSE (1-20) | 197861 | Completed | 14a | High | Smoke Alarms | Above the door of the ground floor level electrical room/cupboard by flat 1 there is a hole in the brickwork where a cable has been passed through and a repair has not made good. | The hole in the wall lining of this electrical room/ cupboard should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-06-09 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-05-19 16:01 | 2015-06-09 16:03 | 2015-05-19 16:01 | 2016-02-02 20:07 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:03 | S210008550002 | HARRIET HOUSE (1-20) | 197863 | Completed | 14b | High | Responsive Item | Part of the staircase landing ceiling has been cut away on the 2nd floor level by flat 11. | This staircase landing ceiling should be repaired using suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | John Tatham | 2015-06-03 | 201554019 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-05-19 16:03 | 2015-06-09 16:05 | 2015-05-19 16:03 | 2016-03-07 17:28 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:11 | S217008750001 | HAZLEWOOD TOWER | 133646 | Completed | 12b | High | Responsive Item | There is a large gap at the head of the door off the entrance lobby area which goes to the electrical intake room and the bulk storage area. This door set is now not 30 minute fire rated and smoke can easily pass through this gap. | I would recommend that this door is repaired or replaced so that this door is of 30 minute fire rating and will stop the passage of smoke into the ground floor level entrance lobby area. As required by the Building Regulations. Replacement FD30 door set contractor is Multi Installations. | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-07 14:11 | 2014-03-28 14:12 | 2014-03-07 14:11 | 2015-11-27 20:50 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:13 | S217008750001 | HAZLEWOOD TOWER | 133647 | Completed | 12c | High | Responsive Item | On floor levels 4, 7, 8, and 13 the hoppers/flaps to rubbish chutes are damaged and do not shut fully | The hoppers/flaps to the rubbish chutes openings on these levels should be repaired or replaced so that they shut fully. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 14:13 | 2014-03-28 14:13 | 2014-03-07 14:13 | 2015-11-12 16:25 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:17 | S217008750001 | HAZLEWOOD TOWER | 133650 | Completed | 12f | Low | Flat Door | The flap is missing from the letter box of flat 54 and the letter box is damaged, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that a new letter box and flap is fitted to the flat entrance door of flat 54 so that the compartmentation of the protected staircase is maintained. (tenanted flat) | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 14:17 | 2014-09-03 14:18 | 2014-03-07 14:17 | 2015-11-12 16:26 | -180 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:22 | S217008750001 | HAZLEWOOD TOWER | 133655 | Completed | 14 | High | Responsive Item | There is a steel plate fitted to cover over a hole in the wall lining of the staircase next to the refuse chute opening on the 4th floor level. This steel plate is not fixed to the wall fully. | I would recommend that the steel plate is securely fixed to the wall so that it does not fall off and there is a hole in the wall lining. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-07 14:22 | 2014-03-28 14:23 | 2014-03-07 14:22 | 2015-11-12 16:27 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:01 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153362 | Completed | 12 | Medium | Responsive Item | The nosing on two of the external steps from the patio area to the children's play area are damaged, this could cause a trip hazard. | The nosing on these external steps should be repaired. | Responsive Repairs | Michael Lyons | 2014-09-15 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-07-17 16:01 | 2014-09-15 16:02 | 2014-07-17 16:01 | 2016-02-02 20:09 | -60 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:48 | S217008850001 | HOLMEFIELD HOUSE | 130783 | Completed | 1a | High | Responsive Item | In the ground floor level electrical room near to flats 601 and 621 there is a hole in the floor with a large diameter black electrical cable coming through it. Is this cable providing the electricity to the new dwellings? | I would recommend that the floor slab in this electrical room is made good and if the electrical board in this room has been altered in any way has a new electrical certificate been provided for this board. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-02-19 16:48 | 2014-03-12 16:50 | 2014-02-19 16:48 | 2015-11-12 16:29 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:51 | S217008850001 | HOLMEFIELD HOUSE | 130786 | Completed | 1b | High | Communal Lighting | The light units in the residents storage area called B1 are damaged. | New light units should be fitted in this storage area and the electrical wiring completely checked. | Responsive Repairs | Alex Bosman |  | RMA CHECKED LIGHTS AND FOUND ALL WORKING FINE | 2015-11-17 | Fully Completed | Maria Ares | 2014-02-19 16:51 | 2014-03-12 16:52 | 2014-02-19 16:51 | 2015-11-18 14:49 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:07 | S217008850001 | HOLMEFIELD HOUSE | 130815 | Completed | 11 | Medium | Responsive Item | After some recent construction work to building the 3 new flats it was noticed that some pigeon netting covering a passageway has been removed by the contractors, this is next to flat 618. | The pigeon netting covering the passageway area next to flat 618 should be reinstated correctly. | Responsive Repairs | Alex Bosman | 2016-01-13 | Noted as information only | 2016-01-13 | Fully Completed | Maria Ares | 2014-02-20 09:07 | 2014-04-21 09:08 | 2014-02-20 09:07 | 2016-01-14 15:44 | -60 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:08 | S217008850001 | HOLMEFIELD HOUSE | 130816 | Completed | 21a | High | Responsive Item | The complete door leaf and a section of glass is missing from the door set from the lobby area next to flat 201, the door is in the cleaners cupboard next to flat 217. | I would recommend that the door is refitted and the missing section of glass is replaced in the door set. | Responsive Repairs | Alex Bosman | 2015-06-03 | Completed 2nd Dec 2015 | 2015-12-02 | Fully Completed | Janice Wray | 2014-02-20 09:08 | 2014-03-13 09:09 | 2014-02-20 09:08 | 2016-01-21 12:34 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:10 | S217008850001 | HOLMEFIELD HOUSE | 130817 | Completed | 12b | High | Responsive Item | The hinge of the lobby area door next to flat 601 is damaged and the door does not shut fully. | I would recommend that the door is repaired or replaced so that the door shuts fully onto its stops. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-02-20 09:10 | 2014-03-13 09:11 | 2014-02-20 09:10 | 2015-11-12 16:30 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:12 | S217008850001 | HOLMEFIELD HOUSE | 130818 | Completed | 12c | High | Responsive Item | The window looking out onto the open roof area near to flat 318 is damaged. | I would recommend that the glass in this window is replaced. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-02-20 09:12 | 2014-03-13 09:13 | 2014-02-20 09:12 | 2015-11-12 16:31 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:13 | S217008850001 | HOLMEFIELD HOUSE | 130820 | Completed | 12d | High | Responsive Item | 12d High The hoppers/flaps to the rubbish chutes are damaged, missing or do not shut fully in the following locations: 1. Near to flat 414 2. Near to flat 506 3. Near to flat 307 | These hoppers/flaps to the rubbish chutes openings should be repaired or replaced so that they shut fully or replaced if missing. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-02-20 09:13 | 2014-03-13 09:14 | 2014-02-20 09:13 | 2015-11-12 16:33 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:14 | S217008850001 | HOLMEFIELD HOUSE | 130821 | Completed | 12e | High | Responsive Item | There was cabling hanging down from the wall/cable ducts outside flat 207.These hanging cables could cause an obstruction of the means of escape routes. | The hanging cables should be securely fixed back to the wall or housed in the cable ducts. | Responsive Repairs | Alex Bosman |  | REFIXED 14M OF CABLE THAT WAS HANGING DOWN. COMPLETED | 2015-11-17 | Fully Completed | Maria Ares | 2014-02-20 09:14 | 2014-03-13 09:16 | 2014-02-20 09:14 | 2015-11-18 14:56 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:16 | S217008850001 | HOLMEFIELD HOUSE | 130824 | Completed | 12f | Medium | Responsive Item | The entrance door to flat 531 is damaged and is partly covered over with a piece of chipboard. | I would recommend that this flat entrance door is repaired or replaced. | Responsive Repairs | Alex Bosman |  |  | 2015-11-18 | Fully Completed | Janice Wray | 2014-02-20 09:16 | 2014-04-21 09:17 | 2014-02-20 09:16 | 2015-11-19 19:35 | -60 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:18 | S217008850001 | HOLMEFIELD HOUSE | 130825 | Completed | 12g | Medium | Responsive Item | The banister/hand rail on the staircase next to flat 404 is not securely fixed to the wall and is coming away. | I would recommend that the banister is fixed back to the wall securely so that it does not come away from the wall when a person is leaning on it allowing them to potentially fall down the stairs. | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-02-20 09:18 | 2014-04-21 09:19 | 2014-02-20 09:18 | 2015-11-25 21:55 | -60 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:21 | S217008850001 | HOLMEFIELD HOUSE | 130827 | Completed | 14a | High | Responsive Item | There appears to be hole through the wall of the electrical room into flat 405. | This hole in the wall should be filled in/repaired with a fire rated material. | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-02-20 09:21 | 2014-03-13 09:22 | 2014-02-20 09:21 | 2015-11-25 21:57 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:22 | S217008850001 | HOLMEFIELD HOUSE | 130830 | Completed | 14b | High | Responsive Item | There appears to be holes through the wall of the electrical room next to flat 207. | These holes in the walls should be filled in/ repaired with a fire rated material | Responsive Repairs | Alex Bosman |  |  | 2015-11-24 | Fully Completed | Janice Wray | 2014-02-20 09:22 | 2014-03-13 09:23 | 2014-02-20 09:22 | 2015-11-25 21:59 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:37 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171886 | Completed | 19e | High | Dry or Wet Riser | The door and box of the dry riser outlet located on the 1st floor level of the 500 section, riser number 10, by flat 514, is damaged. | This damaged dry riser box and the door to it should be repaired or replaced. | Responsive Repairs | Alex Bosman | 2014-12-19 | 201542483 - RD to monitor | 2016-03-13 | Partially Completed | Janice Wray | 2014-11-28 11:37 | 2014-12-19 11:38 | 2014-11-28 11:37 | 2016-03-14 11:29 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 11:18 | S217002640001 | INGELOW HOUSE | 204021 | Completed | 14 | High | Responsive Item | There is a hole in the wall linings in the electrical room by flat 33 where an electrical cables has been passed through the wall and the wall has not been made good | This hole in the wall lining should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall linings have been made good. | Responsive Repairs | John Tatham | 2015-07-31 | 201554025 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-30 11:18 | 2015-07-21 11:19 | 2015-06-30 11:18 | 2016-03-07 17:30 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:15 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181509 | Active | 1b | High | Responsive Item | I was told that if most of the wall mounted electrical heaters in this premises are all turned on, the RCDs on the distribution board have to be re-set. | I would strongly recommend that the electrical socket ring main circuit is checked to see that the electrical wiring is appropriate for the number heaters presently installed in this premises. If it is found not to be suitable when all of the electrical heaters are running then the recommendations of the electrician are to be actioned to rectify the situation. | Responsive Repairs | John Tatham |  |  |  |  | Cyril Morris | 2015-02-03 10:15 | 2015-02-24 10:17 |  |  | 407 | 407 days overdue
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:03 | B217009120001 | KENSAL HOUSE | 102852 | Completed | 12d | Medium | Responsive Item | The nosing on some of the stairs of the staircases in these buildings damaged or missing. There are too many areas to mention individually, this damaged or missing nosing could result in a trip and fall down the stairs. | I would recommend that a check of all the steps of the staircases is undertaken and an damaged or missing nosing is repaired or replaced. | Responsive Repairs | Jackie Gaikwad | 2013-09-17 | Areras completed that required immediate attention. | 2014-05-22 | Fully Completed | Michael Lyons | 2013-08-20 14:03 | 2013-10-19 14:05 | 2013-08-20 14:03 | 2014-06-18 15:46 | -60 | In target | 2013-08-20 14:03 | 2014-05-10 08:13 | Michael Lyons
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:07 | B217009120001 | KENSAL HOUSE | 102855 | Completed | 15a | High | Responsive Item | The light unit on the staircase landing outside the entrance doors to flats 10 and 11 has contractors label on it stating" Fault Do Not Use" | Can this light unit be checked to see if it is working correctly, this could also be an emergency light unit. If it is working correctly why is the label attached to it? If it is not working it should be repaired or replaced immediately. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Block Job number 201357315 | 2014-04-03 | Fully Completed | Michael Lyons | 2013-08-20 14:07 | 2013-09-10 14:10 | 2013-08-20 14:07 | 2014-05-02 12:30 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 09:46 | B217009120001 | KENSAL HOUSE | 102739 | Completed | 1b | Low | Responsive Item | On the staircase landing near to flats 45 and 46 and in the staircase by flats 20 and 21, and also flats 22 and 23 the covers are missing from the BT telephone boxes and wires are hanging out of them. | I would recommend that a new covers are fitted to these BT boxes so that the wires are enclosed within them. | Responsive Repairs | Jackie Gaikwad | 2014-02-03 | Block Job number 201357315 | 2014-04-16 | Fully Completed | Michael Lyons | 2013-08-20 09:46 | 2014-02-16 10:02 | 2013-08-20 09:46 | 2014-05-02 12:27 | -180 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:33 | B217009120001 | KENSAL HOUSE | 102798 | Completed | 3 | High | Responsive Item | The fire fighter entry over ride device fitted to the staircase entrance doors of the staircase to flats 1 to 7, 8 to 16, 49 to 58 and 59 to 68 did not function and release the locking device on the doors and open the doors. All the other entrance doors fitted with them worked correctly. | The fire fighter entry over ride devices fitted to these entrance doors should be repaired or replaced so that they releases the locking device fitted to the entrance doors. The over ride device allows the Fire and Rescue Service to access the staircase/ building in an emergency without the use of a key. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Site job number 201357315 The device was tested and found to be functional on the 9/4 and 20/4, additional tests are due to be scheduled to ensure taht there is no intermittant fault | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-20 11:33 | 2013-09-10 11:35 | 2013-08-20 11:33 | 2014-05-07 20:26 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 12:49 | B217009120001 | KENSAL HOUSE | 102829 | Completed | 12a | High | Responsive Item | The entrance door to flat 23 has been changed from the originally fitted door, it is not known if the door is a 30 minute self closing fire rated door. | I would recommend that the entrance door to flat 23 is checked to see that it is a 30 minute self closing fire rated door this includes the glazing in this door. If it is not a new 30 minute fire rated self closing door complying with the requirements of the Building Regulations should be fitted. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | Please transfer this job to the FRA. Carl Stokes was unable to obtain access to this flat but is confident from his visual inspection / assessment of the external face that the door and the integral glazing in non-fire-rated. Please arrange for a FD30 door with self-closer to be fitted and fully complete once this is installed. 201554029 - RD confirm completion | 2016-03-05 | Fully Completed | Michael Lyons | 2013-08-20 12:49 | 2013-09-10 12:51 | 2013-08-20 12:49 | 2016-03-07 17:34 | -21 | In target | 2013-08-20 12:49 | 2016-03-12 17:32 | Janice Wray
KENSAL HOUSE - 2013.06.01 | 2013-08-20 12:51 | B217009120001 | KENSAL HOUSE | 102830 | Completed | 12b | High | Responsive Item | The door and frame to the residents storage cupboard next to flat 18 is badly damaged and this door set is now not 30 minute fire rated. | I would recommend that this storage cupboard door is replaced with a new lockable 30 minute fire rated door complying with all the requirements of the Building Regulations and that the frame is repaired or instead a complete new door set is fitted. | Responsive Repairs | Jackie Gaikwad | 2013-09-10 | site job number 201357315 Ordered and due for instillation on 07/05 RD confirm completion | 2016-02-22 | Fully Completed | Michael Lyons | 2013-08-20 12:51 | 2013-09-10 13:42 | 2013-08-20 12:51 | 2016-02-23 22:21 | -21 | In target | 2013-08-20 12:51 | 2014-05-14 15:35 | Janice Wray
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:20 | S217007970011 | KENSAL COMMUNITY OFFICE | 181611 | Active |  | Information Only | Responsive Item | Some of the walls and ceiling in the community area are still waiting to be painted after a water leak over a year ago. Once the redecoration is completed then fire signage can be displayed. | I would recommend that the redecoration of this area is completed so that the fire signage can be displayed. | Responsive Repairs | John Tatham
KENSINGTON MANSIONS - 2015.04.09 | 2015-04-27 14:39 | S217006800001 | KENSINGTON MANSIONS | 194311 | Completed | 12a | High | Responsive Item | There is a glazed door and screen separating the under the staircase cupboard from the ground floor entrance hall area. The glazing in the screens and the door do not appear to be constructed of fire rated materials. This area is used by the contract cleaner as a storage area. | The door and screens of this ground floor under staircase cupboard must be constructed of fire rated materials if this area is to be used as a storage area. The staircase should also be underdrawn. I would recommend that the screen and door of this cupboard are up graded to a minimum of 30 minutes fire rated construction and the staircase is underdrawn. Alternatively the cupboard could be kept completely empty/sterile and secured locked shut so that no items can be placed within it. | Responsive Repairs | John Tatham | 2015-05-29 | 201554042 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-04-27 14:39 | 2015-05-18 14:41 | 2015-04-27 14:39 | 2016-03-07 17:36 | -21 | In target
KENSINGTON MANSIONS - 2015.04.09 | 2015-04-27 14:42 | S217006800001 | KENSINGTON MANSIONS | 194313 | Completed | 12b | High | Responsive Item | One of the upright rails of the staircase is missing on the ground floor near flats 67A and B. | This upright rail of the staircase on the ground floor by flats 67A and B should be replaced. | Responsive Repairs | John Tatham | 2015-05-18 | 201554048 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-04-27 14:42 | 2015-05-18 14:43 | 2015-04-27 14:42 | 2016-03-07 17:38 | -21 | In target
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 11:43 | S217002180001 | KEPPEL HOUSE | 200432 | Completed | 3 | High | Responsive Item | The steel shut off plate built into the base of the refuse chute in the bin room is missing, the steel shut off plate is so that the refuse chute can be isolated from the bin room. | I would recommend that a new steel shut off plate is fitted at the base of this refuse chute in the bin room so that the refuse chute can be isolated from the bin room. | Responsive Repairs | John Tatham | 2015-06-29 | 201554055 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-08 11:43 | 2015-06-29 11:44 | 2015-06-08 11:43 | 2016-03-07 17:40 | -21 | In target
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:11 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164644 | Completed | 12a | High | Responsive Item | The door to the first meeting has a hole straight through it where the lock has been removed. | A new lock should be fitted to this door or a new 30 minute self closing fire rated doors fitted, so this meeting room is fire separated from the entrance hall/lobby area. | Responsive Repairs | John Tatham | 2014-10-08 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-10-09 11:11 | 2014-10-30 11:12 | 2014-10-09 11:11 | 2016-02-23 22:24 | -21 | In target
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:20 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164652 | Completed | 12c | Information Only | Responsive Item | Recommendation The door to the end meeting room has a stable door on it, this door is not fire rated or fitted with a self closing device. | I would recommend that this door is replaced with a 30 minute self closing fire rated door so that this room is fire separated from the entrance hall/lobby area. | Responsive Repairs | John Tatham | 2015-04-07 | 201554061 RD confirm completion | 2016-03-05 | Fully Completed |  |  |  | 2014-10-09 11:20 | 2016-03-07 17:43
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-06 16:21 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164190 | Completed | 3 | High | Responsive Item | It appears that the top hinge of the right hand side door of the double entrance doors has dropped, this door is not shut fully by the self closing device. | I would recommend that the door is checked and repaired so that the entrance doors can be shut fully by the self closing devices. | Responsive Repairs | John Tatham | 2014-10-28 | 201554066 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-10-06 16:21 | 2014-10-28 14:09 | 2014-10-06 16:21 | 2016-03-07 17:45 | -21 | In target
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 09:11 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164220 | Active | 12a | High | Responsive Item | There has been a new fire rated door set installed into the waiting room area from the entrance hall area, this door has been fitted with a magnetic lock. There has been no manual override button, green button, fitted next to this door to manually open it. You can only open this door from behind the reception desk so persons can be trapped in the waiting room. | A manual over ride button must be installed next to this door on the waiting room side. Inner face so that this door can be opened by a person stood next to the door. This is a British Standard requirement when a magnetic lock is fitted to a door. | Responsive Repairs | John Tatham |  |  |  |  | Cyril Morris | 2014-10-07 09:11 | 2014-10-28 14:11 |  |  | 526 | 526 days overdue
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 14:17 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164296 | Completed | 14a | High | Responsive Item | It appears that an air conditioning unit has been removed from the wall in the office and there is a hole though this wall into the garage at presently covered by a plastic vent. | This hole in the wall should be fire stopped to the same standard as the concrete wall, a minimum though of 60 minutes fire rating, the plastic vent covers can be replaced for aesthetic reason if required. | Responsive Repairs | John Tatham | 2014-10-28 | 201554066 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-10-07 14:17 | 2014-10-28 14:19 | 2014-10-07 14:17 | 2016-03-07 17:47 | -21 | In target
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 14:19 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164297 | Completed | 14b | High | Responsive Item | There are holes in the wall lining within the cupboard in the office. | These holes in the wall lining should be fire stopped to the same standard as the concrete wall, a minimum though of 60 minutes fire rating, the plastic vent covers can be replaced for aesthetic reason if required. | Responsive Repairs | John Tatham | 2014-10-28 | 201554069 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-10-07 14:19 | 2014-10-28 14:20 | 2014-10-07 14:19 | 2016-03-07 17:50 | -21 | In target
LEDBURY HOUSE | 2015-03-26 16:04 | S217012270005 | LEDBURY HOUSE | 190061 | Completed | 14 | High | Responsive Item | There is a vent in the compartment wall between the bin storage area and the under stairs cupboard of the staircase of flats 11 to 18 that could allow the passage of flames and smoke between the 2 areas. | This wall between the bin area and this cupboard should be made a minimum of 30 minutes fire rated so fire separating these 2 areas. If this fire compartmentation is not undertaken very soon then a new 30 minute fire rated door must be fitted to the under staircase cupboard to stop smoke etc entering the staircase enclosure. This is because the presently fitted door to the staircase cupboard has rows of air holes drilled into it. | Responsive Repairs | John Tatham |  | 201529229, removed vent and bricked up | 2015-10-02 | Fully Completed | Janice Wray | 2015-03-26 16:04 | 2015-04-16 16:06 | 2015-03-26 16:04 | 2015-10-07 13:06 | -21 | In target
LONSDALE HOUSE-2012.12.20 | 2014-05-15 15:25 | S217012270006 | LONSDALE HOUSE | 144058 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide and dry powder fire extinguishers located in the basement water pump room are out of test date according to the RGE servicing labels, the last test date being December 2009. | The fire extinguishers located in the basement water pump room should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | Responsive Repairs | Michael Lyons | 2016-01-21 | AP confirmed service complete 8.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-05-15 15:25 | 2014-06-05 15:27 | 2014-05-15 15:25 | 2016-01-22 13:16 | -21 | In target
LONSDALE HOUSE-2012.12.20 | 2014-05-15 15:28 | S217012270006 | LONSDALE HOUSE | 144060 | Active | 23b | High | Fire Extinguisher | The carbon dioxide fire extinguisher located within flat number 1(caretakers room) is out of test date according to the RGE servicing labels, the last test date being March 2013. | This fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. I would recommend that a fire blanket is provided in the kitchen area of this flat. | Responsive Repairs | Michael Lyons |  |  |  |  | Clare Davis System Administration | 2014-05-15 15:28 | 2014-06-05 15:30 |  |  | 671 | 671 days overdue
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:47 | S217010570003 | LOWERWOOD COURT | 133672 | Completed | 3 | High | Responsive Item | Some of the glass in the windows of the ground floor level cleaners area is broken or cracked and there are gaps in the glass where the glass does not go to the top of the window frame. | These gaps in the windows or where the glass is cracked and broken could allow persons to break into the cleaners area or to set fire to the rooms. I would recommend that the broken/ cracked panes of glass are replaced and any gaps in the windows filled in to stop any arson attacks. | Responsive Repairs | Alex Bosman |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-03-07 14:47 | 2014-03-28 14:49 | 2014-03-07 14:47 | 2015-12-14 16:06 | -21 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:52 | S217010570003 | LOWERWOOD COURT | 133678 | Completed | 14 | High | Boiler | The pipes from the temporary boiler to the basement boiler room of the residential area run through the lower floor level of this car park. Large holes have been made in the basement boiler room wall from the car park. | These large holes should be filled in immediately with bricks and fire rated materials to the fire rating of the original party wall. | Responsive Repairs | Alex Bosman |  | Works will be completed as part of temporary boiler works. | 2015-10-28 | Fully Completed | Gillian Kennedy | 2014-03-07 14:52 | 2014-03-28 14:57 | 2014-03-07 14:52 | 2015-10-29 15:10 | -21 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:10 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205668 | Completed | 14c | High | Responsive Item | The covers of the duct work have been removed between flats 19 and 20 and not put back correctly. | I would recommend that the covers of this duct is replaced correctly. | Responsive Repairs | John Tatham | 2015-07-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-09 09:10 | 2015-07-30 09:11 | 2015-07-09 09:10 | 2016-02-02 20:12 | -21 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:14 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205670 | Completed | 17 | High | Responsive Item | The electrical hardwired heat detector/alarm fitted in the kitchen of flat 48 is hanging off the ceiling and does not appear to be workings. This defective heat detector has been reported to the TMO help line on more than one occasion according to the occupant. | I would recommend that the heat detector/alarm fitted in the kitchen of this flat is repaired or replace immediately. | Responsive Repairs | John Tatham | 2015-07-30 | 201554093 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-07-09 09:14 | 2015-07-30 09:15 | 2015-07-09 09:14 | 2016-03-07 17:52 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 09:57 | S217010050008 | MARLEY HOUSE | 143626 | Active | 1b | Medium | Responsive Item | The covers of some of the lighting units located on the external roof area and in the roof space area of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units located at the roof level of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | Responsive Repairs | Michael Lyons |  |  |  |  | Clare Davis System Administration | 2014-05-14 09:57 | 2014-07-13 10:00 |  |  | 633 | 633 days overdue
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:01 | S217010050008 | MARLEY HOUSE | 143629 | Completed | 3a | Low | Responsive Item | The extractor fan in the window of flat 1 onto the walkway area has been removed and there is now a hole in this pane of glass where the extractor fan used to be. Any smoke etc can now come straight though this hole from the flat onto the balcony. | I would recommend that this hole in the glass of flat 1's window in filled in, this can be done by fitting a new extractor fan or replacing the piece of glass. | Responsive Repairs | Michael Lyons | 2014-11-10 | 201554094 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-05-14 10:01 | 2014-11-10 10:03 | 2014-05-14 10:01 | 2016-03-07 17:55 | -180 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:04 | S217010050008 | MARLEY HOUSE | 143630 | Completed | 3b | Low | Responsive Item | The bathroom window of flat 6 is covered over with a piece of cardboard, if this window is broken the cardboard is will not stop any smoke etc from coming from the flat onto the balcony. | I would recommend that a new piece of glass is fitted into this window or a new window fitted. | Responsive Repairs | Michael Lyons | 2014-11-01 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-05-14 10:04 | 2014-11-10 10:10 | 2014-05-14 10:04 | 2016-02-23 22:27 | -180 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:31 | S217010050008 | MARLEY HOUSE | 143645 | Completed | 16b | High | Responsive Item | The "Push Bar to Open" signs are missing on each of the exit doors at the base of the staircases at the ground floor level. | A "Push Bar to Open" signs should be displayed on each of the ground floor final exit doors at the base of each staircase. | Responsive Repairs | Michael Lyons | 2014-06-04 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-05-14 10:31 | 2014-06-04 10:32 | 2014-05-14 10:31 | 2016-02-02 20:16 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:33 | S217010050008 | MARLEY HOUSE | 143647 | Completed | 16c | High | Responsive Item | There is no sign displayed in the ground floor level entrance lobby area informing the emergency services which flats are located on which floor level. There are signs on all of the upper floor levels which are permanently fixed to the wall and in a large font. | I would recommend that a sign is displayed in the ground floor level entrance lobby area showing which flat numbers are located on which floor level. This sign should be permanently fixed to the wall by the lifts and in a large font. | Responsive Repairs | Michael Lyons | 2014-06-04 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-05-14 10:33 | 2014-06-04 10:34 | 2014-05-14 10:33 | 2016-02-02 20:20 | -21 | In target
MATTHEW CLOSE, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 10:21 | S217009400001 | MATTHEW CLOSE (1-28) | 225100 | Completed | 12a | High | Responsive Item | The Georgian wired fire rated glass in the vision panel of flat 8's entrance door has been replaced with a piece of clear glass, which does not appear to be marked as fire rated glass. | Can it please be confirmed that the clear glass in the vision panel of flat 8's entrance doors is fire rated glazing. If it is not then it should be replaced with a piece of fire rated glass immediately which has been correctly fitted. RD - Alan Bro | Responsive Repairs | Alan Brooks | 2015-11-23 | 201554150 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-11-02 10:21 | 2015-11-23 10:22 | 2015-11-02 10:21 | 2016-03-07 17:59 | -21 | In target
MORLAND HOUSE- 2015.06.22 | 2015-06-29 12:01 | S217009210003 | MORLAND HOUSE | 203799 | Completed | 14 | High | Responsive Item | There is a hole in the wall linings over flat 15's entrance door where cable has been passed through the wall and a repair not made good. | This hole in the wall lining over flat 15's door should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | John Tatham | 2015-07-20 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-06-29 12:01 | 2015-07-20 12:02 | 2015-06-29 12:01 | 2016-02-02 20:23 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 15:45 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151233 | Completed | 12 | Information Only | Responsive Item | There is present not a self closing device fitted to the kitchen fire door, there is escape in 2 directions in this building but by closing this door the compartmentation in the building will be improved. . | I would recommend that consideration is given to the fitting of self closing devices to the kitchen fire door and also the door to the community room from the corridor. | Responsive Repairs | Michael Lyons | 2014-12-28 | 201554155 RD confirm completion | 2016-03-05 | Fully Completed |  |  |  | 2014-07-01 15:45 | 2016-03-07 18:01
NOTTING BARN ROAD, FLATS 1 TO 12 - 2015.10.13 | 2015-10-21 12:48 | S217009560001 | NOTTING BARN ROAD (1-6) | 223090 | Completed | 12a | High | Responsive Item | At the ground and 1st floor levels of both staircases the frames of the lobby doors onto the staircase landings are not sealed to the brick work fully. There are gaps between the door frames and the brickwork which could allow the passage of smoke and this down grades the structural fabric of this building. | I would recommend that the gaps between the door frames of all of the lobby to staircase doors and the brick work are filled using suitable fire rated materials. This is to maintain the fire rating of the structure of this building and stop the passage of smoke into the staircase enclosure. | Responsive Repairs | Alan Brooks | 2015-11-11 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-10-21 12:48 | 2015-11-11 12:49 | 2015-10-21 12:48 | 2016-02-23 22:32 | -21 | In target
NOTTING BARN ROAD, FLATS 1 TO 12 - 2015.10.13 | 2015-10-21 12:50 | S217009560001 | NOTTING BARN ROAD (1-6) | 223092 | Completed | 12b | High | Responsive Item | The lock fitted to the door which gives access to the entrance door of flat 5 has been removed and now there is a hole straight through this fire rated door. | The lock should be put back in this hole so that this door is maintained as a fire rated door or a new self closing 30 minute fire rated door should be fitted. This new door should comply with all of the requirements of the current Building Regulations. | Responsive Repairs | Alan Brooks | 2015-11-15 | 201554159 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-10-21 12:50 | 2015-11-11 12:55 | 2015-10-21 12:50 | 2016-03-07 18:04 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:44 | S217010030001 | OCTAVIA HOUSE | 205867 | Completed | 12b | High | Responsive Item | The doors/flaps to rubbish chutes by flats, 66 to 68 and 27 and 28 are damaged and do not shut fully | The doors/flaps to the rubbish chutes openings by these flats should be repaired or replaced so that they shut fully. | Responsive Repairs | John Tatham | 2015-07-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-09 14:44 | 2015-07-30 14:46 | 2015-07-09 14:44 | 2016-02-02 20:28 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:48 | S217010030001 | OCTAVIA HOUSE | 205869 | Completed | 12d | High | Responsive Item | The gerda lock on the gate to the roof by flats 44 to 46 is open and could not be locked shut. | I would recommend that the lock on this gate is repaired or replaced so that this gate can be secured shut. | Responsive Repairs | John Tatham | 2015-07-30 | 201554247 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-07-09 14:48 | 2015-07-30 14:50 | 2015-07-09 14:48 | 2016-03-07 18:06 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:03 | S217010030001 | OCTAVIA HOUSE | 102889 | Completed | 12b | High | Responsive Item | Above the entrance door to flat 14 a vent has been installed in the transom light area, this is a fire rated part of the buildings structure. | I would recommend that this vent is removed from the transom light area above this flat entrance door and this area reinstated back to be a fire rated part of the buildings structure. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357318 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-20 15:03 | 2013-09-10 15:03 | 2013-08-20 15:03 | 2014-05-07 20:23 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:04 | S217010030001 | OCTAVIA HOUSE | 102891 | Completed | 12c | Medium | Responsive Item | The doors/flaps to rubbish chutes by flats, 15 and 16 , 27 and 28 also 31 and 32 are damaged and do not shut fully | The doors/flaps to the rubbish chutes openings by these flats should be repaired or replaced so that they shut fully. | Responsive Repairs | Jackie Gaikwad | 2014-11-04 | Site job number 201357318 All bin chute works are contracted out and will be completed 21/05 RD confirm completion | 2016-02-22 | Fully Completed | Michael Lyons | 2013-08-20 15:04 | 2013-10-19 15:07 | 2013-08-20 15:04 | 2016-02-23 22:35 | -60 | In target | 2013-08-20 15:04 | 2014-05-14 15:36 | Janice Wray
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:12 | S217010030001 | OCTAVIA HOUSE | 102898 | Completed | 14 | High | Responsive Item | Part of the panelling in the staircase enclosure has been removed and not correctly been put back by flats 49 and 50 also by flats 15 and 16. | These pieces of boarding should be correctly fixed/secured back in place. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad |  | Block job number 201357318 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-20 15:12 | 2013-09-10 15:30 | 2013-08-20 15:12 | 2014-05-06 08:26 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:57 | S217010050005 | PICKWICK HOUSE | 158121 | Completed | 12 | High | Flat Door | The letter box in the flat entrance door to flat 23 is damaged and hanging off the door. (Tenanted flat.) | This letter box should be screwed back to the flat entrance door or a new letter and flap fitted. The present situation where there is a hole straight through the flat entrance door means that this flat entrance door is not fulfilling the function of a fire rated door. | Responsive Repairs | Michael Lyons | 2014-09-09 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-08-19 15:57 | 2014-09-09 15:59 | 2014-08-19 15:57 | 2016-02-02 20:36 | -21 | In target
POND HOUSE, FLATS 1 TO 32 - 2015.07.16 | 2015-09-01 14:12 | S217004267702 | POND HOUSE (1-32) | 214349 | Completed | 3 | High | Responsive Item | The staircase entrance door for flats 1 to 16 is damaged, the hinge I believe and this door does not now close. A contractor appears to have tried to get this door to close by removing some of the floor tiles. This has now made the floor in the doorway uneven. | I would recommend that this entrance door is repaired or replace as soon as possible because presently the door does not shut fully so anybody can just walk into this part of the building. I would also recommend that the damaged floor surface is also repaired so that the floor surface is not uneven. | Responsive Repairs | Alan Brooks | 2016-09-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-01 14:12 | 2015-09-22 14:14 | 2015-09-01 14:12 | 2016-02-02 20:39 | -21 | In target
POND HOUSE, FLATS 1 TO 32 - 2015.07.16 | 2015-09-01 14:14 | S217004267702 | POND HOUSE (1-32) | 214351 | Completed | 14a | High | Responsive Item | Next to flat 9's entrance door a pane of fire rated glazing is missing in the side screen of the door and a piece of cardboard has been inserted in the hole. | A new piece of fire rated glazing should be fitted in the side screen by flat 9's entrance door. | Responsive Repairs | Alan Brooks | 2015-09-22 | 201554260 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-01 14:14 | 2015-09-22 14:23 | 2015-09-01 14:14 | 2016-03-07 18:08 | -21 | In target
POND HOUSE, FLATS 1 TO 32 - 2015.07.16 | 2015-09-01 14:24 | S217004267702 | POND HOUSE (1-32) | 214353 | Completed | 14b | Medium | Responsive Item | On each landing level of each staircase the light fitting have been replaced, where the old light fittings have been removed the holes in the ceiling lining have not been repaired or made good. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-10-31 | 201554211 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-01 14:24 | 2015-10-31 14:25 | 2015-09-01 14:24 | 2016-03-07 18:11 | -60 | In target
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 08:56 | S217004267703 | POND HOUSE (33-47) | 214211 | Completed | 12 | High | Responsive Item | The original lock has been removed from the ground floor electrical room door and there is now a large hole in this fire rated door. | I would recommend that the hole in the door where the lock has been removed in filled in with a suitable fire rated material so that the integrity of the fire door is maintained. Or a new 30 minute fire rated door is fitted. | Responsive Repairs | Alan Brooks | 2015-09-22 | 20155428 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-01 08:56 | 2015-09-22 08:57 | 2015-09-01 08:56 | 2016-03-07 18:13 | -21 | In target
PURCELL HOUSE- 2015.01.28 | 2015-02-03 11:17 | S217012760009 | PURCELL HOUSE | 181541 | Completed | 14 | Medium | Responsive Item | Cover plates have been removed from next to the flat entrance doors of flats 1 and 3 at low level and not fitted back correctly. | I would recommend that these cover plates are correctly fixed back onto the walls. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-04-04 | RD confirnm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-02-03 11:17 | 2015-04-04 11:18 | 2015-02-03 11:17 | 2016-02-02 20:42 | -60 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:50 | S217010420002 | RAYMEDE TOWER | 148301 | Completed | 3 | High | Responsive Item | The fire fighter entry over ride device fitted to the main entrance door of this did not function easily and release the locking device on the door. The device fitted to the other entrance door worked correctly. | The fire fighter entry over ride devices fitted to the main entrance door should be repaired or replaced so it releases the locking device fitted to this main entrance door. The over ride device allows the Fire and Rescue Service to access the staircase/ building in an emergency without the use of a key. | Responsive Repairs | Michael Lyons | 2016-02-16 | S&M tested; confirmed all working 27.1.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2014-06-11 17:50 | 2014-07-02 17:51 | 2014-06-11 17:50 | 2016-02-17 11:03 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:53 | S217010420002 | RAYMEDE TOWER | 148303 | Completed | 12a | High | Responsive Item | The door handles are missing from the lift lobby to staircase doors on the 2nd floor level, there are now holes straight through these doors. | New door handles should be fitted to these doors immediately or new fire rated self closing doors fitted instead. | Responsive Repairs | Michael Lyons | 2014-07-02 | 201554204 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-06-11 17:53 | 2014-07-02 17:54 | 2014-06-11 17:53 | 2016-03-07 18:23 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:54 | S217010420002 | RAYMEDE TOWER | 148304 | Completed | 12b | High | Responsive Item | The left hand side door, of the staircase to lift lobby area, if looking from the staircase side does not shut fully. | This door and the self closing device should be checked and the door repaired or a new self closing device fitted so that this fire door closes fully. | Responsive Repairs | Michael Lyons | 2014-07-02 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-06-11 17:54 | 2014-07-02 17:55 | 2014-06-11 17:54 | 2016-02-23 22:41 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:55 | S217010420002 | RAYMEDE TOWER | 148305 | Completed | 12c | Medium | Responsive Item | On floor levels 3, 7 and 10 the door flaps/hoppers to rubbish chutes are damaged and do not shut fully | The door flaps/hopper to the rubbish chutes openings on these levels should be repaired or replaced so that they shut fully. | Responsive Repairs | Michael Lyons | 2014-08-10 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-06-11 17:55 | 2014-08-10 17:56 | 2014-06-11 17:55 | 2016-02-02 20:44 | -60 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:57 | S217010420002 | RAYMEDE TOWER | 148306 | Completed | 14 | High | Responsive Item | In the staircase enclosure there is a cable duct, the covers have been removed from this duct on some landings and are now missing or not replaced correctly. In other cases the original metal covers have been replaced with thin pieces of plywood fitted instead. | Where covers are missing or have been replaced with thin plywood they should be replaced with a suitable material capable of resisting fire. These covers could have been removed when the digital TV cabling was installed. | Responsive Repairs | Michael Lyons | 2014-07-02 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-06-11 17:57 | 2014-07-02 17:58 | 2014-06-11 17:57 | 2016-02-02 20:47 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:01 | S217010420002 | RAYMEDE TOWER | 148309 | Completed | 16a | Medium | Responsive Item | The floor numbers are not displayed in the lift lobby areas or the staircase landings of this building. These floor numbers will aid the fire service if there is an incident in this building. | I would recommend that the floor numbers are painted on the wall of the lift lobby area. Opposite the lifts and on each staircase landings of this building where there is a balcony. | Responsive Repairs | Michael Lyons | 2014-08-10 | 201554193 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-06-11 18:01 | 2014-08-10 18:02 | 2014-06-11 18:01 | 2016-03-07 18:27 | -60 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:47 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215779 | Completed | 1 | High | Responsive Item | An electrical cable in conduit is hanging down from the wall by flat 3B's entrance door. | This cable and the conduit should be fixed back to the wall correctly. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 16:47 | 2015-09-30 16:49 | 2015-09-09 16:47 | 2016-02-02 20:56 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:03 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215796 | Completed | 12b | High | Responsive Item | The lock on the door of the electrical room/cupboard by flat 1B is damaged. | The lock on this door should be repaired or replaced so that this door can be secured locked shut. | Responsive Repairs | Alan Brooks | 2015-09-30 | 201554188 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-09 17:03 | 2015-09-30 17:04 | 2015-09-09 17:03 | 2016-03-07 18:31 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:05 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215797 | Completed | 12c | High | Responsive Item | 12c High The flat entrance door and the door frame of flat 47B is damaged around the lock area. TENANTED FLAT Order 201520813 raised | This door and door frame should be repaired if possible or a new self closing 30 minute fire rated door should be fitted, complying with all the requirements of the current Building Regulations. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-09 17:05 | 2015-09-30 17:07 | 2015-09-09 17:05 | 2016-02-23 22:45 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:08 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215799 | Completed | 12d | High | Responsive Item | The self closing devices on the staircase to lobby area doors by flats 5A and B and also by flats 33A and B are damaged and do not shut these doors. | These self closing devices should be repaired or replaced so that they close these fire doors fully onto their stops. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-09 17:08 | 2015-09-30 17:09 | 2015-09-09 17:08 | 2016-02-23 22:47 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:11 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215804 | Completed | 12f | High | Responsive Item | In the staircase up to flats 11A and B and also in the staircase up to flats 39A and B the carpet is damaged and could be a trip hazard. | I would recommend that the damaged areas of carpet are repaired or replaced so that this carpet is not a trip hazard.. | Responsive Repairs | Alan Brooks | 2015-09-30 | 201554180 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-09 17:11 | 2015-09-30 17:12 | 2015-09-09 17:11 | 2016-03-07 18:33 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:04 | S217010180014 | ST MARKS GROVE 13-48 | 203727 | Completed | 12c | High | Responsive Item | The fire rated glazing in the transom light area above flat 31's entrance door is cracked. | I would recommend that this cracked piece of fire rated glazing is replaced with a new piece of fire rated glazing. | Responsive Repairs | John Tatham | 2015-07-20 | 201554177 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-29 10:04 | 2015-07-20 10:05 | 2015-06-29 10:04 | 2016-03-07 18:35 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:08 | S217010180014 | ST MARKS GROVE 13-48 | 203732 | Completed | 12e | High | Responsive Item | The storage cupboard door next to flats 38 has air holes drilled through the fire door and the one next to flat 39 has had a vent installed in the top part of this fire door. These doors are not now fire rated. | I would recommend that the vent and holes in these cupboard doors are filled in or covered over with a suitable fire rated material or the doors replaced with new fire rated ones. Alternatively the cupboards could be emptied out of all items and secured locked shut and not used. | Responsive Repairs | John Tatham | 2015-07-22 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-06-29 10:08 | 2015-07-20 10:09 | 2015-06-29 10:08 | 2016-02-23 22:50 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:18 | S217008220100 | STABLE WAY SITE | 105902 | Completed | 16b | High | Responsive Item | There is no push bar to open sign is presently missing from the secondary side exit door of this building. | A Push bar to open sign should be displayed on the secondary side exit door of this building. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357319 Installed by steve | 2014-04-21 | Fully Completed | Michael Lyons | 2013-09-12 14:18 | 2013-10-03 14:20 | 2013-09-12 14:18 | 2014-05-07 20:10 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:39 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151162 | Completed | 3 | High | Responsive Item | The glazed units in the windows of the old BT room on the ground floor level by flat 25 are broken. | I would recommend that new glazing units are inserted in the windows of this room. | Responsive Repairs | Michael Lyons | 2014-07-22 | 201554173 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-07-01 12:39 | 2014-07-22 12:41 | 2014-07-01 12:39 | 2016-03-07 18:37 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:59 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151171 | Completed | 12a | High | Responsive Item | The gerda lock to the room located between flats 47 and 69 has been damaged and this door could not be opened. | I would recommend that this door lock is repaired or replaced. Once this room is accessed if there is any storage in this room it should be removed or the metal door should be replaced with a 30 minute fire door. Please also see items 8a above and 14 below. | Responsive Repairs | Michael Lyons | 2014-07-09 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-07-01 12:59 | 2014-07-22 13:00 | 2014-07-01 12:59 | 2016-02-23 22:52 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:21 | S217012770006 | TALBOT GROVE HOUSE | 177706 | Completed | 1b | Low | Responsive Item | The light in the electrical meter room of the staircase of flats 1 to 14 is not working. | I would recommend that this light units is checked and repaired/replaced or the bulb replaced so that this light is in full working order. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on 201552577 | 2016-02-16 | Fully Completed | Maria Ares | 2015-01-12 11:21 | 2015-07-11 11:23 | 2015-01-12 11:21 | 2016-02-17 11:04 | -180 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:24 | S217012770006 | TALBOT GROVE HOUSE | 177715 | Completed | 4 | High | Responsive Item | The gas meter box outside flat 36 is not secured to the wall, it appears that only the gas pipe is supporting this gas meter box. | This gas meter box should be secured correctly to the wall, so there is not a gas leak if the box and meter come away from the wall completely. | Responsive Repairs | John Tatham | 2015-02-02 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-01-12 11:24 | 2015-02-02 11:25 | 2015-01-12 11:24 | 2016-02-23 22:55 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:53 | S217012770006 | TALBOT GROVE HOUSE | 177739 | Completed | 12b | Medium | Responsive Item | The hoppers/flaps to rubbish chute openings by flats 36 and 43 are damaged and do not shut fully | The hoppers/flaps to these rubbish chute openings, should be repaired or replaced so that they shut fully. | Responsive Repairs | John Tatham | 2015-04-02 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-01-12 11:53 | 2015-03-13 11:54 | 2015-01-12 11:53 | 2016-02-23 22:57 | -60 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 15:48 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215299 | Completed | 12 | High | Responsive Item | The hinges of the staircase doors located opposite flats 135, 241 and 285 are damaged and these self closing fire doors will now not close fully. | The damaged hinges on these doors should be replaced with the correct fire rated hinges so that these fire doors close fully. | Responsive Repairs | Alan Brooks | 2015-09-28 | 201554164 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-07 15:48 | 2015-09-28 16:07 | 2015-09-07 15:48 | 2016-03-07 18:40 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:08 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215308 | Completed | 12b | High | Responsive Item | The hinges of the electrical room/cupboard doors located opposite flats 181 and 225 are damaged and these doors do not close easily. | These damaged hinges on these door should be replaced. | Responsive Repairs | Alan Brooks | 2015-09-28 | 201554163 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-09-07 16:08 | 2015-09-28 16:09 | 2015-09-07 16:08 | 2016-03-07 18:42 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:09 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215309 | Completed | 12c | High | Responsive Item | The self closing device on the staircase door located opposite flat 147 is damaged and this fire door will now not close fully. | This damaged self closing device on this door should be replaced so that this fire door automatically closes fully. | Responsive Repairs | Alan Brooks | 2015-09-28 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-07 16:09 | 2015-09-28 16:10 | 2015-09-07 16:09 | 2016-02-23 22:58 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:11 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215310 | Active | 12d | Medium | Responsive Item | The window of flat 237 onto the balcony area is boarded up. TENANTED | I would recommend that this boarded up window is checked and a new piece of glass is fitted in this window. | Responsive Repairs | Alan Brooks
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:08 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173288 | Completed | 1a | High | Responsive Item | There is a large diameter black electrical cable through the wall above the entrance door of flat 439, this cable then goes along the corridor wall and out of the building into electrical intake room 7. This electrical cable has not been fire stopped as it comes out of the wall and this cable appears not to be secured securely to the wall in places. | Can if please be confirmed that this electrical cable has been secured to the wall in accordance with the requirements of the electrical wiring regulations? The hole in the wall by the flat entrance door should be fully fire stopped. | Responsive Repairs | John Tatham | 2014-12-29 | 201554136 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-08 16:08 | 2014-12-29 16:10 | 2014-12-08 16:08 | 2016-03-07 18:45 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:25 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173310 | Completed | 12c | High | Flat Door | The fire rated glazing in the flat entrance door of flat 443 (tenanted) s broken and now taped over, this flat entrance door is now not fire rated. | I would recommend that the fire rated glazing in the vision panel of this flat entrance door is replaced with a new piece of fire rated glazing or boarded over using a fire rated material. This is so that this flat entrance door is maintained as a fire rated door. | Responsive Repairs | John Tatham | 2014-12-29 | 201554133 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-08 16:25 | 2014-12-29 16:26 | 2014-12-08 16:25 | 2016-03-07 18:48 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:27 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173311 | Completed | 12d | High | Responsive Item | The self closing device has been removed from the fire door fitted at the base of the staircase from the lower ground floor area in the 400 section next to the dry riser inlet marked as number 7. | A new self closing device should be fitted to this fire door, it should be capable of closing the fire door fully onto its stops. | Responsive Repairs | John Tatham | 2014-12-29 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-08 16:27 | 2014-12-29 16:28 | 2014-12-08 16:27 | 2016-02-23 23:00 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:45 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173315 | Completed | 12f | Medium | Responsive Item | The letter box flaps are missing from the letter boxes on the flat entrance doors of flats 323, 326 and 334 (all tenanted), this could allow smoke to leave the flat and enter the common parts of the building, even if the flat door is closed. | I would recommend that the letter boxes are repaired or new letter boxes are fitted to these flat entrance doors, so that the compartmentation of the building is maintained. | Responsive Repairs | John Tatham | 2015-02-06 | 201554130 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-08 16:45 | 2015-02-06 16:47 | 2014-12-08 16:45 | 2016-03-07 18:50 | -60 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:56 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173321 | Completed | 14 | High | Responsive Item | At the lower ground floor level, outside garages 43 and 44 there are melted plastic pipes and electrical cables above the garage doors. It appears this could have been damaged caused by a fire? | I would recommend that the electrical cables above these garage doors are checked, also what did the plastic pipe contain, this should be checked as well. Any repairs necessary should then be undertaken. I would also recommend that the cause of this damage is investigated? | Responsive Repairs | John Tatham | 2015-01-09 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-08 16:56 | 2014-12-29 16:57 | 2014-12-08 16:56 | 2016-02-23 23:02 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:20 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173536 | Completed | 19a | High | Responsive Item | The door for the water ring main outlet above dry riser number 7 is missing. | A new door should be fitted to protect the water ring main outlet from being used by unauthorised persons. All the rubbish in this water main box should be removed. | Responsive Repairs | John Tatham | 2014-12-30 | 201554127 RD confirms completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-09 15:20 | 2014-12-30 15:22 | 2014-12-09 15:20 | 2016-03-07 18:52 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:27 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173546 | Completed | 19e | High | Dry or Wet Riser | The door and box of the dry riser outlet located on the 1st floor level of the 500 section, riser number 10, by flat 514, is damaged. | This damaged dry riser box and the door to it should be repaired or replaced. | Responsive Repairs | John Tatham | 2014-12-30 | 201554126 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-09 15:27 | 2014-12-30 15:28 | 2014-12-09 15:27 | 2016-03-07 18:54 | -21 | In target
TOR COURT - 2015.06.15 | 2015-06-29 11:40 | S217005550001 | TOR COURT | 203785 | Completed | 12 | Low | Responsive Item | The cabling box located on the wall opposite flat 5 at the base of the staircase to the 1st floor had its cover missing, with cables hanging out of the box. | I would recommend that a cover is fitted to this box so that the contents are kept secured and to stop unauthorised access to this box. | Responsive Repairs | John Tatham | 2015-12-26 | 201554123 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-06-29 11:40 | 2015-12-26 11:42 | 2015-06-29 11:40 | 2016-03-07 18:57 | -180 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:17 | S217008170001 | TREADGOLD HOUSE | 205783 | Completed | 14 | Medium | Responsive Item | There is a hole in the wall of the ground floor electrical cupboard/room, to the left hand side of the door where a cable has been passed through the wall and the job not made good afterwards. | This hole in the wall of the ground floor electrical cupboard/room should be repaired so that the wall is not breached. Please see item 13 regarding the removal of this electrical cable. This is an external wall but is near to the lift and staircase of this building. | Responsive Repairs | John Tatham | 2015-09-07 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-07-09 12:17 | 2015-09-07 12:19 | 2015-07-09 12:17 | 2016-02-02 20:59 | -60 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:37 | S217008770001 | TRELLICK TOWER | 136761 | Completed | 8b | High | Responsive Item | There is an unsecured disused area at ground level located under the communal staircase in the small block. (The staircase furthest from the main reception.) This area is also full of combustible items and rubbish. Caretaker confirms that he has sometimes had to move on a rough sleeper from here. | I would recommend that this area is cleared out and secured asap. Currently there is no door or access panel so one will need to be fabricated and fixed securely in place. (ESA may be able to assist with dimensions.) | Responsive Repairs | Alex Bosman |  |  | 2015-11-26 | Fully Completed | Janice Wray | 2014-03-26 16:37 | 2014-04-16 16:39 | 2014-03-26 16:37 | 2015-11-27 20:52 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:43 | S217008770001 | TRELLICK TOWER | 136766 | Completed | 12b | High | Flat Door | The door frame of flat 182 is damaged | This damaged door frames should be repaired so that the whole flat entrance door set is fire rated. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-26 16:43 | 2014-04-16 16:44 | 2014-03-26 16:43 | 2015-11-12 16:38 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:45 | S217008770001 | TRELLICK TOWER | 136770 | Completed | 12d | High | Responsive Item | 12d High The fire rated glass in the following flat entrance doors vision panels or the glazing in the corridor fire doors is cracked or damaged. 1. Flat door of flat number 199 2. Flat door of flat number 93 3. Both corridor doors on the 15th floor level off the lift lobby area 4. One of the staircase doors from the lift lobby area on the 18th floor level 5. One of the staircase doors from the lift lobby area on the 6th floor level | These cracked or damaged pieces of fire rated glazing should be replaced with new pieces of fire rated glazing. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-26 16:45 | 2014-04-16 16:47 | 2014-03-26 16:45 | 2015-11-12 16:40 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:47 | S217008770001 | TRELLICK TOWER | 136772 | Completed | 12e | High | Responsive Item | The corridor doors of the following floor levels ground and do not shut fully. 27th floor level lift lobby area of the link bridge 12th floor level flat end of the link bridge 12th floor level lift lobby area of the link bridge 9th floor level lift lobby area 6th floor level to the short tower corridor 3rd floor level lift to staircase doors | These corridor doors should be eased or the hinges adjusted so that the doors can be shut fully by the self closing devices fitted to them. | Responsive Repairs | Alex Bosman |  |  | 2015-11-18 | Fully Completed | Janice Wray | 2014-03-26 16:47 | 2014-04-16 16:49 | 2014-03-26 16:47 | 2015-11-19 19:39 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:49 | S217008770001 | TRELLICK TOWER | 136774 | Completed | 12f | High | Responsive Item | The fire door to the 9th floor level refuse chute room is damaged. | This fire door should be repaired or replace so that it is a fully functional 30 minute fire rated door. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-26 16:49 | 2014-04-16 16:50 | 2014-03-26 16:49 | 2015-11-12 16:41 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:50 | S217008770001 | TRELLICK TOWER | 136776 | Active | 12g | High | Responsive Item | Numerous pieces of cold smoke seal are missing from the corridor sub division doors or the doors to the staircases or the refuse chute rooms. | I would recommend that a survey is under taken of all the corridor, staircase and refuse chute room doors that were fitted with cold smoke seals during the refurbishment work as numerous pieces are now missing. Cold smoke seals should be securely fitted using both glued and pins. | Responsive Repairs | Alex Bosman |  |  | 2015-11-18 | Partially Completed | Janice Wray | 2014-03-26 16:50 | 2014-04-16 16:52 | 2014-03-26 16:50 | 2015-11-19 21:07 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:53 | S217008770001 | TRELLICK TOWER | 136781 | Completed | 12i | Medium | Flat Door | The flap is missing from the letter box of flat 73and the letter box is damaged, this could allow smoke to enter the staircase enclosure from the flat. | I would recommend that a new letter box and flap is fitted to the flat entrance door of flat 73 so that the compartmentation of the protected staircase is maintained. | Responsive Repairs | Alex Bosman |  |  | 2015-11-11 | Fully Completed | Janice Wray | 2014-03-26 16:53 | 2014-05-25 16:54 | 2014-03-26 16:53 | 2015-11-12 16:43 | -60 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:01 | S217008770001 | TRELLICK TOWER | 136785 | Completed | 16 | High | Signage | The "Push Bar to Open" signs are missing from each exit door from the corridor to the staircase at the end of each of the corridors. | A "Push Bar to Open" signs should be displayed on each exit door on to the staircase where a push bar device is fitted. Escape signage was provided under the phase 4 refurbishment so why not the push bar signs | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-03-26 17:01 | 2014-04-16 17:02 | 2014-03-26 17:01 | 2015-11-30 16:48 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:20 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181317 | Completed | 1 | High | Responsive Item | The lights in the entrance lobby area and in male toilet area are not working, please see item 14a below as well reference the ceiling being down in these two areas. . | I would recommend that all of the lights in this community area checked not just the entrance lobby area and the male toilets because the ceiling has been partially removed in these areas along with the light units. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on 201552584 | 2016-02-16 | Fully Completed | Maria Ares | 2015-02-02 12:20 | 2015-02-23 12:22 | 2015-02-02 12:20 | 2016-02-17 11:04 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:27 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181320 | Completed | 14a | High | Responsive Item | Some of the ceiling has been removed in the entrance lobby area and in the male toilet area along with some of the wall linings covering the risers/duct work in the toilets. | I would recommend that the ceilings in this whole area are reinstated and that all of the damaged/missing wall linings are replaced/ repaired using fire rated plasterboard or other fire rated materials so that the risers/ducts are all compartmented off. This is to maintain the fire rating of the structure of this building. I would recommend that in future checks are carried out after contractors have undertaken work to make certain all fire stopping has been undertaken and any work is made good. | Responsive Repairs | John Tatham | 2015-02-23 | 201554117 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-02-02 12:27 | 2015-02-23 12:29 | 2015-02-02 12:27 | 2016-03-07 19:00 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:30 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181321 | Completed | 14b | Medium | Responsive Item | There are air bricks located in the wall above the entrance doors to the community room from the lift/lobby area, so these two areas are not fire separated from each other. This was the way that this area was constructed, the entrance doors are self closing fire rated doors. | I would recommend that these air bricks are either removed and replaced with normal bricks or covered over with a fire rated material so that the lift/lobby area and the community room are fire separated from each other. Alternately the air bricks presently installed could be removed and intumescent blocks with suitable covering installed instead. | Responsive Repairs | John Tatham | 2015-02-23 | 201554114 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2015-02-02 12:30 | 2015-02-23 12:31 | 2015-02-02 12:30 | 2016-03-07 19:03 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:15 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111267 | Completed | 1b | High | Responsive Item | There are electrical cables with exposed wires and plugs hanging from the ceiling of this clubroom, by the desk on the left as you enter the room by the main entrance door. | I would recommend that an electrician is asked to check these cables and plugs hanging from the ceiling to make certain that they are safe. The wires, cables and plugs should then be tidied up and fixed to the ceiling properly or removed. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357324 made safe and removed | 2014-04-11 | Fully Completed | Michael Lyons | 2013-10-18 11:15 | 2013-11-08 11:16 | 2013-10-18 11:15 | 2014-05-07 19:55 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:22 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111271 | Completed | 2 | High | Responsive Item | The floor of the external ramp by the main entrance door is covered by discarded cigarette ends. I am told that this area at the base of the ramp just outside the entrance door is used as the designated smoking area. There is no suitable wall mounted cigarette bin provided for the used smoking materials. | Can it please be confirmed that this external area just outside the entrance door to the clubroom is the designated smoking area? If this is the designated smoking area I would recommend that a suitable and appropriate wall mounted cigarette bin is provided. This bin should be emptying regularly and the area around it kept clean of all discarded smoking material. All the currently discarded cigarette ends on the floor should be removed. The H&S can supply NO SMOKING signs for this area | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357324 fitted 8/4 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-10-18 11:22 | 2013-11-08 11:27 | 2013-10-18 11:22 | 2014-05-07 19:56 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 12:22 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111309 | Completed | 8 | Medium | Responsive Item | There are a couple of the linoleum floor tiles missing from the clubroom floor. | I would recommend that the flooring is this clubroom is checked and that the missing linoleum floor tiles are replaced and any other loose ones found are stuck back down again. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357324 | 2014-04-11 | Fully Completed | Michael Lyons | 2013-10-18 12:22 | 2013-12-17 12:25 | 2013-10-18 12:22 | 2014-05-07 19:56 | -60 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 12:28 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111312 | Completed | 16b | High | Responsive Item | There are no fire action notices displayed in this clubroom informing the occupants what to do in the event of a fire. | Suitable pictogram fire action notices should be displayed in this clubroom, one by the entrance door and one in the kitchen area, describing the actions to take if there is a fire in this clubroom. Fire Action Notices are available from H&S Team | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357324 | 2014-04-08 | Fully Completed | Michael Lyons | 2013-10-18 12:28 | 2013-11-08 12:29 | 2013-10-18 12:28 | 2014-05-07 19:54 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 16:07 | S217010420001 | TREVERTON TOWER | 148246 | Completed | 8a | High | Responsive Item | There is an 8 x 4 sheets of plywood laying on the open roof area of this building. | I would recommend that this sheet of plywood is removed from the open roof area in case it is blown off the roof. | Responsive Repairs | Michael Lyons | 2014-06-11 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-06-11 16:07 | 2014-07-02 16:08 | 2014-06-11 16:07 | 2016-02-02 21:01 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 16:09 | S217010420001 | TREVERTON TOWER | 148248 | Completed | 8b | High | Miscellaneous | One of the panes of glass in the window on the staircase half landing below the 8th floor level is cracked and damaged. | I would recommend that this pane of glass is replaced in case it falls out. | Responsive Repairs | Michael Lyons | 2014-07-02 | 201554110 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2014-06-11 16:09 | 2014-07-02 16:10 | 2014-06-11 16:09 | 2016-03-07 07:58 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:07 | S217010420001 | TREVERTON TOWER | 148284 | Completed | 12b | Medium | Responsive Item | On floor levels 5and 8 the door flaps/hoppers to rubbish chutes are damaged and do not shut fully | The door flaps/hopper to the rubbish chutes openings on these levels should be repaired or replaced so that they shut fully. | Responsive Repairs | Michael Lyons | 2014-08-10 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-06-11 17:07 | 2014-08-10 17:09 | 2014-06-11 17:07 | 2016-02-02 21:04 | -60 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:13 | S217010420001 | TREVERTON TOWER | 148288 | Completed | 14 | High | Responsive Item | In the staircase enclosure there is a cable duct, the covers have been removed from this duct on some landings and are now missing. Not replaced correctly as on the 5th floor level or in other cases the original metal covers have been replaced with thin pieces of plywood, on levels 6, 9 and 10 for instance. | Where covers are missing or have been replaced with thin plywood they should be replaced with a suitable material capable of resisting fire. These covers could have been removed when the digital TV cabling was installed. | Responsive Repairs | Michael Lyons | 2014-07-02 | 201554106 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2014-06-11 17:13 | 2014-07-02 17:14 | 2014-06-11 17:13 | 2016-03-07 08:00 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:22 | S217010420001 | TREVERTON TOWER | 148293 | Completed | 16b | Medium | Responsive Item | The floor numbers are not displayed in the lift lobby areas or the staircase landings of this building. These floor numbers will aid the fire service if there is an incident in this building. | I would recommend that the floor numbers are painted on the wall of the lift lobby area. Opposite the lifts and on each staircase landings of this building where there is a balcony. | Responsive Repairs | Michael Lyons | 2014-08-10 | 201554103 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2014-06-11 17:22 | 2014-08-10 17:24 | 2014-06-11 17:22 | 2016-03-07 08:02 | -60 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:24 | S217010420001 | TREVERTON TOWER | 148294 | Completed | 16c | Medium | Responsive Item | There is no signs displayed in the ground floor level entrance lobby area of this building informing the emergency services which flats are located on which floor levels. This sign would aid would aid the fire service or any other emergency service person if there is an incident in this building. | I would recommend that a sign is displayed in the ground floor level entrance lobby area of this building showing which flat numbers are located on which floor level. This sign should be permanently fixed to the wall and in a large font. | Responsive Repairs | Michael Lyons | 2014-08-10 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-06-11 17:24 | 2014-08-10 17:27 | 2014-06-11 17:24 | 2016-02-02 21:06 | -60 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:34 | S217005570001 | WALNUT TREE HOUSE | 103476 | Completed | 12a | High | Responsive Item | The Georgian fire rated glazing in the transom light areas above some of the refuse chute room doors has been replaced with non fire rated boarding. The worst examples are the refuse chute rooms next to flats 8 and 23. | I would recommend that all of the transom light areas above the refuse chute room doors are checked to see if the boarding inserted there is fire rated. If it is not is should be replaced immediately with suitably fitted 30 minute fire rated boarding/material. Or Georgian fire rated glazing could be reinstated. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357326 | 2014-04-18 | Fully Completed | Michael Lyons | 2013-08-23 11:34 | 2013-09-13 11:35 | 2013-08-23 11:34 | 2014-05-06 14:53 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:35 | S217005570001 | WALNUT TREE HOUSE | 103477 | Completed | 12b | High | Responsive Item | A piece of non fire rated boarding has been inserted in the transom light area above the ground floor level electrical cupboard by flat 6. | The presently fitted non fire rated boarding in this transom light area should be replaced with 30 minute fire rated boarding/material suitably fixed in place. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357326 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-23 11:35 | 2013-09-13 11:41 | 2013-08-23 11:35 | 2014-05-07 20:15 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:46 | S217005570001 | WALNUT TREE HOUSE | 103485 | Completed | 12d | High | Responsive Item | There are no self closing devices fitted to the refuse chute room doors. | Self closing device should be fitted to all of the refuse chute room fire doors so that the fire doors close automatically and fully on to their stops. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357326 6 devices fitte din total | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-23 11:46 | 2013-09-13 11:47 | 2013-08-23 11:46 | 2014-05-07 20:15 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:56 | S217005570001 | WALNUT TREE HOUSE | 103491 | Active | 12g | High | Responsive Item | There is just a hole in the entrance door to flat 26 where the letter box should be and this door appears not to be a fire rated door. | Can it please be confirmed that this flat entrance door is a 30 minute fire rated door, if it is a new letter box and flap should be fitted to this flat entrance door. If it is not then this door should be replaced with a self closing 30 minute fire rated door, complying with all the requirements of the Building Regulations. | Responsive Repairs | Jackie Gaikwad |  | Cn this be passed toCarl Stokes for assessment Carl unable to access dwelling and records do not show that TMO changed the door so furterh investigation withthe resident required to ensure door is FD30 | 2014-10-14 | Partially Completed | Michael Lyons | 2013-08-23 11:56 | 2013-09-13 11:57 | 2013-08-23 11:56 | 2014-10-15 09:45 | -21 | In target | 2013-08-23 11:56 | 2014-10-21 09:42 | Janice Wray
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:02 | S217005570001 | WALNUT TREE HOUSE | 103495 | Completed | 14 | High | Responsive Item | There is a hole in the door frame of the electrics cupboard at the ground floor level next to flat 3, where a black electrical cable comes through the door frame. | This hole in the door frame should be repaired/ filled in with a suitable fire rated material to maintain the fire rating of the door frame. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Jackie Gaikwad |  | Site job number 201357326 | 2014-04-10 | Fully Completed | Michael Lyons | 2013-08-23 12:02 | 2013-09-13 12:04 | 2013-08-23 12:02 | 2014-05-07 20:17 | -21 | In target
WESTFIELD HOUSE - 2015.01.28 | 2015-02-03 11:23 | S217012760001 | WESTFIELD HOUSE | 181546 | Completed | 14 | High | Responsive Item | On the wall of flat 4, in the entrance hall area a cover plate has been removed and a piece of plywood has been fitted back instead. | I would recommend that the piece of plywood is removed and a proper metal cover plate is fixed to cover the hole in this wall, this should be fitted correctly with no gaps around the edge of the plate. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. | Responsive Repairs | John Tatham | 2015-02-24 | 201554099 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2015-02-03 11:23 | 2015-02-24 11:25 | 2015-02-03 11:23 | 2016-03-07 08:06 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:01 | S217012740010 | WHISTLER TOWER 1-61 | 102277 | Completed | 1b | Medium | Responsive Item | The cover of the light unit located on the 7th floor level flat/lift lobby area near to flats 23 and 24 is damaged with pieces broken off of it. | I would recommend that a new cover is fitted to this light unit. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357327 | 2014-04-17 | Fully Completed | Michael Lyons | 2013-08-16 15:01 | 2013-10-15 15:04 | 2013-08-16 15:01 | 2014-05-02 10:04 | -60 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:23 | S217012740010 | WHISTLER TOWER 1-61 | 102282 | Completed | 8c | Low | Responsive Item | The doors of the double rise cupboard on the flat/lift lobby area on the 5th floor level can not be opened. | I would recommend that the lock fitted to this cupboard door is repaired or replaced so that the door can be opened. | Responsive Repairs | Jackie Gaikwad | 2013-02-15 | Block Job number 201357327 | 2014-04-09 | Fully Completed | Michael Lyons | 2013-08-16 15:23 | 2014-02-12 15:25 | 2013-08-16 15:23 | 2014-05-02 10:05 | -180 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:26 | S217012740010 | WHISTLER TOWER 1-61 | 102284 | Completed | 8d | Low | Responsive Item | In door to the double riser cupboards on the 16th floor level does not have a lock fitted to it, so cannot be secured shut. I | would recommend that a lock is fitted to this cupboard door so that it can be secured locked shut. | Responsive Repairs | Jackie Gaikwad | 2014-02-14 | Block Job number 201357327 | 2014-04-18 | Fully Completed | Michael Lyons | 2013-08-16 15:26 | 2014-02-12 15:27 | 2013-08-16 15:26 | 2014-05-02 10:05 | -180 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:32 | S217012740010 | WHISTLER TOWER 1-61 | 102297 | Completed | 12a | High | Responsive Item | The ground floor level door separating the lift lobby area from the staircase is damaged and does not shut fully. | I would recommend that this door is repaired or replaced so that the door closes fully on to its stops. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357327 | 2014-04-04 | Fully Completed | Michael Lyons | 2013-08-16 15:32 | 2013-09-06 15:34 | 2013-08-16 15:32 | 2014-05-02 10:05 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:52 | S217012740010 | WHISTLER TOWER 1-61 | 102312 | Completed | 14 | High | Responsive Item | There are holes in the boarding or the boarding is missing above the riser cupboard doors on the 1st floor level where contractors have passed cables through these areas and not made good. | I would recommend that the missing pieces of boarding are replaced and any holes are filled in with a suitable material above the doors of these 1st floor level cupboard doors. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all fire stopping and making good has been carried out. | Responsive Repairs | Jackie Gaikwad | 2013-09-06 | Block Job number 201357327 | 2014-04-02 | Fully Completed | Michael Lyons | 2013-08-16 15:52 | 2013-09-06 15:55 | 2013-08-16 15:52 | 2014-05-02 10:06 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:55 | S217012740010 | WHISTLER TOWER 1-61 | 102315 | Completed | 16 | Medium | Responsive Item | The floor level and flat numbers signs are missing from the staircase landings on floor levels, 3 and 7. Also the sign on the flat/lift lobby area of the 15th floor level is also missing. These signs are to aid the emergency services when trying to locate a particular floor level and flat number. | I would recommend that the floor level and flat numbers signs are provided for these floor levels. These signs should be similar to the other floor/flat number signs in the tower and permanently fixed to the wall in the same location as on the other floor levels. | Responsive Repairs | Jackie Gaikwad | 2013-09-13 | Block Job number 201357327 | 2014-04-28 | Fully Completed | Michael Lyons | 2013-08-16 15:55 | 2013-10-15 15:58 | 2013-08-16 15:55 | 2014-05-02 10:06 | -60 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:14 | S217009090002 | WHITCHURCH HOUSE | 142361 | Completed | 1b | High | Responsive Item | In the generator room there are 2 electrical meters marked Tumble Dryer and Washing Machine with the wires cut and exposed on the wall. | Can it be confirmed that these 2 electrical meters are redundant and the electrical wires are not live? I would recommend that the wires from these meters are capped off correctly and the meters removed if now not used. | Responsive Repairs | Alex Bosman |  | RMA REMOVED METER AND ALSO A RYEFIELD BOARD AND DOOR THAT WAS IN THE ROOM. | 2015-11-17 | Fully Completed | Maria Ares | 2014-05-06 14:14 | 2014-05-27 14:15 | 2014-05-06 14:14 | 2015-11-18 15:25 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:19 | S217009090002 | WHITCHURCH HOUSE | 142372 | Completed | 12a | High | Responsive Item | The ground floor level kitchen door has so much paint on the cold smoke seals that I believe that this seal will not now function correctly. | The cold smoke seals fitted to other fire doors also have paint on them but only a small amount. The cold smoke seals fitted to the kitchen door should be replaced with new ones as these ones are covered with paint. In future I would recommend that a check is undertaken after redecoration work has been undertaken and the painting contractor is asked to change any cold smoke seals found with paint on them. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 14:19 | 2014-05-27 14:21 | 2014-05-06 14:19 | 2015-11-30 16:56 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:21 | S217009090002 | WHITCHURCH HOUSE | 142375 | Completed | 12b | High | Responsive Item | A piece of cold smoke seals is missing from the corridor sub division fire door by flat 33 on the 2nd floor level. | A new piece of cold smoke seals should be fitted to this corridor sub division fire door by flat 33 on the 2nd floor level. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 14:21 | 2014-05-27 14:22 | 2014-05-06 14:21 | 2015-11-30 16:54 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:29 | S217009090002 | WHITCHURCH HOUSE | 142381 | Completed | 14a | High | Responsive Item | The wall lining is damaged on the 1st floor level opposite flat 17th entrance door. | These damaged wall should be repaired/filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 14:29 | 2014-05-27 14:30 | 2014-05-06 14:29 | 2015-11-30 16:53 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:30 | S217009090002 | WHITCHURCH HOUSE | 142383 | Completed | 14b | High | Responsive Item | There is a hole in the ceiling lining of the corridor between flats 22 and 23 | This hole in the ceiling should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 14:30 | 2014-05-27 14:32 | 2014-05-06 14:30 | 2015-11-30 16:52 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:32 | S217009090002 | WHITCHURCH HOUSE | 142385 | Completed | 14c | High | Responsive Item | The wall and ceiling linings in the ground floor level toilet are damaged where new electrical cables have been run into the electrical cupboard. This issue was highlighted by the Fire Officer during his audit and on the Deficiency Notice issued after his audit. | "The Deficiency Notice asks for the wall and ceiling in the ground floor intake room to be repaired to fire resistant standards" This should achieved by using suitable fire rated materials to maintain the fire rating of the structure of the building. | Responsive Repairs | Alex Bosman |  |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 14:32 | 2014-05-27 14:33 | 2014-05-06 14:32 | 2015-11-30 16:50 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:43 | S217009090002 | WHITCHURCH HOUSE | 142392 | Completed | 18b | Medium | Responsive Item | In the central staircase on the 1st floor level the wall bracket for the fire extinguisher has come off the wall and the water fire extinguisher is just standing on the staircase landing. | I would recommend that the fire extinguisher wall bracket is re-fixed back onto to the wall and the fire extinguisher hung on it so that the extinguisher cannot be knocked over or trip somebody over. | Responsive Repairs | Alex Bosman |  | FE'S SERVICED ON 25.09.15 | 2015-11-17 | Fully Completed | Maria Ares | 2014-05-06 14:43 | 2014-07-05 14:44 | 2014-05-06 14:43 | 2015-11-18 15:26 | -60 | In target
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:37 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214791 | Completed | 12 | High | Responsive Item | The door to the lift motor room was unlocked at the time of this assessment and could not be locked shut by myself. | I would recommend that the lock on the lift motor room is repaired or replaced so that this door can be locked shut to restrict access to this room. s | Responsive Repairs | Alan Brooks | 2015-09-24 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-03 16:37 | 2015-09-24 16:40 | 2015-09-03 16:37 | 2016-02-02 21:08 | -21 | In target
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:41 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214792 | Completed | 14 | High | Responsive Item | In the wall above the electrical room of the protected staircase by flats 27 and 28 there is a cable hole in the wall lining where a cable has been pasted through the wall and a repair has not made good. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-09-24 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-03 16:41 | 2015-09-24 16:41 | 2015-09-03 16:41 | 2016-02-02 21:10 | -21 | In target
WILTSHIRE CLOSE FLATS 147 TO 180 - 2015.07.27 | 2015-09-09 14:52 | S217011667704 | WILTSHIRE CLOSE (147-180) | 215710 | Completed | 12b | High | Responsive Item | The original door lock has been removed from the ground floor electrical cupboard/ room door by flats 147 and 148, there is now a large hole in this fire rated door as well as there being air holes drill in this door. | I would recommend that the hole in the door where the lock has been removed in filled in with a suitable fire rated material so that the integrity of the fire door is maintained. The air holes do not need to be filled in unless storage is placed in this cupboard. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 14:52 | 2015-09-30 14:54 | 2015-09-09 14:52 | 2016-02-02 21:12 | -21 | In target
WILTSHIRE CLOSE FLATS 147 TO 180 - 2015.07.27 | 2015-09-09 14:56 | S217011667704 | WILTSHIRE CLOSE (147-180) | 215713 | Completed | 14b | High | Responsive Item | In the wall above the electrical room of the protected staircase by flats 147 and 148 there is a cable hole in the wall lining where a cable has been passed through the wall and a repair has not made good. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 14:56 | 2015-09-30 14:57 | 2015-09-09 14:56 | 2016-02-02 21:34 | -21 | In target
WILTSHIRE CLOSE FLATS 35 TO 68 - 2015.07.27 | 2015-09-09 15:12 | S217011667711 | WILTSHIRE CLOSE (35-68) | 215726 | Completed | 14a | High | Responsive Item | The door frame of the ground floor electrical cupboard, under the staircase by flat 35 needs to be re-fixed back to the brickwork and the gap filled in. | I would recommend that the frame of this electrical cupboard is re-fixed back to the brickwork and any gaps filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 15:12 | 2015-09-30 15:14 | 2015-09-09 15:12 | 2016-02-02 21:37 | -21 | In target
WILTSHIRE CLOSE FLATS 35 TO 68 - 2015.07.27 | 2015-09-09 15:14 | S217011667711 | WILTSHIRE CLOSE (35-68) | 215728 | Completed | 14b | High | Responsive Item | In the wall above the electrical room of the protected staircase by flats 61 and 62 there is a cable hole in the wall lining where a cable has been pasted through the wall and a repair has not made good. | This hole should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 15:14 | 2015-09-30 15:15 | 2015-09-09 15:14 | 2016-02-02 21:39 | -21 | In target
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:26 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215736 | Completed | 12a | High | Responsive Item | One of the fire rated glazed vision panels in flat 77's entrance door has been replaced with a piece of plywood. TENANT | A new piece of fire rated glazing should be correctly fitted in the vision panel area of this flat entrance door or a new self closing 30 minute fire rated door fitted. Order 201525723 raised - is this for fire-rated glazing? | Responsive Repairs | Alan Brooks | 2015-09-30 | 201553855 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2015-09-09 15:26 | 2015-09-30 15:34 | 2015-09-09 15:26 | 2016-03-07 08:10 | -21 | In target
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:36 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215745 | Completed | 12b | High | Responsive Item | The flat entrance door to flat 141 has been changed in the last few weeks by the TMO. TENANT | Please can it be confirmed that this new flat entrance door is a self closing 30 minute fire rated door? If it is not then a self closing 30 minute fire rated door should be fitted. Confirmation required that door fitted under order number 201517235 is self- closing FD30 | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2015-09-09 15:36 | 2015-09-30 15:38 | 2015-09-09 15:36 | 2016-02-23 23:12 | -21 | In target
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:38 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215747 | Completed | 14 | High | Responsive Item | In the walls by the doors of the ground floor level electrical cupboards/rooms near to flats 70 and 80 there is a cable holes in the wall lining where a cable has been passed through the wall and a repair has not made good. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain all fire stopping has been undertaken. | Responsive Repairs | Alan Brooks | 2015-09-30 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2015-09-09 15:38 | 2015-09-30 15:40 | 2015-09-09 15:38 | 2016-02-02 21:41 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:10 | S217012746601 | WORLDS END ESTATE CAR PARK | 134359 | Completed | 14 | High | Responsive Item | There are numerous in the wall linings of the plant rooms off the car park, some areas have whole rows of bricks missing. This is where pipes and cables have been passed through wall and ceiling linings and these have not been made good afterwards. | A full check of all the wall ceiling lining should be undertaken with all the holes filled in and any missing bricks replaced. Any repairs should be with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in this car park or rooms off of it to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. Response Repairs | Responsive Repairs | Alex Bosman |  |  | 2015-12-03 | Fully Completed | Janice Wray | 2014-03-12 17:10 | 2014-04-02 17:11 | 2014-03-12 17:10 | 2015-12-04 17:31 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:37 |  |  | 122460 | Completed | 5b | High | Responsive Item | There is a silver extraction duct/tube in the secondary exit corridor which is badly damaged. This extraction duct is hit by the door every time the door is opened. | The extraction duct/tube in the secondary exit corridor should be replaced and relocated so that the door does not hit it every time the door is opened. | Responsive Repairs | Alex Bosman |  | COMPLETE - AS DAMAGE TO THE DUCT DOES NOT POSE A FIRE RISK | 2015-11-17 | Fully Completed | Maria Ares | 2014-01-03 11:37 | 2014-01-24 11:38 | 2014-01-03 11:37 | 2015-11-18 15:32 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:38 |  |  | 122461 | Active | 8a | High |  | One of the emergency exit routes from this clubroom goes through the bulk storage area, there were items being stored which were partially obstructing this escape route. | The floor area of the bulk storage room used as the emergency exit route should be permanently "Hatched out" or marked up "Keep Clear, do not place items here" or words to this effect, so that the exit route is not obstructed in anyway. | Responsive Repairs | Alex Bosman |  |  |  |  | Clare Davis System Administration | 2014-01-03 11:38 | 2014-01-24 11:40 |  |  | 803 | 803 days overdue
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:43 |  |  | 122465 | Completed | 12 | High | Flat Door | It appears that the glazing in the vision panel in the kitchen fire door is not fire rated. | A check should be carried out the see if the glazing in the kitchen fire door is fire rated, if it is not it should be replaced by 30 minute fire rated glazing. | Responsive Repairs | Alex Bosman | 2016-01-13 | Works included in current refurb works | 2016-01-13 | Fully Completed | Maria Ares | 2014-01-03 11:43 | 2014-01-24 11:43 | 2014-01-03 11:43 | 2016-01-14 16:10 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:44 |  |  | 122466 | Completed | 14 | High | Responsive Item | There is a brick missing in the corridor wall lining in the means of escape corridor near to the electrical meters. | This wall lining in the means of escape corridor should be made good. | Responsive Repairs | Alex Bosman | 2016-01-21 | Included in current community room works | 2016-01-21 | Fully Completed | Maria Ares | 2014-01-03 11:44 | 2014-01-24 11:45 | 2014-01-03 11:44 | 2016-01-22 13:15 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:45 |  |  | 122467 | Completed | 15 | High | Emergency Lighting | There appears not to be a suitable level of illumination for the presently installed emergency lighting units in the bulk storage area covering the secondary exit route from the clubroom. | I would recommend that additional emergency lighting units are installed in the bulk storage area to cover the means of escape route through this area to the exit door. The additional emergency lighting units should conform to the requirements of BS 5266 Part 1 for layout and illumination levels. | Responsive Repairs | Alex Bosman |  | Additional lighting works to be included in clubroom refurbishment surrently taking place | 2015-12-14 | Fully Completed | Maria Ares | 2014-01-03 11:45 | 2014-01-24 11:46 | 2014-01-03 11:45 | 2015-12-15 12:11 | -21 | In target
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 14:55 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215956 | Active | 3 | Medium | Responsive Item | Some of the doors of the brick built bin cupboards are missing or are damaged. | I would recommend that the wooden doors of these bin cupboards are repaired or that new doors are fitted. | Responsive Repairs | Alan Brooks
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 15:07 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215967 | Completed | 12 | High | Responsive Item | The door of the electrical room/cupboard by flat 26 has been forced open and this area is being used to store household items. | The door and door frame should be repaired and a new lock fitted and all the household storage removed from this area. | Responsive Repairs | Alan Brooks | 2015-10-01 | 201553843 RD confirm completion | 2016-03-06 | Fully Completed | Janice Wray | 2015-09-10 15:07 | 2015-10-01 15:08 | 2015-09-10 15:07 | 2016-03-07 08:12 | -21 | In target