## Fire Risk Assessment Total Acti
Key Numb | Process No | Proc Status | CDescription | Item no | Priority | Risk | Action | Who | Action due date | Action taken | Comp date | Reference | High Priority Startdate | High Priority Duedate | High Priority User | Medium Priority Startdate | Medium Priority Duedate | Medium Priority User | Low Priority Startdate | Low Priority Duedate | Low Priority User | Closure Startdate | Closure Duedate | Modifying User | Feedback Startdate | Feedback Duedate | User Name | Category | Block | Descx | Code | Team | Return Stage Startdate | Return Stage Duedate | Return Stage User | Process Start Date | Return User
17085 | 172131 | Completed | GRENFELL TOWER - 2014.10.17 |  | High | Work is presently being undertaken to convert some areas on the lower 3 floor levels of this building into domestic dwellings along with other work and the over cladding of the whole building. Proposals have been submitted to the local Authority Building Control department under the Building Regulations process. | I would recommend that the Building Control Officer's response to the proposed work being undertaken in this building is asked for. A copy of this proposal and the Building Control Officer's response should be kept with this Fire Risk Assessment. Building control application on file, approvals not due until all items resolved. | Claire Williams |  | The Building Control officer has the full application and has met with the contractor, and is taking issues forward with the fire brigade as necessary. We do not get approval until the end of the period. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 09:12 | 2014-12-22 09:16 | CLWILLIAMS | [6 empty] | 2014-12-01 09:12 | 2015-03-26 13:34 | CLWILLIAMS | 2014-12-01 09:12 | 2014-12-22 09:16 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 09:12
17085 | 172134 | Completed | GRENFELL TOWER - 2014.10.17 |  | Information Only | Contractors are currently working in this building to construct some new dwellings on the floor levels previously used as offices etc. | I would advise that when this construction project is completed that the premises Fire Risk Assessment is reviewed and that the layout drawings of this building are amended to show the building new layout. | David Williams |  | I agree, and will notify Janice Wray when handover of the project is undertaken - potentially end of Oct 2015. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 09:17 | 2015-03-26 13:35 |  |  |  |  | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 09:17
17085 | 172136 | Completed | GRENFELL TOWER - 2014.10.17 |  | Information Only | When the construction/refurbishment work is completed on this building all information as required by the Building Regulations must be handed over to the TMO by the contractors before they hand over the areas now under their control. | Documentation must include: 1. A Buildings Regulations completion Certificate as issued by the RBKC Building Control department. 2. All the Regulation 38 information as required by the Building Regulations. 3. New Electrical certificates for any electrical wiring work undertaken, this is for the new dwellings and any common parts wiring 4. New commissioning certificates for any fixed fire systems that have been worked on by them or contractors working on their behalf, Dry Riser, smoke ventilation, fire alarm system etc This is so that if this building is audited by the Fire Authority under the Fire Safety Order documentation can be provided. | Claire Williams | 2015-03-25 | The information above will all be part of the O&M manual or H&S file produced by the contractor at completion. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 09:19 | 2015-03-26 14:26 | [5 empty] | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 09:19
17085 | 172138 | Completed | GRENFELL TOWER - 2014.10.17 |  | Information Only | The service road/area on the right hand side of this tower block is used by the emergency services to park their vehicles, this area has been handed over to the contractors and is presently under their control. The contractors have stated that the LFB are happy with the current parking arrangements whereby the contractors are using part of the service road/area. | I would recommend that Rydon's, the contractors are asked to provide in writing that the LFB are happy with the current parking arrangements on this service road. This is so that if this building is audited by the Fire Authority under the Fire Safety Order documentation can be provided stating that agreements on Part B5 access arrangements of Approved Document B of the Building Regulations have been agreed with the LFB. If there is no agreement or documentation can not be provided from the LFB then I would recommend that the whole of the service road/area is cleared and maintained free of any equipment or materials immediately. Rydon sent email to Carl S, CW to put on file | Claire Williams |  | Contractor Rydon had spoken to the fire brigade about the fact that the service road is within their compound. All watches had seen it and as the access was locked by an FB key, there were no issues with it. An email from Rydon to the Fire Brigade confirming this situation, and the FB's response is in thehousing part of W2. | 2015-06-18 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 09:21 | 2015-06-19 15:32 |  |  |  |  | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 09:21
17085 | 172140 | Completed | GRENFELL TOWER - 2014.10.17 | 1a | High | According to the contractors label on the main electrical supply/distribution board of this building the next fixed electrical wiring test is due in December of this year. | Can it please be confirmed whether the contractors or the TMO will be responsible for undertaking this buildings fixed electrical wiring test in December 2014? | Alex Bosman |  | INSTALLATION TESTED AND CERT SUPPLIED | 2015-11-17 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 09:25 | 2014-12-22 09:27 | MARES | [6 empty] | 2014-12-01 09:25 | 2015-11-18 13:48 | MARES | 2014-12-01 09:25 | 2014-12-22 09:27 | Maria Ares | Electrical Wire Check | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2014-12-01 09:25
17085 | 172141 | Completed | GRENFELL TOWER - 2014.10.17 | 1b | High | At the time of this assessment the lighting was not working in the roof level room where the water tanks are located. | I would recommend that the lighting units in this roof level area are repaired or replaced so that they work correctly. | John Tatham | 2016-02-16 | all necessary works completed on 201552556 | 2016-02-16 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 09:29 | 2014-12-22 09:30 | MARES | [6 empty] | 2014-12-01 09:29 | 2016-02-17 11:02 | MARES | 2014-12-01 09:29 | 2014-12-22 09:30 | Maria Ares | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 09:29
17085 | 172154 | Completed | GRENFELL TOWER - 2014.10.17 | 3a | High | The locking mechanism on the entrance door to this building from the walkway level is damaged and this door cannot be secured locked shut. | The locking mechanism on this entrance door to the building should be repaired or replace immediately so that this building has restricted access to authorised persons only. Awtg Silk & Mackman prog. Mid Dec 2014 | Claire Williams |  | S&Mackman completed works end of Dec, but probs over Christmas meant revisit and works completed mid Jan 2015. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:06 | 2014-12-22 10:07 | CLWILLIAMS | [6 empty] | 2014-12-01 10:06 | 2015-03-26 13:36 | CLWILLIAMS | 2014-12-01 10:06 | 2014-12-22 10:07 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:06
17085 | 172155 | Completed | GRENFELL TOWER - 2014.10.17 | 3a | High | The fire fighter entry over ride device fitted to the entrance door of this building did not function and release the locking device on the door and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride device fitted to the entrance door of this building should be repaired or replaced so that it releases the locking device fitted to the buildings entrance door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | Claire Williams | 2015-05-08 | Siobhan Rumble confirmed that this safety check should be undertaken regularly by her estates services team. As a result of the latest report on 10/4 SR instructed Paul Steadman to carry out this check. Confirmed checked and working as at today's date 8 May 2015. Please transfer to SR as regular monitoring is within her team responsibility | 2015-05-08 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:08 | 2014-12-22 10:14 | CLWILLIAMS | [6 empty] | 2014-12-01 10:08 | 2015-05-11 14:22 | CLWILLIAMS | 2014-12-01 10:08 | 2014-12-22 10:14 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:08
17085 | 172156 | Completed | GRENFELL TOWER - 2014.10.17 | 7 | High | At the time of this assessment there was some damage noticed to the installed lightning protection system in this building. At the time of the last service on this lightning protection system, 4th February 2014, the system was compliant. | I would recommend that the lightning protection system installed to cover this building is repaired immediately and then the whole system retested to ascertain that it is fully functional. Rydon getting price. Ult new frame will be conductor | Claire Williams | 2015-03-25 | Held meeting with M&E team and Rydon. Rydon said they would consider looking at items on servicing list, but none received. CW passed back to Alex Bosman - before Christmas 2014. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:14 | 2014-12-22 10:16 | CLWILLIAMS | [6 empty] | 2014-12-01 10:14 | 2015-03-26 13:37 | CLWILLIAMS | 2014-12-01 10:14 | 2014-12-22 10:16 | Claire Williams | Lightning Protection | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:14
17085 | 172159 | Completed | GRENFELL TOWER - 2014.10.17 | 8 | High | On the 19th and 20th floor levels push bikes have been chained to the dry rising main outlets. | The dry rising main outlets must not be obstructed at anytime, these push bikes should not be chained to these outlets and the owners of the push bikes must be told not to do this. | Siobhan Rumble |  | these have been removed | 2015-03-06 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:16 | 2014-12-22 10:18 | SRUMBLE | [6 empty] | 2014-12-01 10:16 | 2015-03-10 14:54 | SRUMBLE | 2014-12-01 10:16 | 2014-12-22 10:18 | Siobhan Rumble | Communal Area Storage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2014-12-01 10:16
17085 | 172160 | Completed | GRENFELL TOWER - 2014.10.17 | 9 | High | There is a secondary exit route from the basement boiler room area. | The location of this secondary exit from the basement boiler room area should be emphasised to contractors who are working in this area. This secondary exit should not be blocked or obstructed at any time, this is internally in the boiler room and externally where the exit leaves the building. Also see item 12a below. Awaiting Rydon's H&S plan for works | Claire Williams |  | Secondary fire exit is now in place and unobstructed. This is being monitored by Rydon's own H&S team because of ongoing works to the boiler basement. | 2015-06-18 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:18 | 2014-12-22 10:19 | CLWILLIAMS | [6 empty] | 2014-12-01 10:18 | 2015-06-19 15:34 | CLWILLIAMS | 2014-12-01 10:18 | 2014-12-22 10:19 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:18
17085 | 172161 | Completed | GRENFELL TOWER - 2014.10.17 | 12a | High | There is a secondary exit route from the basement boiler room area. It is not known when this hatch was last opened and checked to see that it operated correctly. | Can it be confirmed that regular inspections and checks are carried out to see that the hatch on this secondary route from the basement boiler room area works correctly and opens easily. Rydons opened it - but lethal as v heavy, not sprung. | Claire Williams |  | The secondary access above is not being used. A new access has been formed by a scaffold with ladder access that comes up on the west elevation close to the walkway. This was put in place with Rydon's H&S officer's agreement to overcome issues of the heavy hatch highlighted above. | 2015-06-18 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:20 | 2014-12-22 10:21 | CLWILLIAMS | [6 empty] | 2014-12-01 10:20 | 2015-06-19 15:38 | CLWILLIAMS | 2014-12-01 10:20 | 2014-12-22 10:21 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:20
17085 | 172163 | Completed | GRENFELL TOWER - 2014.10.17 | 12b | High | The access door to the external roof from the internal corridor has had both of the "Gerda" locks removed from it, this door is now only secured by a normal latch type lock opened by a door handle. This door is now damaged and does not shut securely. | I would recommend that this door is repaired or replaced and that locks or a device is fitted to this roof door so that it can be secured fully and that the door does not flap in the wind and get damaged. | John Tatham | 2014-12-22 | 201554098 RD confirm completion | 2016-03-05 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:22 | 2014-12-22 10:23 | JWRAY | [6 empty] | 2014-12-01 10:22 | 2016-03-07 17:23 | JWRAY | 2014-12-01 10:22 | 2014-12-22 10:23 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:22
17085 | 172164 | Completed | GRENFELL TOWER - 2014.10.17 | 12c | High | The contractors are going to erect new cupboards on each of the residential flat/lift lobby areas to enclose pipe work. | Can it please be confirmed that these new cupboards will be a minimum of 30 minutes fire rated with FD30 doors on them fitted with cold smoke seals? Confirmed in spec as FD30s | Claire Williams | 2015-04-10 | The new cupboards will be FD30 doors as described above. | 2015-04-10 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:23 | 2014-12-22 10:25 | CLWILLIAMS | [6 empty] | 2014-12-01 10:23 | 2015-04-13 16:56 | CLWILLIAMS | 2014-12-01 10:23 | 2014-12-22 10:25 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:23
17085 | 172168 | Completed | GRENFELL TOWER - 2014.10.17 | 12d | High | The fire door to the refuse chute room on the 14th floor level grounds and will not shut fully. | I would recommend that this door to the refuse chute room on the 14th floor level is repaired so that is does not ground and that the self closing device shuts the door fully onto its stops. | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:25 | 2014-12-22 10:27 | JWRAY | [6 empty] | 2014-12-01 10:25 | 2016-02-23 20:29 | JWRAY | 2014-12-01 10:25 | 2014-12-22 10:27 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:25
17085 | 172169 | Completed | GRENFELL TOWER - 2014.10.17 | 12e | High | The fire door to the staircase from the lift lobby areas on the 2nd and 19th floor levels are damaged and do not shut fully. | I would recommend that these doors are repaired or replaced so that they shut fully. | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:28 | 2014-12-22 10:28 | JWRAY | [6 empty] | 2014-12-01 10:28 | 2016-02-23 20:33 | JWRAY | 2014-12-01 10:28 | 2014-12-22 10:28 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:28
17085 | 172170 | Completed | GRENFELL TOWER - 2014.10.17 | 12f | High | On the 10th floor level the refuse chute hopper head is damaged - it's handle is missing and it does not shut fully | This hopper head to the rubbish chute on the 10th floor level should be repaired or replaced so that it shuts fully. | John Tatham | 2014-12-22 | 201554019 RD confirm completion | 2016-03-05 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:29 | 2014-12-22 10:31 | JWRAY | [6 empty] | 2014-12-01 10:29 | 2016-03-07 17:25 | JWRAY | 2014-12-01 10:29 | 2014-12-22 10:31 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:29
17085 | 172171 | Completed | GRENFELL TOWER - 2014.10.17 | 12g | High | The door frame and door within the boiler room at the base of the staircase from ground level down into the boiler room (which is located at basement level under Grenfell Tower) is damaged and the door does not shut fully. | I would recommend that this door and door frame are repaired / replaced so that they protect the staircase and that the door is shut fully by the self closing device fitted to it. Rydon's are pricing for new door. They start their boiler works from 8 December, so will be in place by then. | Claire Williams | 2015-03-25 | Remedial works were completed Jan 2015. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:32 | 2014-12-22 10:33 | CLWILLIAMS | [6 empty] | 2014-12-01 10:32 | 2015-03-26 14:30 | CLWILLIAMS | 2014-12-01 10:32 | 2014-12-22 10:33 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:32
17085 | 172174 | Completed | GRENFELL TOWER - 2014.10.17 | 12h | High | The door handle of the staircase door (separating lift lobby and staircase) is missing on the staircase side on the 13th floor level. | A new door handle should be fitted to this staircase door. | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:33 | 2014-12-22 10:35 | JWRAY | [6 empty] | 2014-12-01 10:33 | 2016-02-02 19:58 | JWRAY | 2014-12-01 10:33 | 2014-12-22 10:35 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:33
17085 | 172176 | Completed | GRENFELL TOWER - 2014.10.17 | 12i | Information Only | The following flat entrance doors are the original fire rated flat entrance doors and which were fitted with a self closing device. These are flush solid doors and are all close fitting. These flats are numbers 56, 61, 86, 92, 112, 142, 154, 156, 165,166, 174.185, 195, and 206. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. For information only - please fully complete | David Ward |  | None | 2014-12-08 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:36 | 2014-12-22 10:42 | DWARD | [6 empty] | 2014-12-01 10:36 | 2014-12-09 16:27 | DWARD | 2014-12-01 10:36 | 2014-12-22 10:42 | David Ward | Flat Door | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Home Ownership |  |  |  | 2014-12-01 10:36
17085 | 172177 | Completed | GRENFELL TOWER - 2014.10.17 | 14a | High | There are two largish holes in the wall linings of the ground floor electrical room from the base staircase into the electrical room. | These holes should be filled in with a suitable fire rated material to maintain the fire rating of the structure of the building. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all wall and ceiling linings have been made good so that the structural elements of the buildings remain fire rated. Rydon to carry out. These are the cables to the mast climbers. By first week of Dec 2014 | Claire Williams | 2015-03-25 | completed jan 2015. contractor Rydon will check, and it is understood that Carl Stokes FR Assessor will liaise if at any visits any further issues arise. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:43 | 2014-12-22 10:44 | CLWILLIAMS | [6 empty] | 2014-12-01 10:43 | 2015-03-26 14:27 | CLWILLIAMS | 2014-12-01 10:43 | 2014-12-22 10:44 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:43
17085 | 172180 | Completed | GRENFELL TOWER - 2014.10.17 | 14b | High | On the 2nd and the 15th floor levels the panels covering the cable ducts have been removed and not refitted correctly. One is held on with tape. | These covers should be fitted back correctly. . | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:46 | 2014-12-22 10:47 | JWRAY | [6 empty] | 2014-12-01 10:46 | 2016-02-02 20:01 | JWRAY | 2014-12-01 10:46 | 2014-12-22 10:47 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Responsive Repairs |  |  |  | 2014-12-01 10:46
17085 | 172182 | Completed | GRENFELL TOWER - 2014.10.17 | 15 | High | Some new emergency lighting units have been installed by the contractor on the walkway level in the new entrance hall area. | Can a commissioning certificate for these newly installed emergency lighting units please be provided by the contractor. Rydon to provide by mid Dec 2014 | Claire Williams | 2015-05-08 | Certificate attached. Put in through 'housing' part of W2 | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:48 | 2014-12-22 10:49 | CLWILLIAMS | [6 empty] | 2014-12-01 10:48 | 2015-05-11 10:35 | CLWILLIAMS | 2014-12-01 10:48 | 2014-12-22 10:49 | Claire Williams | Emergency Lighting | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:48
17085 | 172185 | Completed | GRENFELL TOWER - 2014.10.17 | 16a | High | There are no fire action notices displayed in this building next to the break glass call points of the fire alarm system. This is in the basement boiler room and in the roof level areas of this building. These notices describe the actions to be undertaken in the event of discovering a fire or if the fire alarm sounds. There are manual break glass call points in each electrical room. | Fire action notices should be displayed next to each break glass call point of the fire alarm system installed in this building. Notices available - Handyman to be asked to fit | Janice Wray |  | Fire action notioces now installed by handyman. COMPLETED | 2014-12-01 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:49 | 2014-12-22 10:51 | JWRAY | [6 empty] | 2014-12-01 10:49 | 2014-12-02 14:09 | JWRAY | 2014-12-01 10:49 | 2014-12-22 10:51 | Janice Wray | Signage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2014-12-01 10:49
17085 | 172187 | Completed | GRENFELL TOWER - 2014.10.17 | 16b | Medium | The floor number on staircase landing on the 16th floor level has been altered to look like an 18. Floor numbers aid the fire service if there is an incident in this building. | I would recommend that the 16th floor number is altered back to 16 from 18. Opposite the lifts and on each staircase landings of this building where there is a balcony. Seamus or OCS to sort | Siobhan Rumble |  | all done | 2015-03-06 | Level 3 Grenfell Tower - 2014.10.17 |  |  |  | 2014-12-01 10:51 | 2015-01-30 10:53 | SRUMBLE |  |  |  | 2014-12-01 10:51 | 2015-03-10 14:54 | SRUMBLE | 2014-12-01 10:51 | 2015-01-30 10:53 | Siobhan Rumble | Signage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2014-12-01 10:51
17085 | 172190 | Completed | GRENFELL TOWER - 2014.10.17 | 16c | Medium | The sign displayed in the ground floor level entrance lobby area of this building informing the emergency services which flats are located on which floor levels now needs to be moved up to the walkway level. This sign aids the fire service or other emergency service to where an incident in this building maybe. | I would recommend that the sign displayed in the ground floor level entrance lobby area of this building showing which flat numbers are located on which floor level is moved up to the walkway level. Emergency services have said they will enter thro ground floor - so no need to change. | Claire Williams | 2015-03-25 | As comment on 'action taken' fire brigade have said they will entre thro the ground floor, and all watches have done familiarisation visits. NFA required. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 |  |  |  | 2014-12-01 10:53 | 2015-01-30 10:55 | CLWILLIAMS |  |  |  | 2014-12-01 10:53 | 2015-03-26 14:31 | CLWILLIAMS | 2014-12-01 10:53 | 2015-01-30 10:55 | Claire Williams | Signage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:53
17085 | 172191 | Completed | GRENFELL TOWER - 2014.10.17 | 16d | Information Only | When the new pipe work cupboards are constructed on each flat/lift lobby area the floor number on wall will be covered in by the cupboard. Floor numbers aid the fire service if there is an incident in this building. | I would recommend that new floor numbers are displayed on the walls of each flat/lift lobby area opposite the lifts. These numbers must be in a large font and be easily seen at all times. Rydon will paint/fit numbers onto new cupd drs | Claire Williams | 2015-03-25 | As actions - Rydon to paint or fit numerals onto cupboard doors. Temporary signs proposed until final version installed when doors fitted and decorated. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 10:55 | 2015-03-26 14:32 |  |  |  |  | Signage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 10:55
17085 | 172192 | Completed | GRENFELL TOWER - 2014.10.17 | 17a | High | There is a fire alarm system installed in this building there are no TMO employees who work in this building now. | I would recommend that the fire alarm system in this building is connected to a monitoring station/service so in the event of an activation of the fire alarm system the fire service or an on duty caretaker is informed. Paul S was pressing button, but not checking autodialler and speaking to anyone. Rydon tested, and the response was not tested since 8 Nov 2013! | Janice Wray | 2015-08-20 | FA monitored by CAS / Tunstall Telecom | 2016-08-31 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:57 | 2014-12-22 10:59 | JWRAY | [6 empty] | 2014-12-01 10:57 | 2016-09-01 06:57 | JWRAY | 2014-12-01 10:57 | 2014-12-22 10:59 | Janice Wray | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2014-12-01 10:57
17085 | 172193 | Completed | GRENFELL TOWER - 2014.10.17 | 17b | High | The contractor has moved the buildings fire alarm control panel up from the ground floor level to the walkway level. | I would recommend that a fire alarm completion certificate is obtained from the contractor to state that the fire alarm panel is in full working order. Rydon to provide Mid Dec 2014 | Claire Williams | 2015-05-08 | Certificate stored on W2 under 'housing' part of system. This says that the panel is in the same working order as it was taken over. The assumption is that this is still being serviced by Chubb - please check with Alex Bosman's team. | 2015-05-08 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 10:59 | 2014-12-22 11:02 | CLWILLIAMS | [6 empty] | 2014-12-01 10:59 | 2015-05-11 13:44 | CLWILLIAMS | 2014-12-01 10:59 | 2014-12-22 11:02 | Claire Williams | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management | 2014-12-01 10:59 | 2015-05-15 13:43 | JWRAY | 2014-12-01 10:59 | Janice Wray
17085 | 172195 | Completed | GRENFELL TOWER - 2014.10.17 | 17c | High | The fire alarm control panel was showing faults in both zones 9 and 22 at the time of this assessment. | I would recommend that a fire alarm engineer is asked to visit site and clear the faults from this fire alarm control panel immediately. Rectified 20 Oct 2014 | Claire Williams | 2015-03-25 | Panel now functionning as remedial works undertaken. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:03 | 2014-12-22 11:04 | CLWILLIAMS | [6 empty] | 2014-12-01 11:03 | 2015-03-26 14:34 | CLWILLIAMS | 2014-12-01 11:03 | 2014-12-22 11:04 | Claire Williams | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 11:03
17085 | 172201 | Completed | GRENFELL TOWER - 2014.10.17 | 17d | High | In the old ground floor reception there are the fire alarm control panels for the fire alarm detection systems in the nearby TMO buildings. | Can the TMO surveyor responsible for this project please comment on how access to these control panels will be maintained throughout this project? Are these control panels and the smoke ventilation systems in the nearby TMO buildings being serviced and maintained in full working order? Mtg to be booked with CS to discuss prop for finger blocks | Claire Williams | 2015-04-10 | Alex Bosman leading on getting smoke ventilation systems for nearby blocks working as connection with Grenfell severed and system clearly not been in full working order for a while. AB looked at intro perm vent through atrium roofing, but outcome not known. AB to update. | 2015-04-10 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:05 | 2014-12-22 11:06 | CLWILLIAMS | [6 empty] | 2014-12-01 11:05 | 2015-04-13 17:06 | CLWILLIAMS | 2014-12-01 11:05 | 2014-12-22 11:06 | Claire Williams | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 11:05
17085 | 172203 | Completed | GRENFELL TOWER - 2014.10.17 | 17e | High | When the new cupboards are constructed on the flat /lift lobby area the presently installed smoke detectors on these lift lobby areas will be inside the new cupboards in some cases. | Can the contractor please provide the scope of works for the new fire alarm detection installation for the smoke vents? Detectors to be positioned 500mm from obstruction May 2015 | Claire Williams |  | As action to be taken comments. smoke detection alarms to be 500mm distant from smoke vents or other obstructions. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:07 | 2014-12-22 11:20 | CLWILLIAMS | [6 empty] | 2014-12-01 11:07 | 2015-03-26 14:36 | CLWILLIAMS | 2014-12-01 11:07 | 2014-12-22 11:20 | Claire Williams | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 11:07
17085 | 172211 | Completed | GRENFELL TOWER - 2014.10.17 | 19a | High | The lifts in this building are fire fighter/evacuation lifts, the entrance to this building is now from the walkway level. It is not known if the fire service override controls for these lifts have been moved? | Have these two lifts been reprogrammed so that the fire service can control them from the walkway level? Have the fire service control switches been relocated to the walkway level from the ground/ street level? If so can the service documents and certificates from the lift contractors please be forwarded so that there is evidence if required that the lifts are in full working order as fire fighter/evacuation lifts. Fire brigade will access from GF, so no need to relocate equipment | Claire Williams | 2015-03-25 | as 'actions to be taken', fire brigade enter building from gf, so the fire service override control stays in the same position. | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:20 | 2014-12-22 11:22 | CLWILLIAMS | [6 empty] | 2014-12-01 11:20 | 2015-03-26 14:37 | CLWILLIAMS | 2014-12-01 11:20 | 2014-12-22 11:22 | Claire Williams | Lifts | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 11:20
17085 | 172213 | Completed | GRENFELL TOWER - 2014.10.17 | 19b | High | There are fire fighting hose reels in the basement boiler room of this building, these hose reels have not been serviced according to the servicing labels attached to each item since August 2012. I am told that these hose reels are due to be removed as part of the boiler room refurbishment work. | Please can it be confirmed that the fire fighting hose reels in the basement boiler room of this building are being removed as part of the boiler room refurbishment work? If they are not then they should be serviced immediately with any defects found rectified. | Alex Bosman |  | Confirmed fire hose reels will be removed during boiler works | 2015-12-01 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:23 | 2014-12-22 11:29 | MARES | [6 empty] | 2014-12-01 11:23 | 2015-12-02 13:41 | MARES | 2014-12-01 11:23 | 2014-12-22 11:29 | Maria Ares | Hose Reels | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2014-12-01 11:23
17085 | 172214 | Completed | GRENFELL TOWER - 2014.10.17 | 19c | High | The dry rising main in this building is overdue its service according to the last service certificate seen. | The dry rising main in this building should be serviced immediately with any defects found rectified. Is the more recent servicing sheet now available? | Alex Bosman |  | Chub satisfactory test cert held carried out 27.4.2015 | 2015-12-01 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:30 | 2014-12-22 11:31 | MARES | [6 empty] | 2014-12-01 11:30 | 2015-12-02 13:43 | MARES | 2014-12-01 11:30 | 2014-12-22 11:31 | Maria Ares | Dry or Wet Riser | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2014-12-01 11:30
17085 | 172215 | Completed | GRENFELL TOWER - 2014.10.17 | 19d | High | The contractors, Rydon's are going to be working to upgrade the installed smoke extraction system on the flat/lift lobby areas and the refuse chute rooms of this building. | Can it please be confirmed what compensatory measures, if any are being put in place whilst the installed smoke extraction systems are being up graded? Once the new extraction system has been installed then a commissioning certificate for the system must be obtained stating that the smoke extraction system(s) is fully functional. Liaison with LFB, agreement for no hot works, increased inspections etc. | Claire Williams | 2015-04-10 | Fire brigade informed that the smoke vent system being worked on, therefore not working. They have sent all watches to site to understand the set up. Subsequently at a small fire, LFB turned up with breathing apparatus - so all were aware of situation. Passive system due to be complete by end of May, new fans etc just received building control ok - completion summer when certification will be received. | 2015-04-10 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 11:32 | 2014-12-22 12:09 | CLWILLIAMS | [6 empty] | 2014-12-01 11:32 | 2015-04-13 17:09 | CLWILLIAMS | 2014-12-01 11:32 | 2014-12-22 12:09 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 11:32
17085 | 172230 | Completed | GRENFELL TOWER - 2014.10.17 | 19e | Information Only | As part of the refurbishment work to be undertaken in this building the dry riser inlet is to be moved from its current located in the ground floor lobby area to an external position on the face of the building | When this work has been undertaken then a new commissioning certificate for the dry rising main must be obtained stating that the main is fully functional and has passed its hydraulic test. Rydon will not move this until have cert showing in working condition currently. Awaiting Alex info as 19c above. | Claire Williams | 2015-03-25 | awaiting M&E team to provide certification on current dry riser before Rydon's touch it. Alex Bosman leading on this. Cert provided to assessor | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 12:09 | 2017-03-13 10:25 |  |  |  |  | Dry or Wet Riser | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management | 2014-12-01 12:09 | 2015-04-21 21:14 | JWRAY | 2014-12-01 12:09 | Janice Wray
17085 | 172234 | Completed | GRENFELL TOWER - 2014.10.17 | 22a | High | There are contractors working in this building refurbishing the lower floor levels, the street level to the walkway level, this includes constructing some new dwellings. | I would recommend that the contractors, Rydons are asked for a copy of their FRA. This FRA should be inspected and any points concerning any fixed systems covering the residential parts of the building or items involving the common parts of the residential areas noted and acted upon if required. Rydon to forward their H&S plan and evacuation policy. Mid Dec 2014 | Claire Williams | 2015-03-25 | attached | 2015-03-25 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:12 | 2014-12-22 12:13 | CLWILLIAMS | [6 empty] | 2014-12-01 12:12 | 2015-03-26 14:38 | CLWILLIAMS | 2014-12-01 12:12 | 2014-12-22 12:13 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 12:12
17085 | 172235 | Completed | GRENFELL TOWER - 2014.10.17 | 22b | High | There are contractors working in this building refurbishing the lower floor levels, the street level to the walkway level, this includes constructing some new dwellings. | I would recommend that the contractors, Rydons are asked for a copy of their evacuation policy and procedure for a fire incident within the area of this building under their control. As a minimum this policy should have their procedure for the evacuation of their employees, how the TMO residents will be alerted to any incident in the contractors areas and how Rydons will manage any incident. This includes information on incidents which might occur at night or the weekends. Rydon to forward their H&S plan and evacuation policy Mid Dec 2014 | Claire Williams |  | Contractor has their fire risk procedure, which will be amended as works progress/issues change. I attach a version of their risk assessment. It is noted that Rydon H&S team visit site regularly, as well as their own site managers' responsibility for safety checks. | 2015-05-08 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:13 | 2014-12-22 12:17 | CLWILLIAMS | [6 empty] | 2014-12-01 12:13 | 2015-05-11 10:50 | CLWILLIAMS | 2014-12-01 12:13 | 2014-12-22 12:17 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 12:13
17085 | 172239 | Completed | GRENFELL TOWER - 2014.10.17 | 23a | High | The emergency lighting system installed to cover the common parts of this building appears to be overdue for its annual service, maintenance and discharge test. | I would recommend that the installed emergency lighting system in this building is serviced, tested and a discharge test of the batteries in the units undertaken immediately. Any defects should be rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future annual servicing. | Alex Bosman | 2016-01-21 | AP confirmed service complete 9.12.2015 | 2016-01-21 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:18 | 2014-12-22 12:19 | MARES | [6 empty] | 2014-12-01 12:18 | 2016-01-22 13:02 | MARES | 2014-12-01 12:18 | 2014-12-22 12:19 | Maria Ares | Emergency Lighting | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2014-12-01 12:18
17085 | 172240 | Completed | GRENFELL TOWER - 2014.10.17 | 23b | High | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Siobhan Rumble |  | these were done by RGE 6 monthly under contract. inspectors check the block lighting to check if all bulbs and emergency lighting are working and records are kept | 2015-03-06 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:19 | 2014-12-22 12:22 | SRUMBLE | [6 empty] | 2014-12-01 12:19 | 2015-03-10 14:56 | SRUMBLE | 2014-12-01 12:19 | 2014-12-22 12:22 | Siobhan Rumble | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2014-12-01 12:19
17085 | 172242 | Completed | GRENFELL TOWER - 2014.10.17 | 23c | High | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? Including testing the automatic smoke vents | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, including testing the smoke vents with the results recorded as proof of the inspections having been undertaken. | Siobhan Rumble |  | being done by rydons | 2015-03-06 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:23 | 2014-12-22 12:24 | SRUMBLE | [6 empty] | 2014-12-01 12:23 | 2015-03-10 14:57 | SRUMBLE | 2014-12-01 12:23 | 2014-12-22 12:24 | Siobhan Rumble | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2014-12-01 12:23
17085 | 172245 | Completed | GRENFELL TOWER - 2014.10.17 | 23d | High | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Siobhan Rumble |  | yes and these are available for inspection at any time | 2015-03-06 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:25 | 2014-12-22 12:27 | SRUMBLE | [6 empty] | 2014-12-01 12:25 | 2015-03-10 14:59 | SRUMBLE | 2014-12-01 12:25 | 2014-12-22 12:27 | Siobhan Rumble | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2014-12-01 12:25
17085 | 172246 | Completed | GRENFELL TOWER - 2014.10.17 | 23e | Information Only | The fire alarm system installed in this building is due for a test/service and maintenance next month, November 2014. | I would recommend that the fire alarm engineers liaise with the contractors when they undertake the fire alarm system service next month. | Alex Bosman |  | complete - system no longer present | 2015-11-17 | Level 3 Grenfell Tower - 2014.10.17 | [9 empty] | 2014-12-01 12:28 | 2015-11-18 13:49 |  |  |  |  | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2014-12-01 12:28
17085 | 172247 | Completed | GRENFELL TOWER - 2014.10.17 |  | High | The external face of this building is to be over clad. The piece of cladding fixed to the external wall at the moment is on timber battens. | I would recommend that the contractor provides 1. The scope of works covering how this cladding? How will the cladding be fixed to the building? 2. What fixings will be used? 3. The fire rating of the cladding and the fixings? 4. The Building Control Officers acceptance of this fixing system and the cladding used? Timber battens purely for mock-up. Cladding has horiz cavity barrier to 30/30. Awtg building regs approval. May 2015 for full building regs approval. | Claire Williams |  | The contractor has provided information on cladding, inc fixings, fire barriers. This is being inspected as work progresses by the Clerk of Works employed by the TMO as well as Building Control officer (John Hoban). Building control payment for services attached. The final cert will not be issued by them until the end of the job. | 2015-05-08 | Level 3 Grenfell Tower - 2014.10.17 | 2014-12-01 12:30 | 2014-12-22 12:32 | CLWILLIAMS | [6 empty] | 2014-12-01 12:30 | 2015-05-11 10:57 | CLWILLIAMS | 2014-12-01 12:30 | 2014-12-22 12:32 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2014-12-01 12:30
24314 | 269272 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 0 | High | No Item Number High When the construction/refurbishment work is completed on this building all information as required by the Building Regulations, must be handed over to the TMO by the contractors before they hand back the building to the TMO. | Documentation must include: 1. A Buildings Regulations completion Certificate as issued by the RBKC Building Control department. Claire W confirms received - accessed in Grenfell Audit Folder 2. All the Regulation 38 information as required by the Building Regulations. 3. New Electrical certificates for any electrical wiring work undertaken, this is for the new dwellings and any common parts wiring - CW confirms certs on T-drive under A&R / Grenfell 4. New commissioning certificates for any fixed fire systems that have been worked on by them or contractors working on their behalf, Dry Riser, smoke ventilation, fire alarm system etc - CW confirms certs on T-drive under A&R / Grenfell This is so that if this building is audited by the Fire Authority under the Fire Safety Order documentation can be provided. JW | Janice Wray | 2016-09-05 | Claire Williams confirms that Buildig Regns Completion Certificate received & stored on T:drive A&R / Grenfell | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 15:45 | 2016-08-29 15:54 | JWRAY | [6 empty] | 2016-08-08 15:45 | 2016-09-01 18:42 | JWRAY | 2016-08-08 15:45 | 2016-08-29 15:54 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-08 15:45
24314 | 269274 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 0 | Information Only | The layout floor level drawings of this building now do not reflect the building layout after the recent construction work has been undertaken. | I would recommend that the buildings floor level drawings are updated. CW to provide for forwarding to Fire Risk assessor JW | Janice Wray | 2017-02-06 | Drawings provided to Fire Risk Assessor by Claire Williams | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | [9 empty] | 2016-08-08 16:04 | 2016-09-01 18:44 |  |  |  |  | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-08 16:04
24314 | 269277 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 1a | High | The electrical fixed wiring in this building is presently within test date, but this building has had major electrical work undertaken on some fixed wiring during the present refurbishment. | I would recommend that a full fixed electrical periodic wiring test of the landlords areas of this building is undertaken when the present work by Rydons is completed. Any defects found should be rectified. | Alex Bosman | 2016-09-05 | Confirm RMA have completed the testing and on asite works & Certificate awaited | 2016-11-07 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:07 | 2016-08-29 16:09 | JWRAY | [6 empty] | 2016-08-08 16:07 | 2016-11-08 16:27 | JWRAY | 2016-08-08 16:07 | 2016-08-29 16:09 | Janice Wray | Wiring Inspection | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2016-08-08 16:07
24314 | 269278 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 1b | High | At the time of this assessment the lighting was not working in some roof level areas of this building. A check should be undertaken on all of the lighting circuits and light units at the roof level and any defect wiring or bulbs etc repaired or replaced so that the lighting is in full working order. | Nicky Could Paul Steadman check if the lighting in this area is now all operational and if not put it thro to repairs (as I'm not clear of the detail of what works or if it has now been repairs) Janice | Nicola Bartholomew | 2016-09-05 | Alex Bosman confirms that RMA have completed works on site - Certificate awaited | 2016-11-07 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:09 | 2016-08-29 16:11 | JWRAY | [6 empty] | 2016-08-08 16:09 | 2016-11-08 16:31 | JWRAY | 2016-08-08 16:09 | 2016-08-29 16:11 | Janice Wray | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-08 16:09
24314 | 269280 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2 | High | Behind the wire mesh gate off the staircase on the upper floor level to the roof there are used cigarette ends on the floor. | These used cigarette ends should be cleared up and persons remaindered that smoking is not allowed within this building. Nicky Could Paul please increase his inspections in this area and instigate whatever cleaning is required to ensure that this issue is kept under control Janice | Nicola Bartholomew | 2016-09-05 | inspections ongoing | 2017-03-13 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:12 | 2016-08-29 16:13 | JWRAY | [6 empty] | 2016-08-08 16:12 | 2017-03-14 17:05 | JWRAY | 2016-08-08 16:12 | 2016-08-29 16:13 | Janice Wray | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-08 16:12
24314 | 269281 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 3 | Information Only | There is no fireman override switch fitted to the ground floor entrance hall to lift lobby area door. There is one fitted to the buildings entrance/exit door. | No actions are required. The fireman's override switch fitted to the buildings ground floor entrance/exit door releases all the ground floor door locks for a 90 second time period. This has been agreed with the Building Control Officer. So the emergency services can access all the ground floor level areas. | Janice Wray | 2017-02-06 | CONFIRMED | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | [9 empty] | 2016-08-08 16:14 | 2016-09-01 18:45 |  |  |  |  | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-08 16:14
24314 | 269282 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 4 | High | The contractor's are presently working on the boilers in the basement area, there are no flue gas print outs should be attached to the gas boilers. Gas safety certificates have been forwarded to the TMO for the installation work undertaken. | I would recommend that once all work connected with the gas boilers is completed that a final full gas safety check is undertaken and any defects found are rectified. Flue gas print outs should be attached to each gas boiler. Claire - we agreed that you would check with Rydons whether the new technology has superceded this requirement | Claire Williams | 2016-09-05 | Documents attached. In O&M manual - not in basement. | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:16 | 2016-08-29 16:17 | CLWILLIAMS | [6 empty] | 2016-08-08 16:16 | 2016-09-01 19:41 | CLWILLIAMS | 2016-08-08 16:16 | 2016-08-29 16:17 | Claire Williams | Boiler | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management | 2016-08-08 16:16 | 2016-09-07 19:40 | JWRAY | 2016-08-08 16:16 | Janice Wray
24314 | 269283 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 5 | High | At the roof level the last entry in the service book for the plant and extraction equipment located here was on the 5th April 2016, before this there were more frequent servicing and maintenance visits. For the basement water pumps the last check/service was on the 16th April 2016. | Can the frequency of inspection / testing visits by the ppm contractors please be confirmed. (Paperwork indicates annual but believed to be monthly for this type of plant elsewhere) | Alex Bosman | 2016-09-05 | Completed. Equipment on Engie servicing programme. Monthly inspections carried out | 2017-01-06 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:18 | 2016-08-29 16:20 | MARES | [6 empty] | 2016-08-08 16:18 | 2017-01-09 08:27 | MARES | 2016-08-08 16:18 | 2016-08-29 16:20 | Maria Ares | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2016-08-08 16:18
24314 | 269284 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 9b & 12a | High | There is a secondary exit route from the basement boiler room area. This metal hatch and the frame is badly rusted. | The secondary exit from the basement boiler room area should be maintained available at all times. The location of this secondary exit from the basement boiler room area should be emphasised to contractors who are working in this area. This secondary exit should not be blocked or obstructed at any time, this is internally in the boiler room and externally where the exit leaves the building. Also see item 12a below. John Griffin believed to have raised order for metalwork contractors to replace failed hinges - email on 20th July for update - JW | Janice Wray | 2016-09-05 | Hatch is being overhauled & hinges replaced etc. John Griffin progressing work. | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:21 | 2016-08-29 16:24 | JWRAY | [6 empty] | 2016-08-08 16:21 | 2016-09-01 18:50 | JWRAY | 2016-08-08 16:21 | 2016-08-29 16:24 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-08 16:21
24314 | 269290 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 9b | High | There is a lot of contractors waste in the basement boiler room. | All contractors waste and rubbish in the basement boiler room and rooms off of it should be removed before this area is handed back to the TMO. Claire advises that Rydons have now removed all of the rubbish left by their contractors & what is left is historic - can your contractors remove this? JW Alex | Alex Bosman | 2016-09-05 | All have been removed. | 2016-09-08 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:37 | 2016-08-29 16:43 | GKENNEDY | [6 empty] | 2016-08-08 16:37 | 2016-09-09 14:22 | GKENNEDY | 2016-08-08 16:37 | 2016-08-29 16:43 | Gillian Kennedy | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2016-08-08 16:37
24314 | 269294 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12b | High | The timber doors of the new cupboards erected on each of the flat/lift lobby areas are not marked as 30 minute fire rated doors. | The contractors should be asked why the new doors in this building are not marked as fire rated doors? Documentation has been obtained stating that all of the new timber doors in this building are certified 30 minute or 60 minute fire rated doors. | Janice Wray | 2016-09-05 | Claire W confirms that documentation has been obtained to confirm doors are complaint - this is available at the Grenfell audit location on the T drive | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-08 16:49 | 2016-08-29 16:51 | JWRAY | [6 empty] | 2016-08-08 16:49 | 2016-09-01 18:56 | JWRAY | 2016-08-08 16:49 | 2016-08-29 16:51 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-08 16:49
24314 | 269356 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12c | High | Some of the new doors in this building are not fitted with cold smoke seals as required by the Building Regulations. The Building Control Officer has stated that smoke seals should not be fitted to these doors. | If this is the case the Building Control Officer should be asked to put this in writing because if this building is audited by the LFB under the Fire Safety Order them this document will be needed as evidence. | Janice Wray | 2016-09-06 | E-mail from Building Control provided to Assessor (& in H&S Fire directory) | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:22 | 2016-08-30 12:25 | JWRAY | [6 empty] | 2016-08-09 12:22 | 2016-09-01 18:57 | JWRAY | 2016-08-09 12:22 | 2016-08-30 12:25 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-09 12:22
24314 | 269357 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12d | High | It was noted that some of the intumescent strips on the newly installed fire doors have been painted over. | All new fire doors should be checked to see that intumescent strips have not been painted over, if they have then new intumescent strips should be fitted. | Janice Wray | 2016-09-06 | C Stokes asked to provide location details and ESA asked to monitor for any damage to these and report asap | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:26 | 2016-08-30 12:27 | JWRAY | [6 empty] | 2016-08-09 12:26 | 2016-09-01 18:59 | JWRAY | 2016-08-09 12:26 | 2016-08-30 12:27 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-09 12:26
24314 | 269361 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 1a | Information Only | Raised in error | Raised in error | Janice Wray | 2016-10-28 | RAISED IN ERROR | 2016-09-07 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | [9 empty] | 2016-08-09 12:29 | 2016-09-08 12:33 |  |  |  |  | Miscellaneous | GRENFELL TOWER LANCASTER WEST ESTATE | GRENFELL TOWER LANCASTER WEST ESTATE | S217012770009 | Health and Safety |  |  |  | 2016-08-09 12:29
24314 | 269363 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12e | High | There is a metal louvered door separating the ground floor lift lobby area from the shaft and electrical intake room. | This metal louvered door is not fire rated what is there not a fire rated door separating the ground floor lift lobby area from the shaft and electrical intake room? | Janice Wray | 2016-09-06 | Claire Williams confirms that an FD30 door has now been installed behind this louvred door | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:29 | 2016-08-30 12:32 | JWRAY | [6 empty] | 2016-08-09 12:29 | 2016-09-01 19:01 | JWRAY | 2016-08-09 12:29 | 2016-08-30 12:32 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-09 12:29
24314 | 269364 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12f | High | The door and frame at the base of the basement staircase is badly damaged as are other fire doors in this basement area. | New certified 30 minute self closing or if cupboard etc fitted with locks, fire rated doors and door sets should be fitted to replace all the damaged fire doors at the basement level. Any new doors fitted must be FD30 fitted with intumescent strips and cold smoke seals. Damaged doors could be repaired if this is possible. | Janice Wray | 2016-09-06 | Order requested - 26th Aug 2016 201622988 & VARIATION ORDER COMPLETED | 2017-05-25 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:32 | 2016-08-30 12:35 | JWRAY | [6 empty] | 2016-08-09 12:32 | 2017-05-29 10:57 | JWRAY | 2016-08-09 12:32 | 2016-08-30 12:35 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety | 2016-08-09 12:32 | 2017-06-02 10:56 | JWRAY | 2016-08-09 12:32 | Janice Wray
24314 | 269366 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12g | High | The flat entrance door of flat 24 is damaged with the letter box missing. | This door should be repaired and a new fire rated letter box fitted, alternatively a new self closing certified 30 minute fire rated door fitted with intumescent strips and cold smoke seals could be installed. RESPONSE REPAIR REQUESTED | Janice Wray | 2016-09-06 | ESA confirms completion | 2017-01-18 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:35 | 2016-08-30 12:36 | JWRAY | [6 empty] | 2016-08-09 12:35 | 2017-01-19 15:23 | JWRAY | 2016-08-09 12:35 | 2016-08-30 12:36 | Janice Wray | Flat Door | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-09 12:35
24314 | 269367 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12h | High | 12h High The flat entrance door of flat 112 is being replaced, this new door is not marked as a fire rated door and it does not have a self closing device fitted to it. Cold smoke seals are fitted. | The occupier of flat 112 should be asked to confirm that the new flat entrance doors is a certified FD30 door, a self closing device should be fitted to this door. Mr Assad - Claire to contact Claire W | Claire Williams | 2016-09-06 | leaseholder emailed by CW but no response. Chased today 16/8. ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | 2017-10-19 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:37 | 2016-08-30 12:39 | JWRAY | [6 empty] | 2016-08-09 12:37 | 2017-10-20 10:06 | JWRAY | 2016-08-09 12:37 | 2016-08-30 12:39 | Janice Wray | Flat Door | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 12:37
24314 | 269368 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12i | High | Some of the staircase doors are not being closed fully by the self closing devices fitted to the doors. These doors should be picked up during the caretakers inspections of the doors. | Any staircase doors which are not being closed fully by the self closing devices should have the self closer adjusted or a new one fitted so that the doors close fully onto their stops. Could Paul Steadman please monitor and raise response repairs as necessary | Nicola Bartholomew | 2016-09-06 | Repairs raised & completed - monitoring ongoing | 2017-03-13 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 12:40 | 2016-08-30 12:53 | JWRAY | [6 empty] | 2016-08-09 12:40 | 2017-03-14 17:06 | JWRAY | 2016-08-09 12:40 | 2016-08-30 12:53 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-09 12:40
24314 | 269374 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 12j | High | The staircase door at the 16th floor level is damaged. | This door should be repaired or alternatively a new self closing certified 30 minute fire rated door fitted with intumescent strips and cold smoke seals could be installed. Could Paul please confirm if this has now been repaired & if not could he raise / chase the repair | Nicola Bartholomew | 2016-09-06 | ESA confirms repair completed | 2017-03-13 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 13:50 | 2016-08-30 13:51 | JWRAY | [6 empty] | 2016-08-09 13:50 | 2017-03-14 17:08 | JWRAY | 2016-08-09 13:50 | 2016-08-30 13:51 | Janice Wray | Responsive Item | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-09 13:50
24314 | 269375 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 15a | High | There is no emergency light unit in the disabled toilet of the new community area. | An emergency light unit should be fitted in the disabled toilet of the new community area. Rydons were undertaking this work, is it now completed? | Claire Williams | 2016-09-06 | Emergency light fitted at the end of July. Elec cert in O&M manual. | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 13:52 | 2016-08-30 14:15 | CLWILLIAMS | [6 empty] | 2016-08-09 13:52 | 2016-08-17 15:35 | CLWILLIAMS | 2016-08-09 13:52 | 2016-08-30 14:15 | Claire Williams | Emergency Lighting | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 13:52
24314 | 269381 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 15b | High | The contractors are still working in areas of this building. | Once all the work is completed an installation/commissioning certificate to BS 5266 Part 1 should be provided for all the newly installed emergency lighting units in this building. This includes marked up drawings showing all of the emergency lighting units and the wiring layouts as well. - CW to provide | Claire Williams | 2016-09-06 | Elec certs in O&M manual. CW to try and upload onto W2 in next week | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:16 | 2016-08-30 14:17 | JWRAY | [6 empty] | 2016-08-09 14:16 | 2016-12-12 12:33 | JWRAY | 2016-08-09 14:16 | 2016-08-30 14:17 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 14:16
24314 | 269383 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 16 | High | There are TMO standard fire action notices are displayed next to each of the fire alarm break glass call points in the basement boiler room and in the roof level areas of this building. | All other fire action notices which give different information should all be removed. Could Paul / Seamus please sort this? | Nicola Bartholomew | 2016-09-06 | Fire Action Notices installed on each lift lobby adjacent to lift - design and content agreed with assessor | 2017-03-13 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:18 | 2016-08-30 14:19 | JWRAY | [6 empty] | 2016-08-09 14:18 | 2017-03-14 17:10 | JWRAY | 2016-08-09 14:18 | 2016-08-30 14:19 | Janice Wray | Signage | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-09 14:18
24314 | 269387 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17a | High | There are 2 areas of this building covered by BS 5839 Part 1 manual and automatic fire detection systems, the roof level area and the basement boiler room. | Where is the fire alarm panel (s) for these fire detection systems? Are these 2 fire alarm systems in full working order? | Janice Wray | 2016-09-06 | Rydons did not work in the roof area. Need to investigate requirement further with assessor & seek inspection /maintenance records ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | 2017-10-19 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:20 | 2016-08-30 14:25 | JWRAY | [6 empty] | 2016-08-09 14:20 | 2017-10-20 10:07 | JWRAY | 2016-08-09 14:20 | 2016-08-30 14:25 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety | 2016-08-09 14:20 | 2017-06-23 12:35 | JWRAY | 2016-08-09 14:20 | Janice Wray
24314 | 269388 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17b | High | There appears to be no fire detector in the ground floor level area off the lift lobby area in front of the electrical intake room, there is a smoke vent in the ceiling of this area. | How is this smoke vent activated? CW to check with Rydons | Claire Williams | 2016-09-06 | Whole gf lift lobby is treated as one area for fire purposes. See strategy drawing attached. | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:25 | 2016-08-30 14:27 | CLWILLIAMS | [6 empty] | 2016-08-09 14:25 | 2016-08-17 15:38 | CLWILLIAMS | 2016-08-09 14:25 | 2016-08-30 14:27 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 14:25
24314 | 269389 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17c | High | There are fire detection devices installed in this building to activate the newly installed smoke extraction system. | Can the installation and commissioning certificate be provided for the installed fire detection devices? With CW It should be confirmed by a qualified fire alarm engineer that the installed fire detection devices are suitably sited and installed. | Janice Wray | 2016-09-06 | CW confirms that EXOVA fire strategy agreed with Building Control Commissionig Certificate dated March 2016 provided | 2016-12-09 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:28 | 2016-08-30 14:31 | JWRAY | [6 empty] | 2016-08-09 14:28 | 2017-06-16 15:52 | JWRAY | 2016-08-09 14:28 | 2016-08-30 14:31 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-09 14:28
24314 | 269391 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17d | High | It appears that the mains gas supply to this building is interfaced with the automatic opening ventilation system and shuts off if the AOV system operates, the lifts could also be interfaced. LIFTS NOT INTERFACED - CWiliams | I would strongly recommend that the gas supply system in this building is NOT interfaced with the AOV system. Can it be confirmed if any other system are interfaced with the AOV system? If so which systems? I would also say that no systems should be interfaced with the AOV systems. Claire - can you confirm that the gas supply if not interfaced with AOVs? | Claire Williams | 2016-09-06 | Specification to separate main smoke system from basement with gas boilers is in production, with works due to take place this financial year. ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | 2017-10-19 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:32 | 2016-08-30 14:40 | JWRAY | [6 empty] | 2016-08-09 14:32 | 2017-10-20 10:08 | JWRAY | 2016-08-09 14:32 | 2016-08-30 14:40 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 14:32
24314 | 269393 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17e | High | In some of the new dwellings the domestic fire detection systems are not fitted as per the requirements of BS5839 Part 6 2013. The installed devices are to LD3 standard in some flats, to LD 1 in others, some have 2 smoke detectors in the hallway a couple of meters apart others only one detector. Some dwellings have heat detectors installed in the kitchen areas other do not. | Within the new dwellings all domestic detection must be installed as per the requirements of BS 5839 Part 6 2013, this is a Building Regulations requirement. This is normally to LD2 standard, the same standard as the TMO have retrospectively fitted in all the original tenanted dwellings of this building. Why has a lesser standard of domestic fire detection been fitted in some of the newly constructed dwellings? Claire to check with EXOVA and Rydons | Claire Williams | 2016-09-06 | Rydon responded that the new flats have a lesser specification because of their size and their lower location in the building. We have the building regulations certification on the building - in the O&M manual. | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:41 | 2016-08-30 14:47 | CLWILLIAMS | [6 empty] | 2016-08-09 14:41 | 2016-08-17 15:49 | CLWILLIAMS | 2016-08-09 14:41 | 2016-08-30 14:47 | Claire Williams | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-09 14:41
24314 | 269394 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17f | High | At the roof level there is a coil of fire alarm cable not connected at one end to anything. | What is this coil of fire alarm cable for? Could Paul arrange for his to be removed please? | Nicola Bartholomew | 2016-09-06 | Order raised for Allied Protect to attend site with ESA, investigate and report back. To be raised with Rydons at Defects Inspection. (currently not connected) ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | 2017-10-19 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-09 14:47 | 2016-08-30 15:20 | JWRAY | [6 empty] | 2016-08-09 14:47 | 2017-10-20 10:09 | JWRAY | 2016-08-09 14:47 | 2016-08-30 15:20 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-09 14:47
24314 | 269423 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17g | High | BS 5839 Part 1 2013 fire alarm systems are being provided in the boxing club and children's nursery areas of this building. These are stand alone systems. | Will the TMO be required to monitor these systems? Who will be responsible for testing and servicing these systems? Will these fire systems be connected to or interfaced with any system in the TMO residential parts of this building? | Janice Wray | 2016-09-07 | No FA in Boxing Club - AOV only Nursery responsible for testign fire alarm in their area and ensuring any hirers are aware of procedure Grenfell FA linked to CAS / Tunstall Telecom | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:35 | 2016-08-31 09:36 | JWRAY | [6 empty] | 2016-08-10 09:35 | 2016-09-01 19:15 | JWRAY | 2016-08-10 09:35 | 2016-08-31 09:36 | Janice Wray | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 09:35
24314 | 269424 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 17h | High | There are 2 smoke detectors fitted on the 7th floor level ceiling, the 2nd detector is a different style of smoke detector to the newly installed one. This device is on the ceiling near to the flat entrance door of flat 46. The contractor does not know anything about this 2nd device. | What is the reason for the 2nd smoke detector fitted on the 7th floor level ceiling near to flat 46's entrance door? Could Paul investigate this please? | Nicola Bartholomew | 2016-09-07 | Confirmation that second "detector" is actiually a CCTV camera | 2016-12-09 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:37 | 2016-08-31 09:39 | JWRAY | [6 empty] | 2016-08-10 09:37 | 2016-12-12 12:28 | JWRAY | 2016-08-10 09:37 | 2016-08-31 09:39 | Janice Wray | Smoke Alarms | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-10 09:37
24314 | 269425 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19a | High | There are no operating instructions or as installed diagrams located next to the Automatic Opening Vents (AOV) control panel, how is this control panel accessed? | Provide operating instructions and as installed diagrams located next to the AOV control panel along with access information. Written instruction provided & diagram within Hub Room (keysafe in bin room) | Janice Wray | 2016-09-07 | Written instructions provided - diagram within Hub Room on site. (Hub room accessed via key stored in keysafe installed in bin room - accessed via FB14 key) | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:39 | 2016-08-31 09:41 | JWRAY | [6 empty] | 2016-08-10 09:39 | 2016-09-01 19:18 | JWRAY | 2016-08-10 09:39 | 2016-08-31 09:41 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 09:39
24314 | 269427 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19b | High | It is not known if training on the operating of the AOV system has been given to all TMO staff who requires it. | Provide training on the operating of the AOV system to all relevant TMO employees. | Janice Wray | 2016-09-07 | 2 sessions in familiarisation completed by Rydons. LFB also attended for familiarisation | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:41 | 2016-08-31 09:46 | JWRAY | [6 empty] | 2016-08-10 09:41 | 2016-09-01 19:20 | JWRAY | 2016-08-10 09:41 | 2016-08-31 09:46 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 09:41
24314 | 269432 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19c | High | The keys to operate the manually operated individual AOV over ride devices should be on site, they will be in the AOV control box, but there are no keys there at present and the system is in use. | The keys to manually operate the individual AOV over ride devices should be freely available for use by the fire service if needed. Keysafe location & arrangements | Janice Wray | 2016-09-07 | Keys stored in Keysafe located in bin room - accessed via FB key | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:47 | 2016-08-31 09:50 | JWRAY | [6 empty] | 2016-08-10 09:47 | 2016-09-01 19:22 | JWRAY | 2016-08-10 09:47 | 2016-08-31 09:50 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 09:47
24314 | 269439 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19d | High | There is an AOV in the area outside of the ground floor electrical room, how is this AOV activated as there is no smoke detector in this area? Please see item 17b above as well | Please provide details on how this AOV will activate? Cross reference with 17b | Janice Wray | 2016-09-07 | Whole gf lift lobby is treated as one area for fire purposes. See strategy drawing attached | 2016-11-15 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 09:53 | 2016-08-31 09:59 | JWRAY | [6 empty] | 2016-08-10 09:53 | 2017-06-16 10:56 | JWRAY | 2016-08-10 09:53 | 2016-08-31 09:59 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 09:53
24314 | 269441 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19e | High | The AOV system and the installed fire alarm systems in this building is remotely monitored. | What is the procedure and policy if the installed fire alarm or AOV systems in this building activate? | Claire Williams | 2016-09-07 | The alarms go to CAS, who: - tell estates services - whether in working hours or OOH - call the fire brigade 1 Indicators at gf panel show the fire brigade where alarm has been activated. Discussion with fire brigade over how they evidence they have been on site and resolved issue and reset system knowing all is safe. 2 Local estates services teams have been shown how to reset alarms once fire brigade have visited. 3 Residents been notified of stay put policy unless at risk. | 2016-08-16 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 10:06 | 2016-08-31 10:07 | CLWILLIAMS | [6 empty] | 2016-08-10 10:06 | 2016-08-17 15:53 | CLWILLIAMS | 2016-08-10 10:06 | 2016-08-31 10:07 | Claire Williams | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Project Management |  |  |  | 2016-08-10 10:06
24314 | 269444 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 19f | High | It is not known if the fire service controls for the lifts been moved back down to the street level? | Can it be confirmed that the fire service controls for the lifts been moved back down to the street level? If not then this must be undertaken immediately. | Janice Wray | 2016-09-07 | COMPLETED | 2016-12-09 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 10:08 | 2016-08-31 10:10 | JWRAY | [6 empty] | 2016-08-10 10:08 | 2016-12-12 12:29 | JWRAY | 2016-08-10 10:08 | 2016-08-31 10:10 | Janice Wray | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 10:08
24314 | 269445 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 22 | Information Only | When the boxing club and the children's nursery occupy their areas of this building they should be asked to undertake a fire risk assessment (FRA) for their area. | When the boxing club and the children's nursery occupy their areas of the building they should be asked for a copy of their FRAs and the significant findings. Any significant findings should then be co-ordinated with this document so that a full FRA for the building can be finalised, with and actions acted upon. Requirement in lease - RBKC Property Services | Janice Wray | 2017-02-08 | Confirmed this is a requirement of the lease in both cases | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | [9 empty] | 2016-08-10 10:11 | 2016-09-01 19:29 |  |  |  |  | Miscellaneous | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 10:11
24314 | 269446 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23a | High | In the roof level lift motor and plant rooms and in the basement boiler room there is BS 5839 Part 1 fire detection systems fitted. Where is the control panel(s) for these BS5839 Part 1 systems and who is undertaking the servicing etc of this systems? Keystone checked | Please can it be confirmed that testing and servicing of the installed BS 5839 Part 1 fire alarm systems installed in this building are being undertaken? If servicing and testing of the installed fire alarm systems is not being undertaken then these systems must be serviced and tested immediately with any defects rectified. Queried with Carl | Janice Wray | 2016-09-07 | ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | 2017-10-19 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 10:15 | 2016-08-31 10:17 | JWRAY | [6 empty] | 2016-08-10 10:15 | 2017-10-20 10:10 | JWRAY | 2016-08-10 10:15 | 2016-08-31 10:17 | Janice Wray | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 10:15
24314 | 269447 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23b | High | There are BS 5839 Part 1 fire detection systems fitted in this building, is weekly occupier testing of these systems being undertaken? | Weekly occupiers testing of the installed fire alarm systems must be undertaken and the results recorded as proof of testing. Weekly testing by Paul - training provided - please confirm | Nicola Bartholomew | 2016-09-07 | ESA (Paul Steadman) confirms fire alarm tested on weekly basis - Fridays at 10am | 2017-05-24 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 10:17 | 2016-08-31 10:19 | JWRAY | [6 empty] | 2016-08-10 10:17 | 2017-05-25 15:17 | JWRAY | 2016-08-10 10:17 | 2016-08-31 10:19 | Janice Wray | Fire Alarm | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-10 10:17
24314 | 269449 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23c | High | The lightning protection system installed on this building was last serviced/tested in September 2015. It does not state if the system passed or failed this test? Keystone checked. | Can it please be confirmed that the lightning protection system installed on this building passed its last service/test? If it did not any remedial work needed to make this buildings lightning protection system fully serviceable should be undertaken immediately. Docs to C Stokes | Janice Wray | 2016-09-07 | Certificate provided to assessor | 2016-08-31 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 10:19 | 2016-08-31 12:31 | JWRAY | [6 empty] | 2016-08-10 10:19 | 2016-09-01 19:31 | JWRAY | 2016-08-10 10:19 | 2016-08-31 12:31 | Janice Wray | Lightning Protection | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Health and Safety |  |  |  | 2016-08-10 10:19
24314 | 269482 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23d | High | There are emergency lighting units installed on the means of escape routes of this building plus in the roof level lift motor and plant rooms and in the basement area of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | Alex Bosman | 2016-09-07 | Last service carried out 17/1/17 | 2017-06-05 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 12:31 | 2016-08-31 16:47 | JWRAY | [6 empty] | 2016-08-10 12:31 | 2017-06-06 16:58 | JWRAY | 2016-08-10 12:31 | 2016-08-31 16:47 | Janice Wray | Emergency Lighting | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2016-08-10 12:31
24314 | 269520 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23e | High | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Nicola Bartholomew | 2016-09-07 | Confirmed | 2016-12-09 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 16:48 | 2016-08-31 16:49 | JWRAY | [6 empty] | 2016-08-10 16:48 | 2016-12-12 12:32 | JWRAY | 2016-08-10 16:48 | 2016-08-31 16:49 | Janice Wray | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-10 16:48
24314 | 269521 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23f | High | According to the contractors labels on the fire extinguishers in this building they are all out of test date. The last date on the contractors test/servicing labels is October 2014. | All of the fire extinguishers in this building should be tested/serviced immediately and any defective ones replaced. | Alex Bosman | 2016-09-07 | All serviced on 24th Oct 2016 | 2016-11-07 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 16:49 | 2016-08-31 16:50 | JWRAY | [6 empty] | 2016-08-10 16:49 | 2016-11-08 16:38 | JWRAY | 2016-08-10 16:49 | 2016-08-31 16:50 | Janice Wray | Fire Extinguisher | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | A & R Contract Management |  |  |  | 2016-08-10 16:49
24314 | 269522 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23g | High | Are the weekly occupier's tests of the buildings automatic smoke ventilation system being undertaken? | Weekly occupier inspections of the buildings smoke ventilation system should be undertaken, with the results recorded as proof of the inspections having been undertaken. Can you confirm that Paul is undertaking these please? | Nicola Bartholomew | 2016-09-07 | tested weekly on Fridays | 2017-03-13 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 16:51 | 2016-08-31 16:52 | JWRAY | [6 empty] | 2016-08-10 16:51 | 2017-03-14 17:12 | JWRAY | 2016-08-10 16:51 | 2016-08-31 16:52 | Janice Wray | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-10 16:51
24314 | 269524 | Completed | GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 23h | High | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. Can you confirm that Paul is undertaking these please? | Nicola Bartholomew | 2016-09-07 | Confirmed | 2016-12-09 | Level 3 Grenfell Tower, Grenfell Road, London W11 1Tq 2016.06.20 | 2016-08-10 16:52 | 2016-08-31 16:53 | JWRAY | [6 empty] | 2016-08-10 16:52 | 2016-12-12 12:30 | JWRAY | 2016-08-10 16:52 | 2016-08-31 16:53 | Janice Wray | Inspection Regime | GRENFELL TOWER GRENFELL ROAD | GRENFELL TOWER GRENFELL ROAD | S217008800001 | Neighbourhood Management |  |  |  | 2016-08-10 16:52