## Fire Risk Assessment by Team Us
Fire Risk Assessment by Team / User
Total: 743
Risk Assessment | Process Start Date | Prop ref | Block | Process No | Proc Status | Iitem no | Priority | Category | Risk | Action | Team | Who | Action Due Date | Action taken | Comp date | Full or partial | Reporting User | Feedback Start Date | Feedback Due Date | Closure Start Date | Closure Due Date | Date Difference | In Target | Return Stage Startdate | Return Stage Duedate | Return User
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:24 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184137 | Completed | 15 | High | Emergency Lighting | There are combined normal and emergency lighting units installed on the staircase landings of both staircases, apart from it appears at the 2nd floor level on both staircases. | Please can it be confirmed if the lighting units on the 2nd floor level staircase landings are also emergency lighting units? If they are not I would recommend that new combined normal and emergency lights are installed on these floor level landings of both staircases. | A & R Contract Management | Alex Bosman |  | Inspection complete confirmed no EL on 2nd floor landing to be included in upgrade programme. | 2015-12-14 | Fully Completed | Maria Ares | 2015-02-17 15:24 | 2015-03-10 15:25 | 2015-02-17 15:24 | 2015-12-15 10:11 | -21 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:27 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184139 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape routes of this building, on the staircase landings. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service completed 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-17 15:27 | 2015-03-10 15:28 | 2015-02-17 15:27 | 2015-12-02 09:59 | -21 | In target
1 BURNABY STREET - 2013.12.31 | 2013-12-31 14:12 | S217000510001 | BURNABY STREET (1) | 122148 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building, but none were fitted in flat A. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building and one given to the occupant of flat A. The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2004. | A & R Contract Management | Alex Bosman |  | Hard wired smoke & heat detectors fitted during PIR testing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-12-31 14:12 | 2014-06-29 14:13 | 2013-12-31 14:12 | 2014-04-23 16:36 | -180 | In target
1 CLYDESDALE ROAD - 2015.01.06 | 2015-01-12 11:06 | S217008380001 | CLYDESDALE ROAD (1) | 177691 | Completed | 1a | High | Electrical Wire Check | On the RGE contractor's label on the electrical supply board of this building it states that the last electrical 5 year electrical fixed wiring test of the buildings common parts electrical wiring was undertaken in 2013. There is no retest date given just the words "Work Required". | Can it be confirmed that the outstanding work indicated on the RGE contractor electrical label has been undertaken and the fixed electrical wiring has been retested. If it has not then I would recommend that the work indicated is progressed and the buildings common parts fixed electrical wiring retested. Once retested and the wiring is satisfactory, a new contractors label should be fixed to the electrical supply board giving the test and retest dates. This building should then be placed on a planned preventative maintenance schedule for fixed electrical wiring retesting. | A & R Contract Management | Alex Bosman |  | Completed during 14/15 program | 2015-08-07 | Fully Completed | Gillian Kennedy | 2015-01-12 11:06 | 2015-02-02 11:08 | 2015-01-12 11:06 | 2015-08-10 15:51 | -21 | In target
1 CLYDESDALE ROAD - 2015.01.06 | 2015-01-12 11:09 | S217008380001 | CLYDESDALE ROAD (1) | 177694 | Completed | 1b | Medium |  | The covers of some of the lighting units located in the common parts of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. Please also see item 15a below as some of the lights maybe combined emergency light units as well. | I would recommend that the covers of the lighting units located in the common parts of this building, on the staircases and the balconies are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. - could this be built into the contractor's next visit | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.The illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2015-01-12 11:09 | 2015-03-13 11:10 | 2015-01-12 11:09 | 2015-04-14 09:55 | -60 | In target
1 CLYDESDALE ROAD - 2015.01.06 | 2015-01-12 11:11 | S217008380001 | CLYDESDALE ROAD (1) | 177695 | Completed | 4 | High | Miscellaneous | The gas meter boxes for the individual flats gas meters are located on the wall outside the buildings main entrance door, on the right hand side. Two of gas meter boxes are damaged and any person can tamper with the gas valve located in the boxes. | I would recommend that the two damaged gas meter boxes are repaired or replaced. | A & R Contract Management | Alex Bosman |  | Job attended 18/11/15. replacement meter boxes installed | 2015-11-20 | Fully Completed | Maria Ares | 2015-01-12 11:11 | 2015-02-02 11:12 | 2015-01-12 11:11 | 2015-11-23 12:58 | -21 | In target
1 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 10:26 | S217001880001 | ELM PARK GARDENS (1) | 201020 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed and have been replaced with just pendant lights. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | New emergency lighting installed and certs supplied | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-11 10:26 | 2015-07-02 10:29 | 2015-06-11 10:26 | 2015-11-18 12:22 | -21 | In target
1 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 10:29 | S217001880001 | ELM PARK GARDENS (1) | 201021 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the basement level boiler/plant room is out of test date according to the contractors servicing label attached to it. The last test date according to the RGE service label was July 2013. | This portable fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service completed 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-11 10:29 | 2015-07-02 10:30 | 2015-06-11 10:29 | 2015-12-02 10:00 | -21 | In target
1 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 10:31 | S217001880001 | ELM PARK GARDENS (1) | 201024 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO MENTION OF EL ON KEYSTONE | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-11 10:31 | 2015-07-02 10:32 | 2015-06-11 10:31 | 2015-11-27 09:34 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:01 | S217009580001 | NURSERY LANE (1) | 142316 | Completed | 1a | High | Miscellaneous | It is not known if the washing machines and tumble dryers in the laundry are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | serviced all laundry equipment 02/12/15 | 2015-12-14 | Fully Completed | Maria Ares | 2014-05-06 13:01 | 2014-05-27 13:04 | 2014-05-06 13:01 | 2015-12-15 10:12 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:07 | S217009580001 | NURSERY LANE (1) | 142317 | Completed | 1b | High | Miscellaneous | The CCTV recorder and other portable electrical items located in the ground floor level electrical room are out of date for Portable electrical Appliance Testing (PAT). | These portable electrical items located in the ground floor level electrical room should be PAT by a suitably qualified person and portable appliance test labels attached to each item if it passes the test. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-17 | Fully Completed | Alex Bosman | 2014-05-06 13:07 | 2014-05-27 13:08 | 2014-05-06 13:07 | 2015-02-18 15:45 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:09 | S217009580001 | NURSERY LANE (1) | 142318 | Completed | 1c | Medium | Miscellaneous | Some of the covers of the internal and external lighting units in this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the dirty covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels especially in the staircases. | A & R Contract Management | Alex Bosman |  | Complete | 2015-08-07 | Fully Completed | Gillian Kennedy | 2014-05-06 13:09 | 2014-07-05 13:10 | 2014-05-06 13:09 | 2015-08-10 15:56 | -60 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:11 | S217009580001 | NURSERY LANE (1) | 142319 | Completed | 5 | High | Standby Generator | This building has a stand by diesel generator in it. I have been told that this stand by diesel generator is now no longer being used, if this is correct please see the next column. According to the information held on site this generator has not been serviced since the 6th December 2013. | Please can it be confirmed that the stand by diesel generator in this building is now not being used ? If this is the case can the following also please be confirmed. 1. That the generator has been disconnected from all the electrical circuits that it use to backed up? 2. Have all the electrical circuits been correctly isolated? 3. Have the backed up circuits been checked to see that they are now compliant? Ie the emergency lighting units, lift etc, if not this check should be undertaken immediately. 4. Has all the diesel fuel been drained from the generator and any stand by tanks? 5. I would recommend that a large sign is placed on the generator stating that it is not now in use. If the generator has not been taken out of use it should be serviced and run immediately and all the electrical circuits that it backs up checked to see that they work correctly. Monthly running under load, servicing and maintenance should be undertaken in accordance with the manufactures recommendations. | A & R Contract Management | Alex Bosman |  | Confirmed that standby genorators are no longer required as all systems have battery back up. Genorators to be removed 2015/16 | 2015-02-19 | Fully Completed | Gillian Kennedy | 2014-05-06 13:11 | 2014-05-27 13:13 | 2014-05-06 13:11 | 2015-02-20 12:45 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:13 | S217009580001 | NURSERY LANE (1) | 142321 | Completed | 14 | High | Responsive Item | There are holes in the wall lining of the wall between the lift motor room and the cupboard next to it where cables have been passed through the wall by contractors and the holes have not been filled afterwards. | These holes in the wall linings should be filled in with a suitable fire rated material or new blocks to maintain the fire rating of the structure of the building. | A & R Contract Management | Alex Bosman | 2016-07-15 |  | 2015-11-29 | Fully Completed | Janice Wray | 2014-05-06 13:13 | 2014-05-27 13:15 | 2014-05-06 13:13 | 2016-01-19 16:07 | -21 | In target | 2014-05-06 13:13 | 2016-01-25 16:06 | Janice Wray
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:16 | S217009580001 | NURSERY LANE (1) | 142323 | Completed | 15 | High | Emergency Lighting | It appears that the stand by generator is now not in use, all of the emergency lighting units in this building should now be self contained units. | Please can it be confirmed that all of the emergency lighting units in this building are self contained ones and not backed up by the stand by generator as it appears that the generator is now not in use. If it is found that any emergency lighting units are not self contained ones then they must be changed immediately for self contained ones if the stand by generator is now not in use. | A & R Contract Management | Alex Bosman |  | It has been confirmed that the generator is no longer in use. | 2015-08-07 | Fully Completed | Gillian Kennedy | 2014-05-06 13:16 | 2014-05-27 13:17 | 2014-05-06 13:16 | 2015-08-10 15:59 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:19 | S217009580001 | NURSERY LANE (1) | 142325 | Completed | 17a | High | Fire Alarm | There is a heat detector located in the first floor corridor between flats 24 and 25. | Can the fire alarm company be asked why there is a heat detector in the first floor corridor between flats 24 and 25? There are normally smoke detectors located in the means of escape routes of a building. There are open louvered vents in the ceiling all along the 1st floor level corridor with smoke detectors near to them. If there is a reason for this device being a heat detector this is not documented in the buildings fire alarm logbook and it should be. | A & R Contract Management | Alex Bosman |  | AP inspected 18.11.2015 - The most probable reason is that the smoke detector was causing false alarms due to the high air flow through this particular vent. | 2015-11-26 | Fully Completed | Maria Ares | 2014-05-06 13:19 | 2014-05-27 13:23 | 2014-05-06 13:19 | 2015-11-27 09:37 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:24 | S217009580001 | NURSERY LANE (1) | 142327 | Completed | 17b | High | Smoke Alarms | In kitchen is smoke detector as well as a heat detector, the smoke detector was previously in the store room but the dividing wall has now been removed. If cooking is undertaken in this kitchen then this smoke detector which is located near to the cooker will activate. | I would recommend that the smoke detector presently located in the kitchen is swooped to a heat detector to reduce false activations of the buildings fire alarm system. | A & R Contract Management | Alex Bosman |  | Replaced Kitchen smoke alarm for heat alarm in the kitchen. All works Complete | 2015-11-20 | Fully Completed | Maria Ares | 2014-05-06 13:24 | 2014-05-27 13:25 | 2014-05-06 13:24 | 2015-11-23 13:00 | -21 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:29 | S217009580001 | NURSERY LANE (1) | 142331 | Completed | 17d | Medium | Smoke Alarms | On the 1st floor level near to the lift the smoke detectors are wall mounted. | I would recommend that the fire alarm maintenance company are asked why there are wall mounted smoke detectors in this area. Any advice then give by them should be acted upon. | A & R Contract Management | Alex Bosman |  | Complete. The smoke detectors are wall mounted due to Asbestos artex. | 2015-08-07 | Fully Completed | Gillian Kennedy | 2014-05-06 13:29 | 2014-07-05 13:30 | 2014-05-06 13:29 | 2015-08-10 16:01 | -60 | In target
1 NURSERY LANE - 2014.04.07 | 2014-05-06 13:30 | S217009580001 | NURSERY LANE (1) | 142332 | Completed | 23 | High | Fire Alarm | The fire alarm system in this building extends into the private flats. | Can it please be confirmed by the TMO electrical engineer and the fire alarm maintenance company that the devices of the fire alarm system installed in the private flats/dwellings are all being serviced and maintained at the same time as the devices in the common parts of the building? | A & R Contract Management | Alex Bosman |  | complete 06.08.2015 | 2015-11-19 | Fully Completed | Maria Ares | 2014-05-06 13:30 | 2014-05-27 13:31 | 2014-05-06 13:30 | 2015-11-20 10:08 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 11:11 | S217007560001 | PEMBRIDGE SQUARE (1) | 136599 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircase and the corridors etc of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Confirmed on asset list completed by Allied Protection on 12/08/2015. | 2015-08-12 | Fully Completed | Gillian Kennedy | 2014-03-26 11:11 | 2014-04-16 11:13 | 2014-03-26 11:11 | 2015-08-25 14:53 | -21 | In target
1 ST HELENS GARDENS - 2014.03.06 | 2014-03-13 13:27 | S217010100001 | ST HELENS GARDENS (1) | 134458 | Completed | 1 | High | Electrical Wire Check | Flat B is presently empty and has been so now for approximately 18 months. | I would recommend that when flat B is brought back into occupancy the electrical wiring is checked out completely and that new automatic fire detection in fitted within this flat. | A & R Contract Management | Alex Bosman |  | Works completed as part of void works | 2014-04-22 | Fully Completed | Alex Bosman | 2014-03-13 13:27 | 2014-04-03 13:27 | 2014-03-13 13:27 | 2014-04-23 16:37 | -21 | In target
1 ST HELENS GARDENS - 2014.03.06 | 2014-03-13 13:28 | S217010100001 | ST HELENS GARDENS (1) | 134459 | Completed | 12 | High | Flat Door | Flat B is presently empty and has been so now for approximately 18 months. | I would recommend that when flat B is brought back into occupancy that a new 30 minute self closing fire rated door is fitted as this flats entrance door. | A & R Contract Management | Alex Bosman |  | Property is currently being held for possible disposal. If KCTMO retain management then action to carried out. | 2015-10-28 | Fully Completed | Gillian Kennedy | 2014-03-13 13:28 | 2014-04-03 13:29 | 2014-03-13 13:28 | 2015-10-29 15:08 | -21 | In target
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 12:05 | S217007860001 | GOLBORNE GARDENS 1-10 | 182828 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the landings of the staircase, in the entrance hall area, on the 2nd floor level external balcony and the electrical room of this building these do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting units/system being serviced, tested and maintained, including a discharge test being undertaken? | Can it please be confirmed that the installed emergency lighting system in this building is being serviced, tested and a discharge test of the units batteries is being undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Confirmed on asset list completed by Allied Protection on 14/07/2015 | 2015-07-14 | Fully Completed | Gillian Kennedy | 2015-02-10 12:05 | 2015-03-03 12:06 | 2015-02-10 12:05 | 2015-08-25 14:54 | -21 | In target
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 12:13 | S217007860001 | GOLBORNE GARDENS 1-10 | 182834 | Completed | 23c | High | Fire Extinguisher | The water fire extinguisher located in the bulk store room, to the right hand side of the buildings entrance door is out of test date according to the RGE contractors servicing label attached to it. The last test date on this service label was July 2013. | This water fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 19.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-02-10 12:13 | 2015-03-03 12:14 | 2015-02-10 12:13 | 2015-11-27 09:38 | -21 | In target
10 ARUNDEL GARDENS LONDON - 2015 .05.11 | 2015-05-16 08:36 | S217007990002 | ARUNDEL GARDENS (10) | 197383 | Completed | 15 | High |  | There is presently no emergency escape lighting installed in this building, on the staircase landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. | I would recommend that emergency lighting units are installed on the landings of the staircase and in the entrance lobby area as soon as possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not then within budget year 16/17. Action entered into a programme of works | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-16 08:36 | 2015-06-06 08:38 | 2015-05-16 08:36 | 2015-11-23 14:47 | -21 | In target | 2015-05-16 08:36 | 2015-11-29 14:47 | Janice Wray
10 ARUNDEL GARDENS LONDON - 2015 .05.11 | 2015-05-16 08:39 | S217007990002 | ARUNDEL GARDENS (10) | 197384 | Completed | 17a | High | Fire Alarm | There have been electrically powered/operated domestic hardwired interlinked detectors installed in the 1st floor level flat of this building. There is a smoke detector/sounder installed in the hallway and a heat detector/sounder in the kitchen area. But this heat detector/sounder is wall mounted between 1 and 2 meters below the ceiling. This wall mounted detector does not appear to conform to the requirements of BS 5839 Part 6 2013. | I would recommend that the premises file is checked to see if the installation/ completion certificate as required by BS 5839 Part 6 :2013 is located there. If it is not the contactor who installed the domestic heat detector/sounder on the kitchen wall of this flat should be asked for it/them and to explain why the detector is so positioned. The certificate(s) should be as the model standard ones in the British Standard document. | A & R Contract Management | Alex Bosman |  | Confirmed installed correctly to BS | 2015-12-01 | Fully Completed | Maria Ares | 2015-05-16 08:39 | 2015-06-06 08:41 | 2015-05-16 08:39 | 2015-12-02 10:01 | -21 | In target
10 ARUNDEL GARDENS LONDON - 2015 .05.11 | 2015-05-16 08:41 | S217007990002 | ARUNDEL GARDENS (10) | 197385 | Completed | 17b | High | Fire Alarm | Other flats within this building that have had electrically powered/operated domestic hardwired interlinked detectors installed within them. | I would recommend that all of the dwellings in this building are checked to see that the installation of any new domestic detectors conforms to the requirements of BS 5839 Part 6 2013. Also that there is an installation/ completion certificate as required by BS 5839 Part 6 :2013 for each individual dwelling. If it is not the contactor who installed the domestic detectors/sounders within these flats should be asked for them immediately. | A & R Contract Management | Alex Bosman |  | complete - previously confirmed hard wired heat and smoke detectors are installed during PIR programme currently at 94% | 2015-11-17 | Fully Completed | Maria Ares | 2015-05-16 08:41 | 2015-06-06 08:42 | 2015-05-16 08:41 | 2015-11-18 12:33 | -21 | In target
10 ASHBURNHAM ROAD - 2013.09.30 | 2013-10-10 15:38 | S217000190004 | ASHBURNHAM ROAD (10) | 110164 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flats A or B of this building, a detector /sounder is fitted within flat C. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat without detectors in accordance with the requirements of BS 5839 Part 6. | A & R Contract Management | Alex Bosman |  | Hard wired heat & smoke detectors to be fitted during PIR testing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-10-10 15:38 | 2014-04-08 15:42 | 2013-10-10 15:38 | 2014-04-23 16:38 | -180 | In target
10 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 11:22 | S217001880012 | ELM PARK GARDENS (10) | 200419 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed. It appears that the installed emergency lighting system in this building is not in full working order. The neon battery charging lights are not working on some the individual emergency lighting units and when tested some of the EL units did not work | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-08 11:22 | 2015-06-29 11:23 | 2015-06-08 11:22 | 2015-11-27 09:40 | -21 | In target
10 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 11:24 | S217001880012 | ELM PARK GARDENS (10) | 200421 | Completed | 23a | High | Fire Extinguisher | =The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-08 11:24 | 2015-06-29 11:25 | 2015-06-08 11:24 | 2015-12-02 10:03 | -21 | In target
10 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 11:25 | S217001880012 | ELM PARK GARDENS (10) | 200424 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting unit/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO INFO ON KEYSTONE | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-08 11:25 | 2015-06-29 11:26 | 2015-06-08 11:25 | 2015-11-27 09:41 | -21 | In target
104 ELM PARK GARDENS - 2015-06.15 | 2015-06-29 11:09 | S217001880034 | ELM PARK GARDENS (104) | 203772 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But the old emergency lighting units are still installed in the lift motor room. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and roof space area were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | Lighting present and functioning correctly | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-29 11:09 | 2015-07-20 11:10 | 2015-06-29 11:09 | 2015-11-18 12:34 | -21 | In target
104 ELM PARK GARDENS - 2015-06.15 | 2015-06-29 11:11 | S217001880034 | ELM PARK GARDENS (104) | 203776 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | certificates supplied | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-29 11:11 | 2015-07-20 11:11 | 2015-06-29 11:11 | 2015-11-18 12:35 | -21 | In target
104 ELM PARK GARDENS - 2015-06.15 | 2015-06-29 11:12 | S217001880034 | ELM PARK GARDENS (104) | 203777 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-29 11:12 | 2015-07-20 11:24 | 2015-06-29 11:12 | 2015-12-02 10:04 | -21 | In target
104 ELM PARK GARDENS - 2015-06.15 | 2015-06-29 11:25 | S217001880034 | ELM PARK GARDENS (104) | 203782 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-29 11:25 | 2015-07-20 11:26 | 2015-06-29 11:25 | 2015-11-27 09:42 | -21 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:06 | S217009620002 | OXFORD GARDENS (109) | 197395 | Completed | 15 | High | Emergency Lighting | As soon as possible There is presently no emergency escape lighting installed in this building, on the staircase, the landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. | I would recommend that emergency lighting units are installed on the landings of the staircase and in the entrance lobby area as soon as possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not then within budget year 16/17. Action entered into a programme of works. | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-16 09:06 | 2015-06-06 09:08 | 2015-05-16 09:06 | 2015-11-23 14:50 | -21 | In target | 2015-05-16 09:06 | 2015-11-29 14:50 | Janice Wray
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:08 | S217009620002 | OXFORD GARDENS (109) | 197396 | Completed | 17a | High | Smoke Alarms | There has recently been, in the last few weeks, electrically powered/operated domestic hardwired interlinked detectors installed in flat 2 of this building. But both the smoke and heat detectors are in the same area/room and there is no detector in the hallway area. This installation does not appear to conform to the requirements of BS 5839 Part 6 2013. | I would recommend that the premises file is checked to see if the installation/ completion certificate as required by BS 5839 Part 6 :2013 is located there. If it is not the contactor who installed the domestic detectors/sounders within this flat should be asked for it/them and to explain why the detectors are so positioned. The certificates should be as the model standard ones in the British Standard document. | A & R Contract Management | Alex Bosman |  | alarm system FULLY COMMISIONED AND COMPLIANT | 2015-11-17 | Fully Completed | Maria Ares | 2015-05-16 09:08 | 2015-06-06 09:09 | 2015-05-16 09:08 | 2015-11-18 12:36 | -21 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 09:10 | S217009620002 | OXFORD GARDENS (109) | 197397 | Completed | 17b | High | Smoke Alarms | Other flats within this building that have had electrically powered/operated domestic hardwired interlinked detectors installed within them. | I would recommend that all of the dwellings in this building are checked to see that the installation of any new domestic detectors conforms to the requirements of BS 5839 Part 6 2013. Also that there is an installation/ completion certificate as required by BS 5839 Part 6 :2013 for each individual dwelling. If it is not the contactor who installed the domestic detectors/sounders within these flats should be asked for them immediately. | A & R Contract Management | Alex Bosman |  | Completed as part of PIR programme. | 2015-08-07 | Fully Completed | Gillian Kennedy | 2015-05-16 09:10 | 2015-06-06 09:11 | 2015-05-16 09:10 | 2015-08-10 16:02 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:14 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201704 | Completed | 1 | High | Electrical Wire Check | According to the electrical contractor's label on the landlords electrical supply/ distribution board the last fixed electrical wiring test of the common parts electrical wiring in this buildings was undertaken on the 24th November 2008. It was due for retesting in November 2013. | Can it be confirmed with the TMO electrical engineer if the fixed wiring in the building has been retested since November 2013. If it has not been retested then I would recommend that a fixed wiring test is undertaken on the common parts electrical wiring immediately with any defects identified rectified and the buildings fixed electrical wiring then put on the planned preventative maintenance schedule for retesting. KEYSTONE - wiring test completed 12/6/15 - no certificate yet | A & R Contract Management | Alex Bosman |  | 02.02.15 - Completed Certificate in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-16 10:14 | 2015-07-07 10:16 | 2015-06-16 10:14 | 2015-08-25 16:05 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:17 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201706 | Completed | 5 | High | Lifts | There did not appear to be a lift record service book in the lift motor room of this building. It is not known when the lift was last serviced etc. | Can it please be confirmed with the lift maintenance company that this lift is being serviced, tested and maintained and these service visits are up to date? If there is not a lift record service book in this lift motor room then I would recommend that one is provided and the service visits recorded. | A & R Contract Management | Alex Bosman |  | Lift H42 included on monthly servicing contract . Servicing monitored by TAT. | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-16 10:17 | 2015-07-07 10:18 | 2015-06-16 10:17 | 2015-08-25 16:06 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:32 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201711 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But the old emergency lighting units are still installed in the lift motor. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and roof space area were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? KEYSTONE - No reference to EL | A & R Contract Management | Alex Bosman |  | Lighting present and functioning correctly | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-16 10:32 | 2015-07-07 10:34 | 2015-06-16 10:32 | 2015-11-18 12:37 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:34 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201712 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. KEYSTONE - No reference to EL | A & R Contract Management | Alex Bosman |  | certificates supplied | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-16 10:34 | 2015-07-07 10:35 | 2015-06-16 10:34 | 2015-11-18 12:38 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:36 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201713 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-01-13 | AP confirmed complete 4.12.2015 | 2016-01-13 | Fully Completed | Maria Ares | 2015-06-16 10:36 | 2015-07-07 10:37 | 2015-06-16 10:36 | 2016-01-14 15:26 | -21 | In target
110 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:37 | S217001880035 | ELM PARK GARDENS 110 (1-9) | 201714 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? KEYSTONE - No reference to EL | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-16 10:37 | 2015-07-07 10:38 | 2015-06-16 10:37 | 2015-12-15 10:15 | -21 | In target
110 LANCASTER ROAD - 2014.01.09 | 2014-01-09 14:49 | S217009210004 | LANCASTER ROAD (110) | 123455 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last electrical fixed wiring test was carried out in this building. On a flat's supply board there is a last test date of 1993 indicated. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this building was last tested. If the fixed wiring in this building is overdue for testing then it should be retested with any defects identified, rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-04-22 | Fully Completed | Alex Bosman | 2014-01-09 14:49 | 2014-01-30 14:50 | 2014-01-09 14:49 | 2014-04-23 16:39 | -21 | In target
110 LANCASTER ROAD - 2014.01.09 | 2014-01-09 14:50 | S217009210004 | LANCASTER ROAD (110) | 123456 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building, but none were fitted within flat C. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building and one given to the occupant of flat C. The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2004. | A & R Contract Management | Alex Bosman |  | Hard wired heat & smoke detectors to be fitted during PIR testing | 2014-04-22 | Fully Completed | Alex Bosman | 2014-01-09 14:50 | 2014-07-08 14:51 | 2014-01-09 14:50 | 2014-04-23 16:39 | -180 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 11:58 | S217009467707 | MORGAN ROAD ODD (1-11) | 102445 | Completed | 15 | Medium | Emergency Lighting | It is not known if any emergency lighting is installed on the landings of the staircase, ie the common parts of this building. The TMO electrical and contractors asset list says that there is an emergency lighting system installed by I could not seen any neon indicator/charging lights on the installed lighting units. There is defiantly a self contained emergency lighting unit in the electrical room. | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units. If it is found that there are emergency lighting units installed within the staircase of this building these should be tested and serviced immediately with a discharge test carried out. Any defects and/or problems highlighted as a result of this testing and servicing should be rectified. If it is found that none of the lighting units on the staircase are emergency lighting units then some should be installed as there are no windows to allow borrowed light into the staircase. Any installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman | 2013-09-16 | Inspected all necessary works now completed | 2015-12-01 | Fully Completed | Maria Ares | 2013-08-19 11:58 | 2013-10-18 12:01 | 2013-08-19 11:58 | 2015-12-02 14:41 | -60 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 12:02 | S217009467707 | MORGAN ROAD ODD (1-11) | 102447 | Completed | 17 | Low | Smoke Alarms | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Automatic domestic detection was not fitted within flat number 7. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman | 2014-02-03 | Properties included in 10 year PIR program which includes the instillation of hardwired fire alarms | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 12:02 | 2014-02-15 12:06 | 2013-08-19 12:02 | 2013-10-02 17:01 | -180 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 12:09 | S217009467707 | MORGAN ROAD ODD (1-11) | 102450 | Completed | 23b | Medium | Emergency Lighting | It is not known if there is an emergency lighting system installed within the staircase of this building, please see item 15 above. But there is definitely an emergency lighting unit in the electrical room. | Monthly occupiers testing and inspections of the emergency lighting system installed in this building then should be undertaken by the caretaker with the results recorded as proof of testing having been undertaken. If it is found that the lighting units on the staircase landings are combined emergency lighting units testing of these should also be undertaken. The system should also be added to the contractor's maintenance schedule so that planned preventive maintenance and servicing is undertaken. | A & R Contract Management | Alex Bosman | 2013-09-16 | Is this property on the current ppm contract? Confirmed EL present to be reffered to caretaking | 2016-01-13 | Fully Completed | Maria Ares | 2013-08-19 12:09 | 2013-10-18 12:23 | 2013-08-19 12:09 | 2016-01-14 15:28 | -60 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 10:53 | S217009467707 | MORGAN ROAD ODD (1-11) | 102420 | Completed | 1a | High | Electrical Wire Check | There is no contractors label on the supply board or any other records to indicate when the last 5 year electrical fixed wiring test of this building. | Can it be confirmed by the TMO electrical engineer when the last 5 year electrical fixed wiring test of this building was undertaken? If it is overdue for testing I would recommend that a test is undertaken and any defects rectified or repaired as soon as possible. | A & R Contract Management | Alex Bosman | 2013-09-09 | Block included in 13/14 block testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 10:53 | 2013-09-09 10:55 | 2013-08-19 10:53 | 2015-11-27 13:06 | -21 | In target | 2013-08-19 10:53 | 2015-12-03 10:47 | Janice Wray
1-11 MORGAN ROAD, (ODD NUMBERS ONLY) LONDON W10 5YT - 2016.03.04 | 2016-03-21 15:28 | S217009467707 | MORGAN ROAD ODD (1-11) | 250262 | Active | 15 | High | Emergency Lighting | No neon indicator/charging lights could be seen on the light units on the staircase landings of this building, there is an emergency light installed in the electrical room with a glowing indicator light. So it is not known if any emergency lighting is installed on the landings of the staircase, ie the common parts of this building. The W2 sheet states that "Inspected all necessary works now completed" with an action due date of 16/9/13 and the completion date was 1/12/15. So are emergency lights are installed within this building? no new light units have recently been installed. If there are emergency lights installed and as no neon indicator/charging lights cannot be seen I can only assume that the emergency lights are not being charged. | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units and why the neon indicator/charging lights cannot be seen on the light units. Is the installed emergency lighting system to the standard and requirements of British Standard 5266 Part 1 2011, as there are no windows to allow borrowed light into the staircase. If it is not, then emergency lighting units should be installed to the standard as indicated above. | A & R Contract Management | Alex Bosman | 2016-04-18
1-11 MORGAN ROAD, (ODD NUMBERS ONLY) LONDON W10 5YT - 2016.03.04 | 2016-03-21 15:30 | S217009467707 | MORGAN ROAD ODD (1-11) | 250263 | Active | 23a | High | Emergency Lighting | There is an emergency escape lighting units installed in this building, in the electrical room, there may be units on the staircase landings as well. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-04-18
11-18 GOLBORNE GARDENS - 2015.02.05 | 2015-02-10 12:27 | S217008850002 | GOLBORNE GARDENS 11-18 | 182839 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the landings of the staircase, in the entrance hall area and the electrical room of this building these do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting units/system being serviced, tested and maintained, including a discharge test being undertaken? | Can it please be confirmed that the installed emergency lighting system in this building is being serviced, tested and a discharge test of the units batteries is being undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | EL TEST COMPLETED ON 14/07/15 | 2015-11-17 | Fully Completed | Maria Ares | 2015-02-10 12:27 | 2015-03-03 12:28 | 2015-02-10 12:27 | 2015-11-18 12:41 | -21 | In target
1-17 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:24 | S217010500001 | WAYNFLETE SQUARE 2-11 | 215977 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/systems installed in each part/section of this building, on the landings of the staircases, in each of the entrance hall areas and in the electrical rooms/cupboards. The means of escape routes. | Can it please be confirmed when the installed emergency lighting systems in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago then these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 18.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-09-10 15:24 | 2015-10-01 15:25 | 2015-09-10 15:24 | 2015-11-27 09:43 | -21 | In target
1-18 DARTREY WALK - 2014.3.12 | 2014-04-10 15:39 | S217012740004 | DARTREY WALK 1-18 | 139371 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of the common parts of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test for these areas of the Worlds End Estate would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in these areas of the estate are in test date. If they are not, a fixed wiring test should be undertaken with any defects identified rectified and the areas of this building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-10 15:39 | 2014-05-01 15:40 | 2014-04-10 15:39 | 2014-05-13 16:55 | -21 | In target
12 CAMBRIDGE GARDENS - 2015.11.11 | 2015-11-16 12:15 | S217008280001 | CAMBRIDGE GARDENS (12) | 227852 | Completed | 23 | High | Emergency Lighting | There are emergency lighting units/system installed in this building, in the entrance hall area, on the landings of the staircase and at the base of the staircase. Keystone has been checked. | Can it please be confirmed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-11-16 12:15 | 2015-12-07 12:16 | 2015-11-16 12:15 | 2015-12-15 10:16 | -21 | In target
12 RUSSELL GARDENS - 2014.6.11 | 2014-06-30 15:51 | S217006670002 | RUSSELL GARDENS (12) | 151049 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flat A, but none were fitted within flat B. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building and one given to the occupant of flat B. The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | Hard wired detectors to be installed during PIR testing program | 2015-03-23 | Fully Completed | Alex Bosman | 2014-06-30 15:51 | 2014-12-27 15:52 | 2014-06-30 15:51 | 2015-03-24 16:57 | -180 | In target
123 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:37 | S217002110005 | FINBOROUGH ROAD 123 A-H | 194202 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase landings, in the entrance hall/lobby area and also a unit in the electrical cupboard/room under the staircase. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection on 23/07/2015 | 2015-07-23 | Fully Completed | Gillian Kennedy | 2015-04-27 09:37 | 2015-05-18 09:38 | 2015-04-27 09:37 | 2015-08-25 14:56 | -21 | In target
1-26 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 08:54 | S217000830003 | CHELSEA MANOR COURT 1-26 | 207288 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency escape lighting installed in this building on the 2nd floor level external walkway/balcony or on the staircase landings. | I would recommend that if any work is undertaken on the lighting units within this building on the means of escape routes then consideration is given to fitting emergency escape lighting. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not then within budget year 16/17. Action entered into a porgramme of works | 2015-11-19 | Fully Completed |  |  |  | 2015-07-17 08:54 | 2015-11-23 16:22 |  |  | 2015-07-17 08:54 | 2015-11-29 16:21 | Janice Wray
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:36 | S217012740001 | BERENGER WALK 1-28 | 139334 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test for these areas of the Worlds End Estate would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in these areas of the estate are in test date. If they are not, a fixed wiring test should be undertaken with any defects identified rectified and the areas of this building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-10 14:36 | 2014-05-01 14:38 | 2014-04-10 14:36 | 2014-05-13 16:56 | -21 | In target
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:36 | S217009210005 | LANCASTER ROAD (130) | 102678 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed in this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. This could be by the TMO or by RBKC. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | To be added to asset register and included in contract procurment | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-19 16:36 | 2013-09-09 16:38 | 2013-08-19 16:36 | 2014-03-21 16:44 | -21 | In target
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:38 | S217009210005 | LANCASTER ROAD (130) | 102681 | Completed | 23b | High | Fire Alarm | Testing and inspections of the installed fire alarm system, is the installed fire alarm system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the fire alarm contractor are asked if the installed fire alarm system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of devices etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Confirmed fire alarm on service contract last serviced 6.11.2013 | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-19 16:38 | 2013-09-09 16:39 | 2013-08-19 16:38 | 2013-12-10 17:22 | -21 | In target
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:40 | S217009210005 | LANCASTER ROAD (130) | 102682 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-19 16:40 | 2013-09-09 16:41 | 2013-08-19 16:40 | 2015-02-27 12:10 | -21 | In target
14 COLVILLE SQUARE 2014.02.06 | 2014-03-07 10:41 | S217008450003 | COLVILLE SQUARE (14) | 133521 | Completed | 23a | High | Emergency Lighting | There is an emergency escape lighting system/units installed in the staircase enclosure and in the ground floor electrical room of this building these items do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contactor or the TMO electrical engineer is asked if the installed emergency lighting system/units in this building are being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing and testing. | A & R Contract Management | Alex Bosman |  | Added to asset register to be included in service contract | 2014-05-12 | Fully Completed | Alex Bosman | 2014-03-07 10:41 | 2014-03-28 10:42 | 2014-03-07 10:41 | 2014-05-13 17:00 | -21 | In target
140 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:58 | S217002110014 | FINBOROUGH ROAD (140) | 194213 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed in this building, on the landings of the staircase or in the entrance hall area ie the common parts of this building. The common parts of this building are five floors levels. | I would recommend that emergency lighting units are installed in the common parts ie the staircase enclosure of this building to provide illumination of the means of escape routes if the normal lighting fails. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not then within budget year 16/17. Action entered into a programme of works | 2015-11-19 | Fully Completed |  |  |  | 2015-04-27 09:58 | 2015-11-23 14:45 |  |  | 2015-04-27 09:58 | 2015-11-29 14:45 | Janice Wray
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:17 | S217012040001 | LEXHAM GARDENS (140) | 102661 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Automatic domestic detection was fitted within flat 10. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | Instillation of hard wired detectors included in electrical testing spec remidials | 2014-03-20 | Fully Completed |  |  |  | 2013-08-19 16:17 | 2014-03-24 13:12 |  |  | 2013-08-19 16:17 | 2014-03-28 13:12 | Janice Wray
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:19 | S217012040001 | LEXHAM GARDENS (140) | 102663 | Completed | 23a | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-19 16:19 | 2013-09-09 16:20 | 2013-08-19 16:19 | 2015-02-27 12:13 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:30 | S217012040001 | LEXHAM GARDENS (140) | 102505 | Completed | 1 | High | Emergency Lighting | The covers of the lighting units in the common parts of the building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircase. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.The illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-19 13:30 | 2013-09-09 13:38 | 2013-08-19 13:30 | 2015-04-14 09:55 | -21 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:16 | S217012740003 | UPPER BERENGER WALK 1-42 | 139405 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test for these areas of the Worlds End Estate would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in these areas of the estate are in test date. If they are not, a fixed wiring test should be undertaken with any defects identified rectified and the areas of this building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Included in 14/15 communal testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-10 16:16 | 2014-05-01 16:17 | 2014-04-10 16:16 | 2014-05-13 17:01 | -21 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:47 | S217012740003 | UPPER BERENGER WALK 1-42 | 139421 | Completed | 23a | High | Lightning Protection | There are lightning protection systems installed on the roofs of these walkways, these systems do not appear on the asset list as supplied by the TMO engineer. Are these installed lightning protection systems being serviced, tested and maintained. | I would recommend that the TMO engineer is asked if the installed lightning protection systems on the roofs of these walkways are being serviced, tested and maintained. The individual tower blocks are listed but not these walkways. If these lightning protection systems are not being testing and servicing then a service etc should be undertaken immediately and any defects found rectified and then the systems placed on the contractor's maintenance schedule for future servicing. If these systems are being serviced etc then no action is needed but I would recommend that the asset list is up dated. Alex | A & R Contract Management | Alex Bosman |  | Added to asset register for inclusion in on going testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-10 16:47 | 2014-05-01 16:48 | 2014-04-10 16:47 | 2014-05-13 17:02 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:07 | S217010567701 | LONGLANDS COURT (1-48) | 103169 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 16:07 | 2013-09-11 16:08 | 2013-08-21 16:07 | 2014-03-21 17:03 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:09 | S217010567701 | LONGLANDS COURT (1-48) | 103170 | Completed | 1c | High | Emergency Lighting | Some of the covers of the lighting units in the staircase enclosures and in the roof space areas of this building are dirty, thus affecting the level of illumination from the bulb. | I would recommend that the dirty light covers in the staircase enclosures and in the roof space areas of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels from the light units. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on ketswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-21 16:09 | 2013-09-11 16:10 | 2013-08-21 16:09 | 2015-04-14 09:56 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:14 | S217010567701 | LONGLANDS COURT (1-48) | 103175 | Completed | 7 | Low | Lightning Protection | There is a lightning protection system installed on this building, the asset list given to me by the TMO electrical engineer states that this lightning protection system is tested and serviced on a planned preventive maintenance schedule by an external contractor. | Could I ask that the certification records for lightning protection systems are checked to make certain that there is an in date certificate for this particular building. | A & R Contract Management | Alex Bosman |  | system included in 13/14 testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 16:14 | 2014-02-17 16:15 | 2013-08-21 16:14 | 2014-03-21 17:04 | -180 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:26 | S217010567701 | LONGLANDS COURT (1-48) | 103188 | Completed | 15 | Medium | Emergency Lighting | There are combined normal and emergency escape lighting units installed in this building, covering the staircases and means of escape routes as well as other areas of the building. But it is not known if any of the lights in the lift motor room for the lift above flats 13 to 24 's staircase are also combined emergency lighting units. | I would recommend that a check is undertaken to see if any of the installed lighting units in this lift motor room are also emergency lighting units. If there are none installed I would recommend that some are installed, to the requirements of BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CHECKED LIGHTS IN LIFT ROOM AND FOUND 2 X 8W EMERGENCY FITTINGS NOT WORKING AND NO FISH KEY ALSO THE LIGHT ARE ON A 15A MCB. VO 2 X EMERGENCY FITTINGS 1 X FISH KEY 1 X WIRE FISH KEY 1 X RENEW MCB WORKING AND NO FISH KEY ALSO THE LIGHT ARE ON A 15A MCB. VO 2 X EMERGENCY FITTINGS 1 X FISH KEY All works complete. | 2015-11-20 | Fully Completed | Maria Ares | 2013-08-21 16:26 | 2013-10-20 16:28 | 2013-08-21 16:26 | 2015-11-23 13:07 | -60 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:28 | S217010567701 | LONGLANDS COURT (1-48) | 103190 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I pinned a copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders to each notice board in the entrance hall area of each staircase in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | Hard wired detectors fitted during PIR testing program | 2014-03-20 | Fully Completed |  |  |  | 2013-08-21 16:28 | 2014-03-21 17:05
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:30 | S217010567701 | LONGLANDS COURT (1-48) | 103191 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system currently installed on the staircase landings, in the roof level spaces and other areas of this building does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is this installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | COMPLETED 19.08.2015 | 2015-11-19 | Fully Completed | Maria Ares | 2013-08-21 16:30 | 2013-09-11 16:31 | 2013-08-21 16:30 | 2015-11-20 10:21 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:32 | S217010567701 | LONGLANDS COURT (1-48) | 103192 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system/ units in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-21 16:32 | 2013-09-11 16:33 | 2013-08-21 16:32 | 2015-02-27 12:14 | -21 | In target
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:13 | S217008650004 | EDENHAM WAY 15-50 | 207073 | Completed | 1a | High | Electrical Wire Check | The last test date on the landlords/buildings intake electrical supply board in the basement area was 2013. This RGE contractors label had "failed" written on it. | Please can it be confirmed that the fixed electrical wiring in this building has been retested and any defects rectified? If it has not I would recommend that the whole building common parts electrical fixed wiring is tested immediately with any defects found rectified and a new contractors label with the test and retest dates fixed to the basement supply boards. | A & R Contract Management | Alex Bosman |  | 04/11/2014 - Completed by RMA. Certification held on Keystone. | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-07-16 09:13 | 2015-08-06 09:15 | 2015-07-16 09:13 | 2015-08-25 16:09 | -21 | In target
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:30 | S217008650004 | EDENHAM WAY 15-50 | 207083 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE - LAST CERTIFICATE 02/11 | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection on 29/07/2015 | 2015-07-29 | Fully Completed | Gillian Kennedy | 2015-07-16 09:30 | 2015-08-06 09:31 | 2015-07-16 09:30 | 2015-08-25 14:58 | -21 | In target
16 AND 17 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:04 | S217009670005 | PENZANCE STREET 16/17 A-H | 214593 | Completed | 15 | Information Only | Emergency Lighting | When financially possible or if work is planned for the common parts lighting units There is presently no emergency lighting installed on the means of escape routes of this building, on the open external balconies, on the landings of the staircases, in the entrance hall areas or any of the common parts of this building. This is a four storey building. | As soon as financially possible or if work is to be undertaken on the lighting in the common parts of this building. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | complete - included within programmed works | 2015-11-17 | Fully Completed |  |  |  | 2015-09-02 15:04 | 2015-11-18 12:48
16 AND 17 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:11 | S217009670005 | PENZANCE STREET 16/17 A-H | 214594 | Completed | 23 | High | Dry or Wet Riser | According to the Chubb contractor's service labels the last service of these dry risers was undertaken on the 29th July 2014 with each riser charged to a pressure of 10 bar, there was then a visual inspection undertaken on the 11th December 2014. These dry risers are now overdue a service. | I would recommend that these two dry rising mains a tested and serviced with any defects found rectified. | A & R Contract Management | Alex Bosman |  | complete 06.08.2015 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-02 15:11 | 2015-09-23 15:12 | 2015-09-02 15:11 | 2015-11-20 10:37 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 14:36 | S217001880013 | ELM PARK GARDENS (16) | 200530 | Completed | 1 | High | Miscellaneous | According to the electrical contractors label on the basement level landlords electrical supply board this buildings electrical fixed wiring check is over due for retesting. The retest date of the contractors labels was October 2013, having been tested in October 2008. | Can it be confirmed with the TMO electrical engineer if the fixed wiring in the building has been retested? If it has not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. A new contractors label should be fixed to the electrical supply board giving the new test and the retest dates. | A & R Contract Management | Alex Bosman |  | Included within the 2015/16 communal testing programme | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-08 14:36 | 2015-06-29 14:38 | 2015-06-08 14:36 | 2015-08-25 15:00 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 14:40 | S217001880013 | ELM PARK GARDENS (16) | 200534 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-08 14:40 | 2015-06-29 14:41 | 2015-06-08 14:40 | 2015-11-27 09:46 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 14:42 | S217001880013 | ELM PARK GARDENS (16) | 200535 | Completed | 19 | High | Sprinklers | The basement conversion, flat number 16A has been fitted with a water protection system (water mist or domestic sprinklers). It is not known if the manufacturers documentation along with all the servicing and maintenance manuals etc have been handed over by the project manager or the contactor's who installed the system. | I would recommend that the buildings file is checked to see that the following information is contained within it this information is a requirement for fitting a domestic water protection system. 1. Commissioning certificates 2.Leakage test certificates 3. Functional test certificates 4. Documentation saying compliant with The Water Supply (Water Fittings) Regulations 1999 from water authority consulted and any response to the consultation; 5. Drawings showing details of the system which should include: a) the address and location of the premises b) the name and address of the supplier with the designers name; c) the date of installation. d) a general description of the system including water supply details. | A & R Contract Management | Alex Bosman | 2016-02-16 | Conversion project managed by RBKC all documentation has been requested however is not avaialable | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-08 14:42 | 2015-06-29 14:44 | 2015-06-08 14:42 | 2016-02-17 10:10 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 14:45 | S217001880013 | ELM PARK GARDENS (16) | 200538 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the roof level lift room and the basement corridor are out of test date according to the contractors servicing labels attached to them. The last test date on the lift room extinguisher according to the service label was July 2013 with the corridor one September 2012. | These portable fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 20/07/2015 | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-08 14:45 | 2015-06-29 14:47 | 2015-06-08 14:45 | 2015-08-25 15:01 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 14:47 | S217001880013 | ELM PARK GARDENS (16) | 200541 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Can't find any reference to this on Keystone | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-08 14:47 | 2015-06-29 15:18 | 2015-06-08 14:47 | 2015-11-27 09:47 | -21 | In target
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 15:18 | S217001880013 | ELM PARK GARDENS (16) | 200549 | Completed | 23c | High | Miscellaneous | Is there a contract with a specialist contractor to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 16A being undertaken according to the manufactures guidance. This will include any detection and alarm systems. | Is a specialist contractor being employed to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 16A in accordance with the manufactures guidance? If not testing/ servicing etc should be undertaken immediately and any defects etc rectified and then the system placed on a planned maintenance schedule for future testing/servicing etc. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Ap confirmed service compelte 3.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-08 15:18 | 2015-06-29 15:20 | 2015-06-08 15:18 | 2015-12-15 10:17 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:25 | S217002110007 | FINBOROUGH ROAD (169) | 194370 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase/landings, the entrance hall area, on the balconies and in the electrical cupboard/room. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-04-27 16:25 | 2015-05-18 16:26 | 2015-04-27 16:25 | 2015-12-02 10:08 | -21 | In target
17 DANVERS STREET - 2015.10.08 | 2015-10-19 07:53 | S217001420001 | DANVERS STREET (17) | 222466 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps has a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. KEYSTONE HAS DETAILS OF BOOSTER SET BUT NO EVIDENCE OF REGULAR INSPECTION & TESTING | A & R Contract Management | Alex Bosman |  | This pump set has been on the servicing schedule since original installation. Keystone will only show items with a compliance certificate which this does not fall under. | 2015-12-01 | Fully Completed | Maria Ares | 2015-10-19 07:53 | 2015-11-09 08:06 | 2015-10-19 07:53 | 2015-12-02 10:10 | -21 | In target
18 AND 19 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:51 | S217009670006 | PENZANCE STREET 18/19 A-H | 214622 | Completed | 15 | Information Only | Emergency Lighting | When financially possible or if work is planned for the common parts lighting units There is presently no emergency lighting installed on the means of escape routes of this building, on the open external balconies, on the landings of the staircases, in the entrance hall areas or any of the common parts of this building. This is a four storey building. | As soon as financially possible or if work is to be undertaken on the lighting in the common parts of this building. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | complete - included within programmed works | 2015-11-17 | Fully Completed |  |  |  | 2015-09-02 15:51 | 2015-11-18 12:49
18 AND 19 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:53 | S217009670006 | PENZANCE STREET 18/19 A-H | 214628 | Completed | 23 | High | Dry or Wet Riser | According to the Chubb contractor's service labels the last service of these dry risers was undertaken on the 29th July 2014 with each riser charged to a pressure of 10 bar, there was then a visual inspection undertaken on the 11th December 2014. These dry risers are now overdue a service. | I would recommend that these two dry rising mains a tested and serviced with any defects found rectified. | A & R Contract Management | Alex Bosman |  | complete 14.07.2015 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-02 15:53 | 2015-09-23 15:54 | 2015-09-02 15:53 | 2015-11-20 10:43 | -21 | In target
18 BASING STREET - 2015.08.15 | 2015-09-02 14:41 | S217008090002 | BASING STREET (18) | 214579 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the ground floor level entrance hall area of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 11.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-02 14:41 | 2015-09-23 14:46 | 2015-09-02 14:41 | 2015-11-20 10:45 | -21 | In target
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:15 | S217009620004 | OXFORD GARDENS (187) | 241815 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the landings of the staircase of this building. Keystone checked | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-01
191 LADBROKE GROVE, LONDON W10 6HH - 2015.11.03 | 2016-01-25 14:55 | S217009120006 | LADBROKE GROVE (191) | 239395 | Active | 23a | High | Emergency Lighting | There are emergency lighting units/system installed in this building, in the entrance hall area and on the landings of the staircase. Keystone has been checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-22
2 AND 4 ELM PARK GARDENS - 2015.05.22 | 2015-07-16 10:07 |  |  | 207110 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-07-16 10:07 | 2015-08-06 10:07 | 2015-07-16 10:07 | 2015-12-02 10:10 | -21 | In target
2 AND 4 ELM PARK GARDENS - 2015.05.22 | 2015-07-16 10:08 |  |  | 207112 | Completed | 23 | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO REFERENCE TO EL ON KEYSTONE | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-07-16 10:08 | 2015-08-06 10:09 | 2015-07-16 10:08 | 2015-12-02 10:12 | -21 | In target
2 RADDINGTON ROAD -2014.3.6 | 2014-03-26 11:23 | S217009860001 | RADDINGTON ROAD (2) | 136606 | Completed | 17 | Medium | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flat B of this building, but none were fitted within flat A. | A copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders was left for the resident of flat B and one given to the resident of flat A. The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2004. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat in accordance with the requirements of BS 5839 Part 6 :2004. | A & R Contract Management | Alex Bosman |  | hard wired heat and smoke detectors installed during PIR testing | 2014-05-12 | Fully Completed | Alex Bosman | 2014-03-26 11:23 | 2014-05-25 11:24 | 2014-03-26 11:23 | 2014-05-13 17:03 | -60 | In target
21 DANVERS STREET - 2015.10.08 | 2015-10-16 09:04 | S217001420003 | DANVERS STREET (21) | 222235 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps has a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO REFERENCE TO THIS EQUIPMENT ON KEYSTONE SERVICING & INSPECTION MODULE | A & R Contract Management | Alex Bosman |  | Cofely inspected and confirmed pump set added to service contract | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-16 09:04 | 2015-11-06 09:05 | 2015-10-16 09:04 | 2015-12-15 10:19 | -21 | In target
21 DANVERS STREET - 2015.10.08 | 2015-10-16 09:07 | S217001420003 | DANVERS STREET (21) | 222238 | Completed | 23a | High | Fire Extinguisher | The dry powder fire extinguisher located in the lower ground floor level water booster pump cupboard is out of test date according to the contractor's servicing labels attached to it. The last service/test date on this RGE contractors label is October 2011. | This dry powder fire extinguisher should be serviced immediately and it confirmed that it is on the external contractors maintenance schedule. Alternatively it could be removed from this cupboard and not serviced etc or replaced. | A & R Contract Management | Alex Bosman |  | Ap confirmed service complete 3.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-16 09:07 | 2015-11-06 09:08 | 2015-10-16 09:07 | 2015-12-15 10:19 | -21 | In target
210 LADBROKE GROVE, LONDON W10 5LU - 2015.11.19 | 2016-01-27 09:22 | S217009120003 | LADBROKE GROVE (210) | 239688 | Active | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. Keystone checked. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? If this system was installed within the last year is the installation certificate to the requirements of BS 5266 Part 2011 from the contractor on file. | A & R Contract Management | Alex Bosman | 2016-02-25
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:17 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102431 | Completed | 1b | High | Electrical Wire Check | There is no contractors label on the supply board or any other records to indicate when the last 5 year electrical fixed wiring test of this building. | Can it be confirmed by the TMO electrical engineer when the last 5 year electrical fixed wiring test of this building was undertaken? If it is overdue for testing I would recommend that a test is undertaken and any defects rectified or repaired as soon as possible. | A & R Contract Management | Alex Bosman | 2013-09-17 | Block included in 13/14 block electrical testing | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 11:17 | 2013-09-09 11:31 | 2013-08-19 11:17 | 2015-11-27 13:08 | -21 | In target | 2013-08-19 11:17 | 2015-12-03 10:50 | Janice Wray
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:53 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102443 | Active | 15 | Medium | Emergency Lighting | It is not known if any emergency lighting is installed on the landings of the staircase, ie the common parts of this building. The TMO electrical and contractors asset list says that there is an emergency lighting system installed by I could not seen any neon indicator/charging lights on the installed lighting units. There is defiantly a self contained emergency lighting unit in the electrical room. | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units. If it is found that there are emergency lighting units installed within the staircase of this building these should be tested and serviced immediately with a discharge test carried out. Any defects and/or problems highlighted as a result of this testing and servicing should be rectified. If it is found that none of the lighting units on the staircase are emergency lighting units then some should be installed as there are no windows to allow borrowed light into the staircase. Any installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  |  |  |  | Alex Bosman | 2013-08-19 11:53 | 2013-10-18 11:56 |  |  | 901 | 901 days overdue
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:57 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102444 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | Properties included in 10 year PIR testing program which includes the instillation of hard wired smoke detectors | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 11:57 | 2014-02-15 11:58 | 2013-08-19 11:57 | 2013-10-02 17:00 | -180 | In target
2-12 MORGAN ROAD, (EVEN NUMBERS ONLY) LONDON W10 5YS - 2016.03.04 | 2016-03-17 16:22 | S217009467714 | MORGAN ROAD EVEN (2-12) | 249748 | Active | 15 | High | Emergency Lighting | Neon indicator/charging lights could be seen on only 1 of the light units in the staircase enclosure of this building, there is an emergency light installed in the electrical room with a glowing indicator light. So it is not known if emergency lighting is installed on all of the landings of the staircase, ie the common parts of this building. | I would recommend that the an electrical engineer is asked to check the lighting units in this building to ascertain if which are combined emergency lighting units and why the neon indicator/charging lights cannot be seen on all of the light units. Is the installed emergency lighting system to the standard and requirements of British Standard 5266 Part 1 2011, as there are no windows to allow borrowed light into the staircase. If it is not then emergency lighting units should be installed to the standard as indicated above. | A & R Contract Management | Alex Bosman | 2016-04-18
2-12 MORGAN ROAD, (EVEN NUMBERS ONLY) LONDON W10 5YS - 2016.03.04 | 2016-03-17 16:24 | S217009467714 | MORGAN ROAD EVEN (2-12) | 249749 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, at the base of the staircase and in the electrical room. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-04-18
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:04 | S217001880014 | ELM PARK GARDENS (22) | 202875 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But it appears that the old units are still installed in the boiler room, the lift motor and there is no emergency lighting unit in the basement corridor where the electrical meters etc are located. | I would recommend that the installer of the new emergency lighting units/system in this building is asked for the design criteria of the new emergency lighting system as it does not appear to be installed to the requirements of BS 5266 Part 1, 2011. With all means or escape routes and other areas covered with emergency lighting units. | A & R Contract Management | Alex Bosman |  | RMA confirmed all works complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-23 15:04 | 2015-07-14 15:06 | 2015-06-23 15:04 | 2015-12-15 10:20 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:07 | S217001880014 | ELM PARK GARDENS (22) | 202880 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-23 15:07 | 2015-07-14 15:08 | 2015-06-23 15:07 | 2015-11-18 12:50 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:09 | S217001880014 | ELM PARK GARDENS (22) | 202883 | Completed | 19 | High | Miscellaneous | The basement conversion, flat number 22A has been fitted with a water protection system (water mist or domestic sprinklers). It is not known if the manufacturers documentation along with all the servicing and maintenance manuals etc have been handed over by the project manager or the contactor's who installed the system. | I would recommend that the buildings file is checked to see that the following information is contained within it this information is a requirement for fitting a domestic water protection system. 1. Commissioning certificates 2.Leakage test certificates 3. Functional test certificates 4. Documentation saying compliant with The Water Supply (Water Fittings) Regulations 1999 from water authority consulted and any response to the consultation; 5. Drawings showing details of the system which should include: a) the address and location of the premises b) the name and address of the supplier with the designers name; c) the date of installation. d) a general description of the system including water supply details. | A & R Contract Management | Alex Bosman | 2016-02-16 | Conversion project managed by RBKC all documentation has been requested however is not avaialable | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-23 15:09 | 2015-07-14 15:11 | 2015-06-23 15:09 | 2016-02-17 10:11 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:11 | S217001880014 | ELM PARK GARDENS (22) | 202886 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide and dry powder fire extinguishers located in the lift motor room and the boiler room of this building are out of service/test date according to the contractors servicing labels attached to them. The last test date on these RGE service labels was July 2013. | These portable fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-23 15:11 | 2015-07-14 15:12 | 2015-06-23 15:11 | 2015-12-02 10:12 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:12 | S217001880014 | ELM PARK GARDENS (22) | 202887 | Completed | 23b | High | Fire Extinguisher | There is a carbon dioxide fire extinguisher located in the basement level corridor where the electrics are wall mounted, this is out of service/test date according to the contractors servicing label attached to it. The last test date on this RGE service label was September 2012. | This portable fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. Alternatively it could be removed from the building and not serviced etc or replaced. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-23 15:12 | 2015-07-14 15:14 | 2015-06-23 15:12 | 2015-12-02 10:13 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:14 | S217001880014 | ELM PARK GARDENS (22) | 202889 | Completed | 23c | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-23 15:14 | 2015-07-14 15:15 | 2015-06-23 15:14 | 2015-12-02 10:14 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:16 | S217001880014 | ELM PARK GARDENS (22) | 202891 | Completed | 23d | High | Inspection Regime | 2Is there a contract with a specialist contractor to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 22A being undertaken according to the manufactures guidance. This will include any detection and alarm systems. | Is a specialist contractor being employed to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 35B in accordance with the manufactures guidance? If not testing/ servicing etc should be undertaken immediately and any defects etc rectified and then the system placed on a planned maintenance schedule for future testing/servicing etc. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed annual servicing complete 5.11.2015 | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-23 15:16 | 2015-07-14 15:18 | 2015-06-23 15:16 | 2016-02-17 10:12 | -21 | In target
22 ELM PARK GARDENS - 2015.06.10 | 2015-06-23 15:38 | S217001880014 | ELM PARK GARDENS (22) | 202909 | Completed | 23d | High | Miscellaneous | Are the weekly and monthly occupier's tests and inspections of all the mechanical and electrical components that make up the water protection system installed within flat 22A being undertaken according to the manufactures guidance. | Weekly and monthly occupier testing and inspections of the water protection system installed within flat 35B should be undertaken according to the manufactures guidance, with the results recorded in the buildings logbook. | A & R Contract Management | Alex Bosman | 2016-02-16 | Agreed with SJ, BM, PM, JW & AB not practicable to carry out weekly inspection. Further investigation required to identify alternative system solutions which do not require weekly inspection. | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-23 15:38 | 2015-07-14 15:48 | 2015-06-23 15:38 | 2016-02-17 10:14 | -21 | In target
23 DANVERS STREET - 2015.10.08 | 2015-10-16 09:14 | S217001420004 | DANVERS STREET (23) | 222243 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the middle cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing the annual maintenance of the water pump. | Can it be confirmed that the water booster pump in this middle cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing etc as is the case with other water pumps in adjacent buildings. KEYSTONE HAS DETAILS OF INSTALLATION BUT NO EVIDENCE OF REGULAR INSPECTIONS | A & R Contract Management | Alex Bosman |  | This pump set has been on the servicing schedule since original installation. Keystone will only show items with a compliance certificate which this does not fall under. | 2015-12-01 | Fully Completed | Maria Ares | 2015-10-16 09:14 | 2015-11-06 09:16 | 2015-10-16 09:14 | 2015-12-02 10:15 | -21 | In target
24 BURNABY STREET - 2015.09.21 | 2015-10-05 09:44 | S217000510010 | BURNABY STREET (24) | 219903 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/system installed in this building, in the entrance hall area and on the 1st floor level staircase landing. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 16.7.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-05 09:44 | 2015-10-26 09:45 | 2015-10-05 09:44 | 2015-12-15 10:21 | -21 | In target
24 STADIUM STREET - 2013.12.31 | 2013-12-31 14:41 | S217005190011 | STADIUM STREET (24) | 122173 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flat B, flat A had battery powered ones fitted. | A copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders was left for the occupant of flat B who can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | A & R Contract Management | Alex Bosman |  | Hard wired heat & smoke detectors fitted during PIR testing | 2014-04-22 | Fully Completed |  |  |  | 2013-12-31 14:41 | 2014-04-23 16:41
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 11:09 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215857 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/systems installed in each part/section of this building, on the landings of the staircases, in each of the entrance hall areas and in the electrical rooms/cupboards. The means of escape routes. | Can it please be confirmed when the installed emergency lighting systems in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago then these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-10 11:09 | 2015-10-01 11:10 | 2015-09-10 11:09 | 2015-12-15 10:22 | -21 | In target
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 13:09 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215917 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/systems installed in each part/section of this building, on the landings of the staircases, in each of the entrance hall areas and in the electrical rooms/cupboards. The means of escape routes. | Can it please be confirmed when the installed emergency lighting systems in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago then these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-10 13:09 | 2015-10-01 13:13 | 2015-09-10 13:09 | 2015-12-15 10:23 | -21 | In target
25 BASING STREET - 2015.08.13 | 2015-09-02 14:23 | S217008090003 | BASING STREET (25) | 214572 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the ground floor level entrance hall area of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 11.08.2015 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-02 14:23 | 2015-09-23 14:24 | 2015-09-02 14:23 | 2015-11-20 10:47 | -21 | In target
275 LADBROKE GROVE - 2015.10.13 | 2015-10-22 12:11 | S217009120009 | LADBROKE GROVE (275) | 223437 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the ground floor level base of staircase area of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? REFERENCE TO EL ON KEYSTONE BUT NO EVIDENCE OF INSPECTIONS/ TESTING /MAINTENANCE | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed servicing complete 2.2.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2015-10-22 12:11 | 2015-11-12 12:13 | 2015-10-22 12:11 | 2016-02-17 10:18 | -21 | In target
28 BURNABY STREET - 2015.09.21 | 2015-10-05 09:56 | S217000510012 | BURNABY STREET (28) | 219908 | Completed | 15 | High | Emergency Lighting | It appears that two of the light fittings in this building area also combined emergency light units, but the neon indicator lights are not visible on these light fittings. | Please can it be confirmed if there are combined normal and emergency lighting units in this building? If there are combined lighting units these should be repaired or replaced so that the emergency lights are in working order. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA confirmed inspected and works completed | 2016-01-13 | Fully Completed | Maria Ares | 2015-10-05 09:56 | 2015-10-26 09:57 | 2015-10-05 09:56 | 2016-01-14 15:30 | -21 | In target
28 BURNABY STREET - 2015.09.21 | 2015-10-05 09:57 | S217000510012 | BURNABY STREET (28) | 219909 | Completed | 23a | High | Emergency Lighting | There maybe emergency lighting units/system installed in this building, in the entrance hall area and on the 1st floor level staircase landing. | If there are emergency lighting units installed in this building can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO REFERENCE TO EMERGENCY LIGHTING ON KEYSTONE | A & R Contract Management | Alex Bosman |  | AP confirmed no EL present, to be included in upgrade program. | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-05 09:57 | 2015-10-26 10:00 | 2015-10-05 09:57 | 2015-12-15 10:25 | -21 | In target
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 10:01 | S217001880015 | ELM PARK GARDENS (28) | 201428 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But the old emergency lighting units are still installed in the lift motor. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and roof space area were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | RMA confirmed all works complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-15 10:01 | 2015-07-06 10:02 | 2015-06-15 10:01 | 2015-12-15 10:28 | -21 | In target
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 10:04 | S217001880015 | ELM PARK GARDENS (28) | 201433 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-15 10:04 | 2015-07-06 10:10 | 2015-06-15 10:04 | 2015-11-18 12:57 | -21 | In target
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 10:11 | S217001880015 | ELM PARK GARDENS (28) | 201439 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service compelte 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 10:11 | 2015-07-06 10:29 | 2015-06-15 10:11 | 2015-12-02 10:16 | -21 | In target
28 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 10:29 | S217001880015 | ELM PARK GARDENS (28) | 201444 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? | A & R Contract Management | Alex Bosman |  | AP confirmed service compelte 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 10:29 | 2015-07-06 10:32 | 2015-06-15 10:29 | 2015-12-02 10:17 | -21 | In target
29 DANVERS STREET-2013.07.23 | 2013-08-21 11:06 | S217001420007 | DANVERS STREET (29) | 103046 | Completed | 5 | Medium | Miscellaneous | It is not known if a water booster pump has been installed in the externally accessed cupboard at the lower ground floor level of this premises because the cupboard contains storage. Other premises in this terraced row have had water booster pumps installed. | If a water booster pump has been fitted in the lower ground floor level cupboard can it be confirmed that it is being serviced and maintained in accordance with the manufactures instructions etc, on a planned preventative maintenance schedule. If this is not the case then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. If one has not been fitted no actions are required. | A & R Contract Management | Alex Bosman |  | Pump included on service contract | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 11:06 | 2013-10-20 11:09 | 2013-08-21 11:06 | 2014-03-21 17:00 | -60 | In target
29 DANVERS STREET-2013.07.23 | 2013-08-21 11:11 | S217001420007 | DANVERS STREET (29) | 103048 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flat B of this building, but some are fitted within flat A. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. The resident of flat B can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat without detectors in accordance with the requirements of BS 5839 Part 6. | A & R Contract Management | Alex Bosman |  | Hard wired detectors installed as part of PIR teting program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 11:11 | 2014-02-17 11:12 | 2013-08-21 11:11 | 2014-03-21 16:58 | -180 | In target
29 DANVERS STREET-2013.07.23 | 2013-08-21 11:13 | S217001420007 | DANVERS STREET (29) | 103049 | Completed | 18 | Medium | Fire Extinguisher | There is a Dry Powder fire extinguisher (installed October 2011) in the externally accessed cupboard at the lower ground floor level of this building. This is a residential building only, installing fire extinguishers in residential only buildings is against the TMO policy as there is nobody in the building trained to use them etc. This is an external cupboard on the lower ground floor level and the extinguisher is inside the cupboard so if there is a fire in the cupboard nobody will open the cupboard to access the extinguisher, people will move away and call the fire service. Therefore I believe that this extinguisher is not needed. | I would recommend that this Dry Powder fire extinguisher is removed. This is because this is a residential only building and installing this extinguisher goes against TMO policy, guidance provided in national H M Government documents and advice from London Fire and Civil Defence Service. If it is decided that the Dry Powder fire extinguisher is to remain in situ then it must be added to the contractors maintenance and servicing schedule. The correct signage should be displayed and monthly occupier inspections must be undertaken by the caretaker(s). | A & R Contract Management | Alex Bosman |  | Order raised to have extingisher removed | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-21 11:13 | 2013-10-20 11:14 | 2013-08-21 11:13 | 2013-12-10 17:46 | -60 | In target
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:40 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215995 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/systems installed in each part/section of this building, on the landings of the staircases, in each of the entrance hall areas and in the electrical rooms/cupboards. The means of escape routes. | Can it please be confirmed when the installed emergency lighting systems in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago then these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-10 15:40 | 2015-10-01 15:42 | 2015-09-10 15:40 | 2015-12-02 10:18 | -21 | In target
32 DAWSON PLACE, LONDON W2 4TJ - 2016.02.02 | 2016-02-23 16:28 | S217007110001 | DAWSON PLACE (32) | 245316 | Completed | 12c | High | Miscellaneous | A vent has been inserted above flat 4's entrance door, it is not known if there is a fire dampener in this vent. | I would recommend that the vent above flat 4's entrance door is checked to see 1. Why has it been installed? 2. Has it been installed correctly and in accordance with the Building Regulations? 3. Is it fire rated to maintain the 30 minute protection of the staircase enclosure? 4. Has a fire dampener been fitted? 5. Is an intumescent block installed? If it is found that it has not been installed in accordance with the requirements of the Building Regulations it must be removed immediately or refitted correctly and 30 minute fire rated materials used to in fill this transom light area above this flat entrance door. | A & R Contract Management | Alex Bosman | 2016-03-22 | Order raised for RD to inspect & upgrade vent above entrance door so that it achieves 30 min fire resistance 201561477 RD to monitor | 2016-03-14 | Fully Completed | Mainu Miah | 2016-02-23 16:28 | 2016-03-15 16:30 | 2016-02-23 16:28 | 2016-03-31 15:38 | -21 | In target
32 DAWSON PLACE, LONDON W2 4TJ - 2016.02.02 | 2016-02-23 16:32 | S217007110001 | DAWSON PLACE (32) | 245318 | Active | 23 | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building, on the landings of the staircase and in the entrance hall area. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-22
32 ST CHARLES SQUARE - 2015.04.20 | 2015-04-27 15:00 | S217010080001 | ST CHARLES SQUARE (32) | 194321 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase landings and in the entrance hall area. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 24.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-04-27 15:00 | 2015-05-18 15:01 | 2015-04-27 15:00 | 2015-12-02 10:19 | -21 | In target
33 ARUNDEL GARDENS - 2015.05.11 | 2015-05-16 08:48 | S217007990001 | ARUNDEL GARDENS (33) | 197387 | Completed | 15 | High | Emergency Lighting | There is presently no emergency escape lighting installed in this building, on the staircase landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. | I would recommend that emergency lighting units are installed on the landings of the staircase and in the entrance lobby area as soon as possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Wil be included within this years programme if there is capacity. If not then budget year 16/17. Action entered into a programme of works. | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-16 08:48 | 2015-06-06 08:49 | 2015-05-16 08:48 | 2015-11-23 14:49 | -21 | In target | 2015-05-16 08:48 | 2015-11-29 14:49 | Janice Wray
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:21 | S217009120011 | LADBROKE GROVE (339) | 196437 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution boards and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the landlords/common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | 06/02/2014 - Completed by RGE - Certificate held on keystone. | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-05-12 09:21 | 2015-06-02 09:23 | 2015-05-12 09:21 | 2015-08-25 16:21 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:28 | S217009120011 | LADBROKE GROVE (339) | 196445 | Completed | 8b | High | Communal Area Storage | There were 4 suitcases and other household items on the floor outside of the electrical room/cupboard of the staircase of flats 5 to 8. | I would recommend that these items are removed from this area and the residents reminded that combustible items should not be kept in the staircase enclosures. | A & R Contract Management | Martin Barr | 2016-01-29 | Pat confirms the area has been cleared of these items | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2015-05-12 09:28 | 2015-06-02 09:29 | 2015-05-12 09:28 | 2016-04-07 16:57 | -21 | In target | 2015-05-12 09:28 | 2016-04-13 16:57 | Janice Wray
34 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:43 | S217001880016 | ELM PARK GARDENS (34) | 201414 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But the old emergency lighting units are still installed in the lift motor. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and roof space area were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | CONFIRMED THAT EMERGENCY LIGHT PRESENT AND WORKING IN LIFT ROOM AND CERT SUPPLIED FOR THE INSTALLATION | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-15 09:43 | 2015-07-06 09:44 | 2015-06-15 09:43 | 2015-11-18 12:59 | -21 | In target
34 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:44 | S217001880016 | ELM PARK GARDENS (34) | 201416 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-15 09:44 | 2015-07-06 09:45 | 2015-06-15 09:44 | 2015-11-18 13:00 | -21 | In target
34 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:45 | S217001880016 | ELM PARK GARDENS (34) | 201417 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 09:45 | 2015-07-06 09:46 | 2015-06-15 09:45 | 2015-12-02 10:22 | -21 | In target
34 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 09:47 | S217001880016 | ELM PARK GARDENS (34) | 201418 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 09:47 | 2015-07-06 09:48 | 2015-06-15 09:47 | 2015-12-02 10:40 | -21 | In target
34 GORDON PLACE, LONDON W8 4JE - 2015.12.22 | 2016-02-08 13:02 | S217002320001 | GORDON PLACE (34) | 241905 | Active | 15 | High | Emergency Lighting | New lighting units have recently been installed in the entrance hall area and in the staircase enclosure of this building. These are not combined normal and emergency lighting units, the staircase in this building is 4 storey's in height. Emergency lighting should have been installed to BS 5266 Part 1 to comply with the requirements of the Building Regulations and the Fire Safety Order. | Could the TMO electrical engineer please comment on why emergency lighting was not installed in the means of escape route of this building. Emergency lighting units should be installed to the requirements of BS 5266 Part 1, so that the requirements of the Building Regulations and the Fire Safety Order are meet. | A & R Contract Management | Alex Bosman | 2016-03-01
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:25 | S217009620005 | OXFORD GARDENS (34) | 103055 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards, but according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of the buildings common parts expired in March of this year, 2013. | Can it be confirmed with the TMO electrical engineer if the fixed wiring in the building has been retested. If it has not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Included in 13/14 testing program | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-21 11:25 | 2013-09-11 11:27 | 2013-08-21 11:25 | 2013-12-10 17:54 | -21 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:40 | S217009620005 | OXFORD GARDENS (34) | 103065 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room had a last test date on the contractor's label of September 2011 and had "Out of Date" written on the label dated the 13th February 2013. . | The fire extinguishers located in the roof level lift motor room should be replaced immediately with a fully serviceable fire extinguisher. I would recommend that the external contractor is asked to explain why this extinguisher was not replaced/serviced on the 13th February when the engineer wrote on the label. | A & R Contract Management | Alex Bosman |  | RGE to attend and rectify following Feb 2013 visit | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-21 11:40 | 2013-09-11 11:42 | 2013-08-21 11:40 | 2013-12-10 17:58 | -21 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:42 | S217009620005 | OXFORD GARDENS (34) | 103066 | Completed | 23b | High | Emergency Lighting | It appears that the monthly occupier tests and inspections of the emergency lighting and fire extinguishers etc in this building are not being undertaken. | Can it be confirmed that the monthly occupier testing and inspections of the emergency lighting, fire extinguishers and other items in this building are being undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training taking place 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-21 11:42 | 2013-09-11 11:43 | 2013-08-21 11:42 | 2014-04-23 16:43 | -21 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:44 | S217009620005 | OXFORD GARDENS (34) | 103067 | Active | 15 | Information Only | Emergency Lighting | It appears that there is presently no emergency lighting installed in/on the common parts of this building, on the external balconies, on the landings of the staircase or in the entrance hall area. The residential parts of this building are six floors levels. | I would recommend that the lighting units in this building are checked to see if any are also emergency lighting units. If none are not then I would recommend that emergency lighting units are installed in the common parts to provide illumination of the means of escape routes if the normal lighting fails. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed |  |  |  | 2013-08-21 11:44 | 2015-05-13 10:57
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:49 | S217001880004 | ELM PARK GARDENS (35) | 201254 | Completed | 15a | High | Emergency Lighting | It appears that a new emergency lighting system has been installed in this building. But it appears that there are no emergency lighting units installed in the basement level corridor or the basement level boiler room. The external area in front of this building is an emergency escape route from the basement level car park under the building next door and there are no emergency lighting units covering this external means of escape route. | I would recommend that the installer of the new emergency lighting units/system in this building is asked for the design criteria of the new emergency lighting system as it does not appear to be installed to the requirements of BS 5266 Part 1, 2011. With all means or escape routes and areas covered with emergency lighting units. ON ASSET REGISTER BUT NO CURRENT CERTIFICATES ON KEYSTONE | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-12 10:49 | 2015-07-03 10:51 | 2015-06-12 10:49 | 2015-12-15 10:28 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:51 | S217001880004 | ELM PARK GARDENS (35) | 201255 | Completed | 15b | High | Emergency Lighting | It appears that a new emergency lighting system has been installed in this building. | Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-12 10:51 | 2015-07-03 10:53 | 2015-06-12 10:51 | 2015-11-18 13:03 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:53 | S217001880004 | ELM PARK GARDENS (35) | 201256 | Active | 19 | High | Miscellaneous | The basement conversion, flat number 35B has been fitted with a water protection system (water mist or domestic sprinklers). It is not known if the manufacturers documentation along with all the servicing and maintenance manuals etc have been handed over by the project manager or the contactor's who installed the system. | I would recommend that the buildings file is checked to see that the following information is contained within it this information is a requirement for fitting a domestic water protection system. 1. Commissioning certificates 2.Leakage test certificates 3. Functional test certificates 4. Documentation saying compliant with The Water Supply (Water Fittings) Regulations 1999 from water authority consulted and any response to the consultation; 5. Drawings showing details of the system which should include: a) the address and location of the premises b) the name and address of the supplier with the designers name; c) the date of installation. d) a general description of the system including water supply details. | A & R Contract Management | Alex Bosman
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:56 | S217001880004 | ELM PARK GARDENS (35) | 201259 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room and the dry powder fire extinguisher in the basement boiler room are out of service/test date according to the contractors servicing labels attached to them. The last test date on these RGE service labels was July 2013. | These portable fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-12 10:56 | 2015-07-03 10:57 | 2015-06-12 10:56 | 2015-12-02 10:42 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 10:58 | S217001880004 | ELM PARK GARDENS (35) | 201261 | Completed | 23b | High | Fire Extinguisher | There is a carbon dioxide fire extinguisher located in the basement level electrical cupboard, this is out of service/test date according to the contractors servicing label attached to it. The last test date on this RGE service label was September 2011. | This portable fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. Alternatively it could be removed from the building and not serviced etc or replaced. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-12 10:58 | 2015-07-03 11:02 | 2015-06-12 10:58 | 2015-12-02 10:50 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 11:02 | S217001880004 | ELM PARK GARDENS (35) | 201263 | Completed | 23c | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be confirmed when this new emergency lighting system was installed in this building? If this was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-12 11:02 | 2015-07-03 11:03 | 2015-06-12 11:02 | 2015-12-02 10:51 | -21 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 11:04 | S217001880004 | ELM PARK GARDENS (35) | 201264 | Completed | 23d | High | Miscellaneous | Is there a contract with a specialist contractor to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 35B being undertaken according to the manufactures guidance. This will include any detection and alarm systems. | Is a specialist contractor being employed to undertake the quarterly and annual tests, inspections and servicing of all the mechanical and electrical components that make up the water protection system installed within flat 35B in accordance with the manufactures guidance? If not testing/ servicing etc should be undertaken immediately and any defects etc rectified and then the system placed on a planned maintenance schedule for future testing/servicing etc. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-16 | Conversion project managed by RBKC all documentation has been requested however is not avaialable | 2016-02-16 | Fully Completed | Maria Ares | 2015-06-12 11:04 | 2015-07-03 11:05 | 2015-06-12 11:04 | 2016-02-17 10:19 | -21 | In target
37 DANVERS STREET - 2015.10.06 | 2015-10-21 08:34 | S217001420011 | DANVERS STREET (37) | 222950 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO MENTION OF THIS ON KEYSTONE SERVICING INFO | A & R Contract Management | Alex Bosman |  | Cofely inspected and confirmed pump set added to service contract | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 08:34 | 2015-11-11 08:35 | 2015-10-21 08:34 | 2015-12-15 10:29 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 11:28 | S217009700001 | PORTOBELLO ROAD (375) | 201061 | Completed | 5 | High | Miscellaneous | There has been a newly constructed water booster pump room at the rear of this building. There was no service book within this room indicating that the water pumps etc are on a planned preventive maintenance programme. | Can it please be confirmed that the water pumps etc are on a planned preventive maintenance programme with a third party contractor? If they are not then I would recommend that these pumps etc are added to the Cofley maintenance list. KEYSTONE INFO CONFIRMS COFLEY TO SERVICE - BUT NO SERVICING DOCUMENTATION | A & R Contract Management | Alex Bosman |  | It has been confirmed that the water pumps are on a PPM schedule. | 2015-10-28 | Fully Completed | Gillian Kennedy | 2015-06-11 11:28 | 2015-07-02 11:44 | 2015-06-11 11:28 | 2015-10-29 15:09 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:12 | S217009700001 | PORTOBELLO ROAD (375) | 201092 | Completed | 18 | High | Fire Extinguisher | There is no carbon dioxide fire extinguisher in the water pump room. The TMOs policy is to have suitable fire extinguishers located in plant rooms. | I would recommend that a carbon dioxide fire extinguisher is located in this water pump room. | A & R Contract Management | Alex Bosman |  | AP servicing complete 19.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-11 12:12 | 2015-07-02 12:13 | 2015-06-11 12:12 | 2015-11-27 09:49 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:14 | S217009700001 | PORTOBELLO ROAD (375) | 201096 | Completed | 23a | High | Fire Alarm | There has been a newly constructed water booster pump room at the rear of this building. There is a full fire alarm system fitted within this room and there was no service book within this room indicating that this system is being serviced etc on a planned preventive maintenance programme. | Can it please be confirmed that the fire alarm system fitted within this room is on a planned preventive maintenance programme with a third party contractor? If it is not then it should be serviced and tested immediately and then placed on a six monthly service/maintenance list. CANNOT FIND REFERENCE TO THIS ON KEYSTONE SERVICING | A & R Contract Management | Alex Bosman |  | Ap confirmed Fire alarm serviced 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-11 12:14 | 2015-07-02 12:17 | 2015-06-11 12:14 | 2015-12-15 10:30 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:18 | S217009700001 | PORTOBELLO ROAD (375) | 201100 | Active | 23b | High | Miscellaneous | Are the weekly occupier's tests of this pump rooms fire alarm and warning system being undertaken? | Weekly occupier inspections of this pump rooms fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | A & R Contract Management | Alex Bosman
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:21 | S217009700001 | PORTOBELLO ROAD (375) | 201104 | Completed | 23c | High | Emergency Lighting | It appears that there is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? CANNOT FIND REFERENCE TO THIS ON KEYSTONE SERVICING | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-11 12:21 | 2015-07-02 12:23 | 2015-06-11 12:21 | 2015-12-15 10:30 | -21 | In target
38 EARDLEY CRESCENT - 2015.06.10 | 2015-06-15 11:03 | S217001640001 | EARDLEY CRESCENT (38) | 201467 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE FOR "RGE TO SERVICE" but no certificate | A & R Contract Management | Alex Bosman |  | completed on 10.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-06-15 11:03 | 2015-07-06 11:04 | 2015-06-15 11:03 | 2015-11-20 10:50 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:07 | S217007860010 | ADAIR ROAD | 201181 | Completed | 12c | High | Miscellaneous | At the lower ground floor level between studios 13 and 14 a person cannot open these exit doors to the lower ground floor level external areas from the inner face unless they have a fey fob. There are no override buttons etc fitted to these door locks. | I would recommend that suitable release devices, complying with the requirements of the Building regulations are fitted to these two lower ground floor level exit doors. This is so that these exits doors can be used in an emergency situation. | A & R Contract Management | Alex Bosman |  | MA has spoken to both Ronnie the ESA and Silks Engineer and they both confirmed to MA that there are 2 exits, 1 fob operated and the other push handle. | 2015-11-19 | Fully Completed | Maria Ares | 2015-06-11 16:07 | 2015-07-02 16:08 | 2015-06-11 16:07 | 2015-11-20 10:52 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:13 | S217007860010 | ADAIR ROAD | 201187 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape routes of this building, on the staircase landings. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON ASSET REGISTER -NO CERTS | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-11 16:13 | 2015-07-02 16:14 | 2015-06-11 16:13 | 2015-12-15 10:31 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:05 | S217008860001 | HESKETH PLACE (4) | 102543 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-09 | Building included in 14/15 communal electrical testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-19 14:05 | 2013-09-09 14:09 | 2013-08-19 14:05 | 2014-03-21 16:39 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:10 | S217008860001 | HESKETH PLACE (4) | 102548 | Completed | 1b | High | Communal Lighting | The covers of the lighting units in the common parts of the building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircase. | A & R Contract Management | Alex Bosman | 2013-09-09 | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-19 14:10 | 2013-09-09 14:14 | 2013-08-19 14:10 | 2015-04-14 09:57 | -21 | In target
40 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 11:13 | S217001880017 | ELM PARK GARDENS (40) | 201050 | Completed | 15a | High | Emergency Lighting | Individual units of this emergency lighting system have failed and have been replaced with normal pendant lights, outside flats 4 and 5 and 8 and 9 for instance. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | NEW EMERGENCY LIGHTING INSTALLED AND CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-11 11:13 | 2015-07-02 11:14 | 2015-06-11 11:13 | 2015-11-18 13:06 | -21 | In target
40 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 11:14 | S217001880017 | ELM PARK GARDENS (40) | 201053 | Completed | 15b | High | Emergency Lighting | There appears to be no emergency lighting units in the roof level lift and water tank rooms. | I would recommend that emergency lighting units are installed in the roof level lift and water tank rooms, if none are presently installed. | A & R Contract Management | Alex Bosman |  | THERE IS AN EMERGENCY FITTING TO TANK ROOM AND IT IS IN WORKING ORDER. | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-11 11:14 | 2015-07-02 11:15 | 2015-06-11 11:14 | 2015-11-18 13:07 | -21 | In target
40 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 11:16 | S217001880017 | ELM PARK GARDENS (40) | 201054 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO REFERENCE TO EL ON KEYSTONE | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 18.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-11 11:16 | 2015-07-02 11:17 | 2015-06-11 11:16 | 2015-11-27 09:50 | -21 | In target
40 ELM PARK GARDENS - 2015.05.22 | 2015-06-11 11:17 | S217001880017 | ELM PARK GARDENS (40) | 201056 | Completed | 23b | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractors maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-11 11:17 | 2015-07-02 11:18 | 2015-06-11 11:17 | 2015-12-02 10:52 | -21 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:37 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106582 | Completed | 6a | High | Electrical Wire Check | It is not known if the washing machines and the tumble dryers in the laundry room are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. Cyrenians manage high risk residents at this site with on-site 24/7 support staff | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-18 12:37 | 2013-10-09 12:40 | 2013-09-18 12:37 | 2015-02-27 12:15 | -21 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:41 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106583 | Completed | 6b | High | Miscellaneous | It is not known if the extractor in the lower ground floor laundry area is serviced on a planned preventative maintenance schedule? | I would recommend that it is confirmed that the lower ground floor laundry area extractor is serviced on a planned preventative maintenance schedule, along with any other filters or extractors in the building | A & R Contract Management | Alex Bosman |  | RMA confirmed both fans overhauld and serviced | 2015-12-14 | Fully Completed | Maria Ares | 2013-09-18 12:41 | 2013-10-09 12:42 | 2013-09-18 12:41 | 2015-12-15 10:32 | -21 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:45 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106585 | Completed | 18 | High | Fire Extinguisher | The are more fire extinguishers in this building now that when the last fire risk assessment was undertaken, it is not known if the Cyrenians have order additional appliances or the fire extinguisher company has just installed them. The original policy was to have control of any fire extinguishers and none would be located in the staircase enclosure in case they were used as weapons etc. | The TMO are responsible for fire fighting equipment according to the service level agreement, section 4. I would recommend that the policy whereby the fire fighting equipment is kept under control is adopted and the additional fire extinguishers are removed from the building. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 24/07/2015 | 2015-08-24 | Fully Completed | Gillian Kennedy | 2013-09-18 12:45 | 2013-10-09 12:46 | 2013-09-18 12:45 | 2015-08-25 15:02 | -21 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:47 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106587 | Completed | 23a | High | Fire Alarm | According to the service level agreement the occupier testing in this building is the responsibility of the Cyrenians with the servicing and maintenance of the equipment and systems the responsibility of TMO. Presently the fire alarm system in this building is being service 8 times a year, 2 companies undertaking 4 visits each, instead of the 2 visits as required by the British Standard. | I would recommend that the servicing arrangements for the buildings fire alarm system is investigated and the correct number of service visits is adhered to. Presently the system is being serviced 4 times as often as required. There are 2 different companies undertaking the servicing of the buildings fore alarm system. | A & R Contract Management | Alex Bosman |  | completed 20.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-09-18 12:47 | 2013-10-09 12:48 | 2013-09-18 12:47 | 2015-11-20 10:52 | -21 | In target
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:49 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106590 | Completed | 23b | High | Fire Alarm | There are two interface units for the automatic vent, these are located in the ground floor entrance lobby and on the 2nd floor landing, it is not known if these units are being serviced at the same time as the fire alarm and warning system by the maintenance companies. | Can it be confirmed with the fire alarm maintenance company(s) that the two interface units connected too the automatic ventilation system are they being serviced at the same time as the fire alarm and warning system and in accordance with the manufactures instructions. | A & R Contract Management | Alex Bosman |  | completed 20.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-09-18 12:49 | 2013-10-09 12:50 | 2013-09-18 12:49 | 2015-11-20 10:53 | -21 | In target
41 DANVERS STREET -2015.10.06 | 2015-10-21 08:43 | S217001420013 | DANVERS STREET (41) | 222952 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufactures instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO MENTION OF BOOSTER PUMP IN KEYSTONE SERVICING | A & R Contract Management | Alex Bosman |  | Cofely inspected and confirmed pump set added to service contrac | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 08:43 | 2015-11-11 08:44 | 2015-10-21 08:43 | 2015-12-15 10:33 | -21 | In target
41 DANVERS STREET -2015.10.06 | 2015-10-21 08:45 | S217001420013 | DANVERS STREET (41) | 222953 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? EL ON KEYSTONE BUT LAST INSPECTION ? TESTING CERTIFICATE 02/13 | A & R Contract Management | Alex Bosman |  | Ap confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 08:45 | 2015-11-11 08:46 | 2015-10-21 08:45 | 2015-12-15 10:35 | -21 | In target
43 DANVERS STREET - 2015.10.08 | 2015-10-22 11:37 | S217001420014 | DANVERS STREET (43) | 223401 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. BOOSTER MENTIONED ON KEYSTONE BUT NO INSPECTION / SERVICING INFO | A & R Contract Management | Alex Bosman |  | This pump set has been on the servicing schedule since original installation. Keystone will only show items with a compliance certificate which this does not fall under. | 2015-12-01 | Fully Completed | Maria Ares | 2015-10-22 11:37 | 2015-11-12 11:39 | 2015-10-22 11:37 | 2015-12-02 10:53 | -21 | In target
43 DANVERS STREET - 2015.10.08 | 2015-10-22 11:40 | S217001420014 | DANVERS STREET (43) | 223405 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently being installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? EL MENTIONED ON KEYSTONE BUT LAST CERTIFICATE 02/2013 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-22 11:40 | 2015-11-12 11:42 | 2015-10-22 11:40 | 2015-12-15 10:36 | -21 | In target
45 DANVERS STREET - 2015.10.06 | 2015-10-21 07:46 | S217001420015 | DANVERS STREET (45) | 222933 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO MENTION OF BOOSTER PUMP AT THIS BLOCK ON KEYSTONE. | A & R Contract Management | Alex Bosman |  | completed | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 07:46 | 2015-11-11 07:47 | 2015-10-21 07:46 | 2015-12-15 10:37 | -21 | In target
45 DANVERS STREET - 2015.10.06 | 2015-10-21 07:51 | S217001420015 | DANVERS STREET (45) | 222936 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently being installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? EL ON KEYSTONE BUT last inspection Certificate 02/13 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 07:51 | 2015-11-11 07:52 | 2015-10-21 07:51 | 2015-12-15 10:37 | -21 | In target
47 DANVERS STREET - 2015.10.06 | 2015-10-21 14:53 | S217001420016 | DANVERS STREET (47) | 223168 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufacturers instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. BOOSTER PUMP RECORDED ON KEYSTONE BUT NO INSPECTION / SERVICING / MAINTENANACE RECORDS | A & R Contract Management | Alex Bosman |  | This pump set has been on the servicing schedule since original installation. Keystone will only show items with a compliance certificate which this does not fall under. | 2015-12-01 | Fully Completed | Maria Ares | 2015-10-21 14:53 | 2015-11-11 14:54 | 2015-10-21 14:53 | 2015-12-02 11:00 | -21 | In target
47 DANVERS STREET - 2015.10.06 | 2015-10-21 15:17 | S217001420016 | DANVERS STREET (47) | 223182 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 15:17 | 2015-11-11 15:18 | 2015-10-21 15:17 | 2015-12-15 10:38 | -21 | In target
49 DANVERS STREET - 2015.10.6 | 2015-10-21 14:41 | S217001420017 | DANVERS STREET (49) | 223153 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufactures instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO MENTION OF BOOSTER PUMP AGAINST THIS BLOCK IN KEYSTONE | A & R Contract Management | Alex Bosman |  | Cofely inspected and confirmed pump set added to service contract | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 14:41 | 2015-11-11 14:42 | 2015-10-21 14:41 | 2015-12-15 10:39 | -21 | In target
49 DANVERS STREET - 2015.10.6 | 2015-10-21 14:42 | S217001420017 | DANVERS STREET (49) | 223155 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? EL ON KEYSTONE BUT LAST TESTING - 02/13 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 14:42 | 2015-11-11 14:44 | 2015-10-21 14:42 | 2015-12-15 10:40 | -21 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 14:52 | S217010567702 | LONGLANDS COURT (49-81) | 103123 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 14:52 | 2013-09-11 14:53 | 2013-08-21 14:52 | 2014-03-21 17:02 | -21 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 14:54 | S217010567702 | LONGLANDS COURT (49-81) | 103124 | Completed | 7 | Low | Lightning Protection | There is a lightning protection system installed on this building, the asset list given to me by the TMO electrical engineer states that this lightning protection system is tested and serviced on a planned preventive maintenance schedule by an external contractor. | Could I ask that the certification records for lightning protection systems are checked to make certain that there is an in date certificate for this particular building. | A & R Contract Management | Alex Bosman |  | Included in 13/14 testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 14:54 | 2014-02-17 14:55 | 2013-08-21 14:54 | 2014-03-21 17:03 | -180 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:08 | S217010567702 | LONGLANDS COURT (49-81) | 103136 | Completed | 15 | Medium | Emergency Lighting | There are combined normal and emergency escape lighting units installed in this building, covering the balcony's, staircase and other areas of the building. But it is not known if any of the lights in the lift motor room area are also combined emergency lighting units. | I would recommend that a check is undertaken to see if any of the installed lighting units in the lift motor room are also emergency lighting units. If there are none installed I would recommend that some are installed, to the requirements of BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | LIFT ROOM AND FOUND THE 8W FITTINGS NOT WORKING AND NO FISH KEY. VO 2 X 8W EMERGENCY FITTINGS 1 X FISH KEY 1 X WIRE FISH KEY All works completed | 2015-11-20 | Fully Completed | Gillian Kennedy | 2013-08-21 15:08 | 2013-10-20 15:09 | 2013-08-21 15:08 | 2015-11-23 13:11 | -60 | In target | 2013-08-21 15:08 | 2015-05-20 12:03 | Maria Ares
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:09 | S217010567702 | LONGLANDS COURT (49-81) | 103137 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system currently installed in the staircase, on the open balconies and in some other areas of this building including the resident's storage area does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 19.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-08-21 15:09 | 2013-09-11 15:12 | 2013-08-21 15:09 | 2015-11-20 10:54 | -21 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:12 | S217010567702 | LONGLANDS COURT (49-81) | 103140 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system/ units in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training booked 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-21 15:12 | 2013-09-11 15:14 | 2013-08-21 15:12 | 2014-04-23 16:43 | -21 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:17 | S217010567702 | LONGLANDS COURT (49-81) | 103145 | Completed | 1b | High | Emergency Lighting | Some of the covers of the lighting units in the staircase enclosure and on the open balconies of this building are dirty, thus affecting the level of illumination from the bulb. | I would recommend that the dirty light covers in the staircase enclosure and the open balconies of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels from the light units. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on ketswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-21 15:17 | 2013-09-11 15:19 | 2013-08-21 15:17 | 2015-04-14 10:05 | -21 | In target
5 BURNABY STREET - 2013.12.31 | 2013-12-31 14:19 | S217000510002 | BURNABY STREET (5) | 122154 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. But a battery operated one was fitted in flat A. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | hard wired heat & smoke detectors fitted during PIR testing | 2014-04-22 | Fully Completed |  |  |  | 2013-12-31 14:19 | 2014-04-23 16:44
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:25 | S217001880002 | ELM PARK GARDENS (5) | 102406 | Completed | 15 | High | Emergency Lighting | It appears that there are no emergency lighting units installed in the roof level cold water tank room or the left hand side lift motor room. No neon charging lights can be seen on the normal light fittings installed in these areas. The neon charging lights are clearly visible on similar other light fittings in this building. | I would recommend that a check is undertaken of these light units to see if they are combined emergency /normal lighting units. If they are not emergency lighting units then I would recommend that self contained emergency lighting are installed in these areas. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. | A & R Contract Management | Alex Bosman | 2013-09-09 | INSTALL 3 X EM FLOURESCENT 5FT FITTINGS & DIFFUSERS FOR TANK & LIFT ROOM All works completed | 2015-11-20 | Fully Completed | Maria Ares | 2013-08-19 10:25 | 2013-09-09 10:27 | 2013-08-19 10:25 | 2015-11-23 13:12 | -21 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:28 | S217001880002 | ELM PARK GARDENS (5) | 102407 | Completed | 17 | Low | Smoke Alarms | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I would recommend that a copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders is delivered to each flat in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman | 2014-02-03 | Properties included in 10 year PIR program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 10:28 | 2014-02-15 10:30 | 2013-08-19 10:28 | 2013-10-02 16:56 | -180 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:31 | S217001880002 | ELM PARK GARDENS (5) | 102408 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircases, on the flat/lift lobby areas, the storage areas and in the roof and basement level areas of this building do not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-09 | Added to Keystone database for inclusion in future servicing | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 10:31 | 2013-09-09 10:32 | 2013-08-19 10:31 | 2013-10-02 16:57 | -21 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:48 | S217001880002 | ELM PARK GARDENS (5) | 102418 | Active | 23c | High | Sprinklers | Are the weekly occupier's inspections of the installed sprinkler system being undertaken? | Weekly occupier inspections of the as installed sprinkler system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | A & R Contract Management | Alex Bosman | 2013-09-09 |  |  |  | Alex Bosman | 2013-08-19 10:48 | 2013-09-09 10:51 |  |  | 940 | 940 days overdue
51 - 80 EDENHAM WAY - 2015.06.16 | 2015-06-25 15:56 | S217008650002 | EDENHAM WAY (51-80) | 203411 | Completed | 1a | High | Electrical Wire Check | There is an in date last tested November 2014 Stewards Electrical Limited contractors label on the 2nd floor level landlords electrical supply board. But no contractor's label on the ground floor level one. | Please can it be confirmed that all of the landlords or common parts fixed electrical wiring in this building has been tested? If it has not I would recommend that the whole building common parts electrical fixed wiring is tested with any defects found rectified. | A & R Contract Management | Alex Bosman |  | 14/11/2014 - Complted - Certificate held in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-25 15:56 | 2015-07-16 15:57 | 2015-06-25 15:56 | 2015-08-25 16:23 | -21 | In target
51 - 80 EDENHAM WAY - 2015.06.16 | 2015-06-25 16:02 | S217008650002 | EDENHAM WAY (51-80) | 203415 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the floor level electrical cupboards and the dry powder fire extinguisher in the externally accessed ground floor bin storage room are out of test date according to the contractors servicing label attached to them. The last service date was January 2014 according to the RGE contractors servicing labels. | These fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. Alternatively these carbon dioxide fire extinguishers could be removed and not serviced. It is not known why there is a dry powder fire extinguisher in the bin room though. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 24/07/2015 | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-25 16:02 | 2015-07-16 16:03 | 2015-06-25 16:02 | 2015-08-25 15:02 | -21 | In target
51 - 80 EDENHAM WAY - 2015.06.16 | 2015-06-25 16:03 | S217008650002 | EDENHAM WAY (51-80) | 203416 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE - LAST SERVICE "03/13" | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 28/07/2015 | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-25 16:03 | 2015-07-16 16:04 | 2015-06-25 16:03 | 2015-08-25 16:25 | -21 | In target | 2015-06-25 16:03 | 2015-08-31 16:25 | Janice Wray
52 ELM PARK GARDENS - 2015.06.22 | 2015-07-09 10:12 | S217001880023 | ELM PARK GARDENS (52) | 205706 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed and have been replaced with just pendant lights. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | System serviced by chubb 22.5.2015 confirmed | 2015-08-11 | Fully Completed | Gillian Kennedy | 2015-07-09 10:12 | 2015-07-30 10:13 | 2015-07-09 10:12 | 2015-08-12 12:20 | -21 | In target
52 ELM PARK GARDENS - 2015.06.22 | 2015-07-09 10:14 | S217001880023 | ELM PARK GARDENS (52) | 205707 | Completed | 23 | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Keystone - visit 04/13 & no documentation | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 24/07/2015 | 2015-07-24 | Fully Completed | Gillian Kennedy | 2015-07-09 10:14 | 2015-07-30 10:15 | 2015-07-09 10:14 | 2015-08-25 15:05 | -21 | In target
55 DANVERS STREET - 2015.10.08 | 2015-10-22 12:01 | S217001420019 | DANVERS STREET (55) | 223434 | Completed | 4 | High | Miscellaneous | There is a gas meter wall mounted at a high level and located in the entrance hall/lobby area of this building, behind the buildings entrance/exit door. There are electrical meters next to this gas meter. The Building Regulations states that "Gas services, installations or meters should not be incorporated within a protected staircase/route unless the gas installation is in accordance with the Gas Safety (Installation and Use) Regulations 1998. Gas Meter is for flat B - leasehold flat. (Previous TMO engineers agreed to box in the gas meter but this was never done.) | Can it be confirmed that the wall mounted gas meter located in the entrance hall area of this building complies to the requirements of the Gas Safety (Installation and Use) Regulations 1998? Have there been any comments about the gas and electrical meters being located next to each other by the contractors undertaking the buildings annual gas safety checks? | A & R Contract Management | Alex Bosman |  | Inspected and necessary works being progressed with National Grid. | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-22 12:01 | 2015-11-12 12:04 | 2015-10-22 12:01 | 2015-12-15 10:41 | -21 | In target
55 DANVERS STREET - 2015.10.08 | 2015-10-22 12:05 | S217001420019 | DANVERS STREET (55) | 223435 | Completed | 5 | High | Miscellaneous | It is not known if there is a water booster pump installed at the lower ground floor level of this building, there is in every one of the other buildings in this terraced row. There is no access to the lower ground floor level area unless you go through the lower level flat. If there is a water pump installed in a cupboard at this lower floor level it is not known if this pump is being maintained. The water booster pumps in the other buildings have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed if there is a water booster pump in a cupboard at the lower ground floor level of this building? If there is, is it being serviced and maintained in accordance with the manufactures instructions etc on a planned preventative maintenance mp schedule. How do you access the water pump? If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. NO REFERENCE TO BOOSTER PUMPS ON KEYSTONE | A & R Contract Management | Alex Bosman |  | Cofely inspected and confirmed no pump set on site | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-22 12:05 | 2015-11-12 12:06 | 2015-10-22 12:05 | 2015-12-15 10:42 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:28 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204207 | Completed | 15a | High | Emergency Lighting | =A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But there appears to be no emergency lighting units installed in the lift motor and water tank rooms or in the external boiler room. | Can it please be confirmed that as part of the installation of the new emergency lighting system that the lack of emergency lighting in the lift motor room and roof space areas as well as the boiler was considered as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | RMA confirmed works complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-07-01 09:28 | 2015-07-22 09:29 | 2015-07-01 09:28 | 2015-12-15 10:43 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:30 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204208 | Completed | 15b | High | Emergency Lighting | There appears to be no emergency lighting units installed in the lift motor and water tank rooms or in the external boiler room. | I would recommend that emergency lighting units are installed in these areas. | A & R Contract Management | Alex Bosman |  | RMA confirmed complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-07-01 09:30 | 2015-07-22 09:31 | 2015-07-01 09:30 | 2015-12-15 10:44 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:31 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204209 | Completed | 15c | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-07-01 09:31 | 2015-07-22 09:32 | 2015-07-01 09:31 | 2015-11-18 13:09 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:32 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204210 | Completed | 23a | High | Fire Extinguisher | All of the fire extinguishers located in this building and in the boiler room and gas meter area at the rear of this building are out of service/test date according to the contractors servicing labels attached to them. The last test date on these RGE service labels was July 2013. | These portable fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 20/07/2015 | 2015-07-20 | Fully Completed | Gillian Kennedy | 2015-07-01 09:32 | 2015-07-22 09:33 | 2015-07-01 09:32 | 2015-08-25 15:06 | -21 | In target
55 ELM PARK GARDENS - 2015.06.22 | 2015-07-01 09:34 | S217001880024 | ELM PARK GARDENS 55 (1-9) | 204213 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? KEYSTONE - NO MENTION OF EL AT THIS BLOCK | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 28.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-07-01 09:34 | 2015-07-22 09:35 | 2015-07-01 09:34 | 2015-11-27 09:51 | -21 | In target
57 AND 59 EDITH GROVE - 2015.05.13 | 2015-05-28 13:42 | S217001780003 | EDITH GROVE (57-59) | 199103 | Completed | 1 | High | Emergency Lighting | As soon as possible There is presently no emergency escape lighting installed in this building, on the staircase landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. | I would recommend that emergency lighting units are installed on the landings of the staircase and in the entrance lobby area as soon as possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Wil be included within this years programme if there is capacity. If not then budget year 16/17. Action entered into a programme of works. | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-28 13:42 | 2015-06-18 13:44 | 2015-05-28 13:42 | 2015-11-23 14:55 | -21 | In target | 2015-05-28 13:42 | 2015-11-29 14:55 | Janice Wray
57 DANVERS STREET - 2015.10.06 | 2015-10-21 07:35 | S217001420020 | DANVERS STREET (57) | 222928 | Completed | 5 | High | Miscellaneous | There is a water booster pump installed at the lower ground floor level of this building in the end cupboard. There is no maintenance logbook for this buildings water pump, other buildings water pumps have a contractors maintenance logbook in the water pump cupboard showing annual maintenance of the water pump. | Can it be confirmed that this water booster pump in the end cupboard at the lower ground floor level of this building is being serviced and maintained in accordance with the manufactures instructions etc on a planned preventative maintenance schedule. If this pump is not being serviced etc then I would recommend that regular servicing is undertaken with all repairs/defects repaired as soon as possible and records kept. A maintenance logbook should be kept on site as proof of servicing of this pump etc as is the case with other water pumps in adjacent buildings. REFERENCE TO BOOSTER PUMP ON KEYSTONE BUT NO SERVICING / INSPECTION DATES OR DOCS. | A & R Contract Management | Alex Bosman |  | This pump set has been on the servicing schedule since original installation. Keystone will only show items with a compliance certificate which this does not fall under. | 2015-12-01 | Fully Completed | Maria Ares | 2015-10-21 07:35 | 2015-11-11 07:37 | 2015-10-21 07:35 | 2015-12-02 11:01 | -21 | In target
57 DANVERS STREET - 2015.10.06 | 2015-10-21 07:39 | S217001420020 | DANVERS STREET (57) | 222930 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting unit currently being installed in the entrance hall area of this building on the means of escape routes of this building, | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? EL recorded on Keystone but only testing certification is from 02/13. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-10-21 07:39 | 2015-11-11 07:40 | 2015-10-21 07:39 | 2015-12-15 10:44 | -21 | In target
58 ELM PARK GARDENS - 2014.04.15 | 2014-04-22 13:46 | S217001880026 | ELM PARK GARDENS (58) | 140528 | Completed | 1 | High | Electrical Wire Check | According to the electrical contractors label on the supply board the last fixed electrical wiring test of the common parts electrical wiring in this buildings was undertaken in January 2004. | Can it be confirmed with the TMO electrical engineer if the fixed wiring in the building has been retested in the last 5 years but no new label fixed to the supply board. If it has not been retested I would recommend that a fixed wiring test is undertaken on the common parts electrical wiring with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | block included in 14/15 communal testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-22 13:46 | 2014-05-13 13:48 | 2014-04-22 13:46 | 2014-05-13 17:04 | -21 | In target
58 ELM PARK GARDENS - 2014.04.15 | 2014-04-22 13:50 | S217001880026 | ELM PARK GARDENS (58) | 140530 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted in flats 1, 2 or 3 of this building. As flat 58A is a new conversion then domestic detectors would have been fitted as part of the conversion process. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | hard wired heat & smoke detectors will be fitted during PIR testing | 2014-05-12 | Fully Completed |  |  |  | 2014-04-22 13:50 | 2014-05-13 17:05
58 ELM PARK GARDENS - 2014.04.15 | 2014-04-22 13:53 | S217001880026 | ELM PARK GARDENS (58) | 140531 | Completed | 23a | High | Emergency Lighting | The emergency lighting system currently installed in the entrance hall and on the landings of the staircase does not appear on the electrical asset list as supplied by the TMO electrical engineer. | Is the installed emergency lighting system being serviced, tested and maintained? I would recommend that the TMO electrical engineer/electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not testing/servicing should be undertaken immediately and any defects etc rectified and the system with unit locations etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to asset register for inclusion in future servicing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-04-22 13:53 | 2014-05-13 13:54 | 2014-04-22 13:53 | 2014-05-13 17:06 | -21 | In target
6 ASHBURNHAM ROAD | 2013-12-31 14:35 | S217000190002 | ASHBURNHAM ROAD (6) | 122169 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flats A or C of this building, battery powered devices have been fitted in flat B by the London Fire Brigade. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat without detectors in accordance with the requirements of BS 5839 Part 6. | A & R Contract Management | Alex Bosman |  | Hard wired heat & smoke detectors fitted during PIR testing | 2014-04-22 | Fully Completed |  |  |  | 2013-12-31 14:35 | 2014-04-23 16:45
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:37 | S217009920001 | RUNCORN PLACE (6) | 102637 | Completed | 1a | High | Electrical Wire Check | There is no contractors label on the supply board or any other records to indicate when the last 5 year electrical fixed wiring test of this building. | Can it be confirmed by the TMO electrical engineer when the last 5 year electrical fixed wiring test of this building was undertaken? If it is overdue for testing I would recommend that a test is undertaken and any defects rectified or repaired as soon as possible. | A & R Contract Management | Alex Bosman | 2013-09-09 | Block included on the 13/14 testing program | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-19 15:37 | 2013-09-09 15:39 | 2013-08-19 15:37 | 2013-12-10 17:08 | -21 | In target
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:40 | S217009920001 | RUNCORN PLACE (6) | 102642 | Completed | 1b | High | Communal Lighting | One of the first floor level light covers has been painted over, the other light covers of the common parts of this building which are bulk head type lights are dirty. Thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the light unit which has the cover painted over is tested by an electrician to see if it works correctly and a replacement cover is fitted. Also I would recommend that the covers of the other lighting units in the staircase enclosure are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircase enclosure. Please also see item 15 below. | A & R Contract Management | Alex Bosman | 2013-09-09 | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-19 15:40 | 2013-09-09 15:41 | 2013-08-19 15:40 | 2015-04-14 10:06 | -21 | In target
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:46 | S217009920001 | RUNCORN PLACE (6) | 102647 | Completed | 15 | Medium | Emergency Lighting | It is not known if the bulk head type lights in this buildings staircase enclosure are also emergency lighting units. No neon indictor/ charging lights can be seen as the light covers are dirty. | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units. If it is found that there are emergency lighting units installed within the staircase of this building these should be tested and serviced immediately with a discharge test carried out. Any defects and/or problems highlighted as a result of this testing and servicing should be rectified. If it is found that none of the lighting units on the staircase are emergency lighting units then no actions are needed as this is a ground and first floor level building and emergency lighting would not be required. | A & R Contract Management | Alex Bosman | 2013-09-16 | Inspection complete. Report and costs to follow. | 2015-05-12 | Fully Completed | Janice Wray | 2013-08-19 15:46 | 2013-10-18 15:48 | 2013-08-19 15:46 | 2015-11-26 19:52 | -60 | In target
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:49 | S217009920001 | RUNCORN PLACE (6) | 102648 | Completed | 18 | Medium | Fire Extinguisher | There are small domestic type dry powder fire extinguishers in each flats kitchen area provided by RGE, it is not the TMOs policy to provide fire extinguishers for domestic dwellings. | It is my understanding that the 1.5 kg small domestic type dry powder fire extinguishers in each flats kitchen area provided by RGE are to be taken out. This is because residents cannot be given practical fire extinguisher training and it is TMO policy not to provide fire extinguishers within domestic dwellings. | A & R Contract Management | Alex Bosman | 2013-09-16 | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2013-08-19 15:49 | 2013-10-18 15:50 | 2013-08-19 15:49 | 2015-09-29 17:17 | -60 | In target
6 STANLEY GARDENS - 2013.05.01 | 2013-08-15 10:34 | S217010240001 | STANLEY GARDENS (6) | 101931 | Active | 15 | Low | Emergency Lighting | There is presently no emergency lighting installed in this building, on the landings of the staircase or in the entrance hall area ie the common parts of this building. The common parts of this building are five floors levels. | I would recommend that emergency lighting units are installed in the common parts ie the staircase enclosure of this building to provide illumination of the means of escape routes if the normal lighting fails. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman | 2014-02-14 | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2013-08-15 10:34 | 2014-02-11 10:45 | 2013-08-15 10:34 | 2015-11-27 09:53 | -180 | In target
62 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 12:48 | S217001880027 | ELM PARK GARDENS (62) | 200484 | Completed | 1 | High | Miscellaneous | The buildings electrical meters and landlords electrical supply boards etc were at the basement level, in what was is now flat 62C, these have now been brought up into the ground floor level cupboard by the rear exit door. | Can it please be confirmed that there are new electrical wiring and test certificates for the buildings electrical wiring etc after the relocation of the buildings electrical meters and landlords electrical supply boards etc from the basement level to the ground floor level cupboard by the rear exit door? If there are not then I would recommend that electrical certificates are obtained from the electrical company that undertook this electrical work. | A & R Contract Management | Alex Bosman |  | There is a current compliant certificate.Cert supplied | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-08 12:48 | 2015-06-29 13:16 | 2015-06-08 12:48 | 2015-12-02 11:02 | -21 | In target
62 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 13:25 | S217001880027 | ELM PARK GARDENS (62) | 200498 | Completed | 23 | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO SERVICING DOCUMENTATION IN KEYSTONE | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 28/07/2015 | 2015-07-28 | Fully Completed | Gillian Kennedy | 2015-06-08 13:25 | 2015-06-29 13:26 | 2015-06-08 13:25 | 2015-08-25 15:07 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:45 | S217002110008 | FINBOROUGH ROAD (62) | 102965 | Completed | 15a | High | Emergency Lighting | The covers of the emergency lighting units currently installed in the staircases of this building are dirty. | I would recommend that the covers of the emergency lighting units currently installed in the staircases of this building are cleaned or replaced to improve the illumination levels. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-20 16:45 | 2013-09-10 16:45 | 2013-08-20 16:45 | 2015-04-14 10:06 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:46 | S217002110008 | FINBOROUGH ROAD (62) | 102967 | Completed | 15b | Information Only | Emergency Lighting | There does not appear to be any emergency lighting units installed in the corridors of this building. These are enclosed internal corridors. The emergency lighting units currently installed in the staircase enclosures are old with dirty light covers etc, please see item 15a. | I would recommend that emergency lighting units are installed in the corridors and new ones maybe in the staircase enclosures of this building, the common parts. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Action entered into programme of work | 2015-11-19 | Fully Completed |  |  |  | 2013-08-20 16:46 | 2015-11-20 10:56
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:49 | S217002110008 | FINBOROUGH ROAD (62) | 102970 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to asset register for future inclusion in servicing program | 2014-05-12 | Fully Completed | Alex Bosman | 2013-08-20 16:49 | 2013-09-10 16:50 | 2013-08-20 16:49 | 2014-05-13 17:08 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:50 | S217002110008 | FINBOROUGH ROAD (62) | 102972 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training booked for 23rd &24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-20 16:50 | 2013-09-10 16:51 | 2013-08-20 16:50 | 2014-04-23 16:54 | -21 | In target
62 ST HELENS GARDENS - 2015.10.30 | 2015-11-16 14:20 | S217010100003 | ST HELENS GARDENS (62) | 227894 | Completed | 1 | High | Electrical Wire Check | There is no contractor's label on the landlords electrical supply/distribution board or on keystone to indicate when the last 5 year electrical fixed wiring test was carried out for the common parts electrical wiring of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | There is a current compliant certificate.Cert supplied | 2015-12-01 | Fully Completed | Maria Ares | 2015-11-16 14:20 | 2015-12-07 14:22 | 2015-11-16 14:20 | 2015-12-02 11:04 | -21 | In target
62 ST HELENS GARDENS - 2015.10.30 | 2015-11-16 14:43 | S217010100003 | ST HELENS GARDENS (62) | 227912 | Completed | 19 | High | Sprinklers | On the 1st floor level staircase landing there is the head of a water sprinkler system, I have seen within flat C and there is no sprinkler system installed within this flat, so this head must be part of a system installed within flat B. | Does the TMO know about this water sprinkler system head installed on the staircase landing and the possiblity of a water sprinkler system being installed within flat B? | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed annual servicing complete 23.11.15 | 2016-02-16 | Fully Completed | Maria Ares | 2015-11-16 14:43 | 2015-12-07 14:46 | 2015-11-16 14:43 | 2016-02-17 10:20 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:15 | S217002110002 | FINBOROUGH ROAD (63) | 189162 | Completed | 15 | Information Only | Emergency Lighting | As soon as financially possible There appears to be no emergency lighting installed in the internal corridors of this building, these corridors have no windows in them to allow natural light or borrowed light to illuminate these areas. There are self contained emergency lighting units installed on both of the staircase landings. | I would recommend that emergency lighting units are installed in the internal corridors of this building as soon as possible. This is provide illumination should be normal lighting fail. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Action entered into programme of work | 2015-11-19 | Fully Completed |  |  |  | 2015-03-20 15:15 | 2015-11-23 14:43 |  |  | 2015-03-20 15:15 | 2015-11-29 14:42 | Janice Wray
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:18 | S217002110002 | FINBOROUGH ROAD (63) | 189165 | Completed | 23a | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. Is this installed lightning protection system being serviced, tested and maintained in full working order? | I would recommend that the TMO engineer is asked if the installed lightning protection system on this building has been serviced, tested and maintained within the last year. If it has not, then testing and servicing should be undertaken immediately and any defects etc found rectified and then the system placed on the contractor's maintenance schedule for future annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA test complete Dec 15. | 2016-01-13 | Fully Completed | Maria Ares | 2015-03-20 15:18 | 2015-04-10 15:19 | 2015-03-20 15:18 | 2016-01-14 15:32 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:20 | S217002110002 | FINBOROUGH ROAD (63) | 189166 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings, the means of escape routes of this building and in the lower ground floor level electrical room. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 29/06/2015 | 2015-06-29 | Fully Completed | Gillian Kennedy | 2015-03-20 15:20 | 2015-04-10 15:21 | 2015-03-20 15:20 | 2015-08-25 15:08 | -21 | In target
65 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-03-23 17:01 | S217008660001 | ELGIN CRESCENT 65 (1-8) | 250866 | Active | 23 | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building, on the landings of the staircase and in the entrance hall area. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-04-20
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:33 | S217002110003 | FINBOROUGH ROAD (65) | 189127 | Completed | 15 | Information Only | Emergency Lighting | As soon as financially possible There appears to be no emergency lighting installed in the internal corridors of this building, these corridors have no windows in them to allow natural light or borrowed light to illuminate these areas. There are self contained emergency lighting units installed on both of the staircase landings. | I would recommend that emergency lighting units are installed in the internal corridors of this building as soon as possible. This is provide illumination should be normal lighting fail. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Action entered into programme of work | 2015-11-19 | Fully Completed |  |  |  | 2015-03-20 14:33 | 2015-11-23 14:38 |  |  | 2015-03-20 14:33 | 2015-11-29 14:37 | Janice Wray
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:37 | S217002110003 | FINBOROUGH ROAD (65) | 189134 | Completed | 23a | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. | Is this installed lightning protection system being serviced, tested and maintained in full working order? I would recommend that the TMO engineer is asked if the installed lightning protection system on this building has been serviced, tested and maintained within the last year. If it has not, then testing and servicing should be undertaken immediately and any defects etc found rectified and then the system placed on the contractor's maintenance schedule for future annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA test complete Dec 15. | 2016-01-13 | Fully Completed | Maria Ares | 2015-03-20 14:37 | 2015-04-10 14:38 | 2015-03-20 14:37 | 2016-01-14 15:33 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:38 | S217002110003 | FINBOROUGH ROAD (65) | 189136 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings, the means of escape routes of this building and in the lower ground floor level electrical room. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Complete 30.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-03-20 14:38 | 2015-04-10 14:39 | 2015-03-20 14:38 | 2015-12-15 10:45 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 13:42 | S217001880006 | ELM PARK GARDENS (67) | 102513 | Completed | 17 | Low | Smoke Alarms | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I would recommend that a copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders is delivered to each flat in this building. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | A & R Contract Management | Alex Bosman | 2014-02-03 | Properties are included in 10 year PIR program which includes instillation of hardwired fire alarms | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 13:42 | 2014-02-15 13:44 | 2013-08-19 13:42 | 2013-10-02 17:08 | -180 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 13:45 | S217001880006 | ELM PARK GARDENS (67) | 102519 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircases, on the flat/lift lobby areas, in the storage areas and in the roof level areas of this building do not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-09 | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 13:45 | 2013-09-09 13:50 | 2013-08-19 13:45 | 2013-10-02 17:09 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 14:00 | S217001880006 | ELM PARK GARDENS (67) | 102541 | Active | 23c | High | Sprinklers | Are the weekly occupier's inspections of the installed sprinkler system being undertaken? | Weekly occupier inspections of the as installed sprinkler system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | A & R Contract Management | Alex Bosman | 2013-09-09 |  |  |  | Alex Bosman | 2013-08-19 14:00 | 2013-09-09 14:03 |  |  | 940 | 940 days overdue
68 ELM PARK GARDENS - 2015.07.16 | 2015-09-01 11:02 | S217001880028 | ELM PARK GARDENS (68) | 214266 | Completed | 23a | High | Fire Extinguisher | There is a carbon dioxide fire extinguisher located in the 5th floor level lift motor room and also one in the basement electrical cupboard. Both of these fire extinguishers are out of test date according to the contractors servicing label attached to it, the last test date according to the servicing labels was the 19th March 2013 for the lift motor room one and January 2014 for the other one. | These portable fire extinguishers in this building should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | completed 20.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-01 11:02 | 2015-09-22 11:07 | 2015-09-01 11:02 | 2015-11-20 10:59 | -21 | In target
68 ELM PARK GARDENS - 2015.07.16 | 2015-09-01 11:07 | S217001880028 | ELM PARK GARDENS (68) | 214268 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings, in the entrance hall area and in the lift motor and water tank rooms of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - last servicing referred to is by RGE in Jan 2013 but no documentation stored | A & R Contract Management | Alex Bosman |  | completed 28.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-09-01 11:07 | 2015-09-22 11:09 | 2015-09-01 11:07 | 2015-11-20 11:08 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:12 | S217010200001 | ST QUINTIN AVENUE (69) | 199063 | Completed | 1a | High | Dry or Wet Riser | There is no contractor's label on the buildings landlords electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the landlords/common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. No info on Keystone curently | A & R Contract Management | Alex Bosman |  | compliant cert issued and labelling present | 2015-11-17 | Fully Completed | Maria Ares | 2015-05-28 11:12 | 2015-06-18 11:13 | 2015-05-28 11:12 | 2015-11-18 13:14 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:21 | S217010200001 | ST QUINTIN AVENUE (69) | 199071 | Completed | 18 | High | Fire Extinguisher | There is portable fire fighting equipment provided in the common parts of this building. As there are no employees in the building only residents, the portable fire fighting equipment could be removed as training cannot be given to residents to use the extinguishers. | The portable fire fighting equipment in the common parts of this building could be removed. As the residents cannot be given training to use the extinguishers. I would recommend that the fire extinguisher in the lift motor room remains but the one in the external electrical room could also be removed. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-05-28 11:21 | 2015-06-18 11:26 | 2015-05-28 11:21 | 2015-12-02 11:07 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:26 | S217010200001 | ST QUINTIN AVENUE (69) | 199072 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase landings, in the entrance hall/lobby area and also a unit in the electrical cupboard/room. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? No info on Keystone so unable to confirm that this is on Asset Register | A & R Contract Management | Alex Bosman |  | AP confirmed service complete; further works required to provide separate isolation of EL to intercom for future servicing | 2015-12-14 | Fully Completed | Maria Ares | 2015-05-28 11:26 | 2015-06-18 11:27 | 2015-05-28 11:26 | 2015-12-15 10:46 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:32 | S217010200001 | ST QUINTIN AVENUE (69) | 199075 | Completed | 23c | High | Fire Extinguisher | The portable fire extinguishers located in this building are out of test date according to the contractors servicing labels attached to them, the last test date according to the service labels was July 2013. | All the portable fire extinguishers in the building should be serviced immediately and it confirmed that they are on the external contractors maintenance schedule. Alternatively please see item 18 above, all the portable fire extinguishers on the staircase landings could be removed from the building and not replaced. The carbon dioxide extinguisher in the roof level lift motor room is required though. Could the extinguishers on the plant areas be serviced asap and those in the communal landings be removed | A & R Contract Management | Alex Bosman |  | completed 31.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-28 11:32 | 2015-06-18 11:33 | 2015-05-28 11:32 | 2015-11-20 11:10 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:27 | S217001880003 | ELM PARK GARDENS (7) | 102457 | Completed | 15 | High | Emergency Lighting | It appears that there is no emergency lighting unit installed in the roof level left hand side lift motor room. No neon charging lights can be seen on the normal light fittings installed in this room. The neon charging lights are clearly visible on similar other light fittings in this building. | I would recommend that a check is undertaken of the light units to see if they are combined emergency /normal lighting units. If they are not emergency lighting units then I would recommend that a self contained emergency lighting unit is installed in this room. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. | A & R Contract Management | Alex Bosman |  | Order raised with RGE to carry out instilation | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-19 12:27 | 2013-09-09 12:31 | 2013-08-19 12:27 | 2013-12-10 17:43 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:32 | S217001880003 | ELM PARK GARDENS (7) | 102459 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I would recommend that a copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders is delivered to each flat in this building. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | A & R Contract Management | Alex Bosman |  | Properties included in 10 year PIR program which includes instillation of hardwired fire alarms | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 12:32 | 2014-02-15 12:35 | 2013-08-19 12:32 | 2013-10-02 17:02 | -180 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:36 | S217001880003 | ELM PARK GARDENS (7) | 102461 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircases, on the flat/lift lobby areas, the storage areas and in the roof level areas of this building do not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 12:36 | 2013-09-09 12:36 | 2013-08-19 12:36 | 2013-10-02 17:04 | -21 | In target
70 PHILBEACH GARDENS - 2014.05.01 | 2014-05-13 13:41 | S217006630004 | PHILBEACH GARDENS (70) | 143509 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all of the flats in this building, hardwired detector/sounders are installed in flat 6 and battery powered ones were fitted within flat 4. Copies of the new LFB leaflet on fitting domestic fire alarm detectors/sounders were left for the residents of this building. The residents can contact the LFB if they want to and arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | Are these flats on the electrical inspection programme? | A & R Contract Management | Alex Bosman |  | Hard wired detectors installed during PIR testing. all properties included on program | 2014-07-14 | Fully Completed |  |  |  | 2014-05-13 13:41 | 2014-07-15 15:49
70 PHILBEACH GARDENS - 2014.05.01 | 2014-05-13 13:43 | S217006630004 | PHILBEACH GARDENS (70) | 143510 | Completed | 23a | High | Emergency Lighting | The emergency lighting units installed in the entrance hall area and on the staircase landings of this building do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting unit being serviced, tested and maintained? | Can it please be confirmed that the emergency lighting units installed in the entrance hall/lobby area of this building and on the staircase landings are being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2016-01-13 | AP confirmed complete 4.12.2015 | 2016-01-13 | Fully Completed | Maria Ares | 2014-05-13 13:43 | 2014-06-03 13:44 | 2014-05-13 13:43 | 2016-01-14 15:34 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:00 | S217010350001 | TAVISTOCK ROAD (70-80) | 104374 | Completed | 1b | High | Electrical Wire Check | It is not known if the washing machines and tumble dryers in the laundry are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 12:00 | 2013-09-23 12:01 | 2013-09-02 12:00 | 2015-02-27 12:16 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:36 | S217010350001 | TAVISTOCK ROAD (70-80) | 104394 | Completed | 1f | High | Electrical Wire Check | If any work is undertaken by the electrical contractors working in this building on the communal electrical wiring then new electrical test certificate must be issued where this electrical has been carried out. | Obtain new electrical test certificates for any work undertaken on the communal areas electrical wiring by the electrical contractors. | A & R Contract Management | Alex Bosman |  | block included on 14/15 communal testing program | 2014-04-22 | Fully Completed | Alex Bosman | 2013-09-02 12:36 | 2013-09-23 12:38 | 2013-09-02 12:36 | 2014-04-23 16:53 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:40 | S217010350001 | TAVISTOCK ROAD (70-80) | 104401 | Completed | 5 | High | Standby Generator | This building has a stand by diesel generator which is used to power some of the electrical system in this building in the event of a mains electrical power cut. The last service date was the 28th March 2013. | The contractors label on the control panel states that the last service was on the 28th March 2013 but the service book for the generator has not been filled in since 2011. I believe that stand by generators should be run under load on a monthly basis. 1. Can it be confirmed that servicing and maintenance etc is being undertaken in accordance with the manufactures recommendations? 2. Could the reason for the logbook not being filled in please be explained? 3. I would recommend that a list of the electrical circuits that the stand by generator powers when running is kept on site. | A & R Contract Management | Alex Bosman |  | Confirmed that standby genorators are no longer required as all systems have battery back up. Genorators to be removed 2015/16 | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 12:40 | 2013-09-23 12:42 | 2013-09-02 12:40 | 2015-02-27 20:22 | -21 | In target | 2013-09-02 12:40 | 2015-03-05 20:21 | Janice Wray
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:43 | S217010336601 | TAVISTOCK CRESCENT PARKING | 104402 | Completed | 7 | High | Lightning Protection | There is a lightning protection system installed on this building, according to the records provided to me this system is tested on an annual basis. There is presently work being undertaken on the roof of this building which will affect the lightning protection system. | Once the roofing work is completed will the roofing contractor be certifying that the installed lightning protection system on this building is fully functional again? 1. I would recommend that the contractor is asked if his workers are competent and qualified to work on lightning protection system? 2. If they are not a specialist company should be contracted to do this work. 3. New installation and test certificates in accordance with the British Standards should be provided. | A & R Contract Management | Alex Bosman |  | tested 3.8.2015 passed. (70 Tavistock road) | 2015-12-01 | Fully Completed | Maria Ares | 2013-09-02 12:43 | 2013-09-23 12:44 | 2013-09-02 12:43 | 2015-12-02 11:44 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 13:23 | S217010350001 | TAVISTOCK ROAD (70-80) | 104425 | Active | 15 | High |  | The presently installed new emergency lighting system/units in this building are being replaced on a like for like basis. The coverage of the installed emergency lighting system is not to the current British Standard. | As all of the emergency lighting units in this building are being replaced, this is a new system, so therefore should met the requirements of the current British Standard. I would recommend that a full survey of the as installed emergency escape lighting system in this building is undertaken. This should then be compared to the requirements of BS 5266 Part 1 2011 and the risk assessment section and then any deficiencies or lack of coverage then rectified. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2013-09-02 13:23 | 2013-09-23 13:24 |  |  | 926 | 926 days overdue
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 15:54 | S217010350001 | TAVISTOCK ROAD (70-80) | 104470 | Completed | 17a | High | Fire Alarm | Work was completed on the fire alarm and warning system in this building in June of this year. It appears that this replacement system will is not to the L2 standard as required by the current British Standard. | I would recommend that a full survey of the as installed fire alarm system in this building is undertaken. This should then be compared to the requirements of BS 5839 Part 1 and any deficiencies or lack of coverage then rectified. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 15:54 | 2013-09-23 15:56 | 2013-09-02 15:54 | 2015-02-27 12:19 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 15:56 | S217010350001 | TAVISTOCK ROAD (70-80) | 104471 | Completed | 17b | High | Fire Alarm | Work was undertaken in the new kitchen area and new devices of this buildings fire alarm and warning system were installed including a hold open device on the kitchen door. | Can it please be confirmed that the building Control Officer is happy with the installation of an electro magnetic hold open device on a kitchen door with a heat detector installed in the kitchen. I would recommend that his written acceptance of this arrangement is placed in the premise file so if this building is audited under the Fire Safety Order that the fire officer can see this documentation. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 15:56 | 2013-09-23 15:58 | 2013-09-02 15:56 | 2015-02-27 12:21 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 15:58 | S217010350001 | TAVISTOCK ROAD (70-80) | 104473 | Completed | 17C | High | Fire Alarm | The installed new fire alarm and warning system in this building, the system as it extends into the flats. There are very old heat detectors in some of the kitchens of the flats in this building and in one flat the detector is hanging off the ceiling by its wires. | Can it please be explained why the very old heat detectors in some of the kitchens of the flats in this building have not been replaced and in other ones detectors not fitted correctly. | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 15:58 | 2013-09-23 15:59 | 2013-09-02 15:58 | 2015-02-27 12:25 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 15:59 | S217010350001 | TAVISTOCK ROAD (70-80) | 104474 | Completed | 17d | High | Fire Alarm | The installed new fire alarm and warning system in this building there are old devices from the previous fire alarm system still installed in this building. | I would recommend that all the old devices from the previously installed fire alarm system are removed, the detectors in the water tank room and the device over the fire alarm control panel. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 15:59 | 2013-09-23 16:00 | 2013-09-02 15:59 | 2015-05-12 16:42 | -21 | In target | 2013-09-02 15:59 | 2015-03-05 20:27 | Gillian Kennedy
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:01 | S217010350001 | TAVISTOCK ROAD (70-80) | 104475 | Completed | 17e | High | Smoke Alarms | There are wall mounted smoke detectors in the 1st floor level corridor. | Can the contractor please provide documentation, a variation certificate for these devices and confirm that these devices are in accordance with the current British Standard for siting and distance etc. | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:01 | 2013-09-23 16:02 | 2013-09-02 16:01 | 2015-02-27 12:26 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:02 | S217010350001 | TAVISTOCK ROAD (70-80) | 104477 | Completed | 17f | High | Fire Alarm | The installed new fire alarm and warning system in this building. | Can the contractor provide the marked up drawings showing the audibility levels for each room, area, flat as required by the British Standard. | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:02 | 2013-09-23 16:03 | 2013-09-02 16:02 | 2015-02-27 12:27 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:05 | S217010350001 | TAVISTOCK ROAD (70-80) | 104482 | Completed | 17g | High | Fire Alarm | The installed new fire alarm and warning system in this building. | I would recommend that the premises file is checked to see if the installation and completion certificates as required by BS 5839 Part 1 are located there. If they are not the contactor who installed the system should be asked to provide them. | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:05 | 2013-09-23 16:06 | 2013-09-02 16:05 | 2015-02-27 12:28 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:06 | S217010350001 | TAVISTOCK ROAD (70-80) | 104483 | Completed | 17h | High | Fire Alarm | The installed new fire alarm and warning system in this building. | There is no layout drawing/plan next to the fire alarm control panel showing the layout of the installed fire alarm system. | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:06 | 2013-09-23 16:07 | 2013-09-02 16:06 | 2015-02-27 12:29 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:08 | S217010350001 | TAVISTOCK ROAD (70-80) | 104484 | Completed | 17i | High | Fire Alarm | The installed new fire alarm and warning system in this building. There are louvered vents on each floor level of this building by the main staircase, it is not known if these are interfaced with the buildings fire alarm system. | Are these louvered vents on each floor level by the main staircase of this building interfaced with the buildings fire alarm system? Are there any other systems interfaced with the buildings fire alarm system? | A & R Contract Management | Alex Bosman |  | Works Complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:08 | 2013-09-23 16:09 | 2013-09-02 16:08 | 2015-02-27 12:30 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:12 | S217010350001 | TAVISTOCK ROAD (70-80) | 104489 | Completed | 17k | High | Smoke Alarms | There appear to be domestic BS 5839 Part 6 smoke detectors in the corridors of this building. | The domestic BS 5839 Part 6 smoke detectors in the corridors of this building should be removed. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-02 16:12 | 2013-09-23 16:13 | 2013-09-02 16:12 | 2015-02-27 14:40 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:16 | S217010350001 | TAVISTOCK ROAD (70-80) | 104495 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed in this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Inspection complete (May 2015). Report and costs to follow. | 2015-05-12 | Fully Completed | Janice Wray | 2013-09-02 16:16 | 2013-09-23 16:17 | 2013-09-02 16:16 | 2015-11-26 17:03 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:17 | S217010350001 | TAVISTOCK ROAD (70-80) | 104497 | Completed | 23c | High | Emergency Lighting | 23c High There are no records of the monthly occupiers tests and inspections of the emergency lighting system, fire extinguishers etc , these tests are being undertaken by the caretaker according to the manager. | Can it be confirmed that all the monthly occupiers tests and inspections are being undertaken as per the caretakers checklist? | A & R Contract Management | Alex Bosman |  | ESA training completed - ongoing refreshers to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-09-02 16:17 | 2013-09-23 16:19 | 2013-09-02 16:17 | 2014-07-15 16:57 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:21 | S217010350001 | TAVISTOCK ROAD (70-80) | 104502 | Active | 23e | High | Miscellaneous | There is a ventilation system installed in the lift lobby area of this building. | Is this ventilation system being serviced, tested and maintained in according to the manufactures guidance? If it is not then testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Report received from RMA Stewarts | 2015-09-28 | Partially Completed | Gillian Kennedy | 2013-09-02 16:21 | 2013-09-23 16:22 | 2013-09-02 16:21 | 2015-09-29 17:19 | -21 | In target | 2013-09-02 16:21 | 2015-10-07 12:19 | Maria Ares
74 ELM PARK GARDENS - 2015.07.16 | 2015-09-02 11:31 | S217001880029 | ELM PARK GARDENS (74) | 214484 | Completed | 15a | High | Emergency Lighting | A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area as well as in the ladder area of the roof level lift motor and water tank rooms. But the old emergency lighting units are still installed in the lift motor room and in the water tank room. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and the water tank room were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | RMA confirmed all works complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-02 11:31 | 2015-09-23 11:32 | 2015-09-02 11:31 | 2015-12-15 10:47 | -21 | In target
74 ELM PARK GARDENS - 2015.07.16 | 2015-09-02 11:33 | S217001880029 | ELM PARK GARDENS (74) | 214485 | Completed | 15b & 23b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. Please can it confirmed that this has been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-09-02 11:33 | 2015-09-23 11:34 | 2015-09-02 11:33 | 2015-11-18 13:18 | -21 | In target
74 ELM PARK GARDENS - 2015.07.16 | 2015-09-02 11:34 | S217001880029 | ELM PARK GARDENS (74) | 214486 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-02 11:34 | 2015-09-23 11:37 | 2015-09-02 11:34 | 2015-12-02 11:48 | -21 | In target
79 - 94 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 09:02 | S217000830006 | CHELSEA MANOR COURT 79-94 | 207293 | Completed | 15 | High | Emergency Lighting | As soon as financially possible There is presently no emergency escape lighting installed in this building on the external walkways/balconies and on the staircase landings. This is a 5 storey building. | I would recommend that as soon as financially possible consideration is given to fitting emergency escape lighting on the means of escape routes of this building. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Already included within a programme of work | 2015-11-19 | Fully Completed | Maria Ares | 2015-07-17 09:02 | 2015-08-07 09:04 | 2015-07-17 09:02 | 2015-11-23 16:23 | -21 | In target | 2015-07-17 09:02 | 2015-11-29 16:22 | Janice Wray
8 ASHBURNHAM ROAD - 2013.9.30 | 2013-10-10 15:28 | S217000190003 | ASHBURNHAM ROAD (8) | 110148 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flats A or C of this building, but none are fitted within flat B. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat without detectors in accordance with the requirements of BS 5839 Part 6. | A & R Contract Management | Alex Bosman |  | hard wired heat & smoke detectors to be fitted during PIR testing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-10-10 15:28 | 2014-04-08 15:30 | 2013-10-10 15:28 | 2014-04-23 16:55 | -180 | In target
8 DAMER TERRACE - 2014.08.14 | 2014-08-22 12:00 | S217001400005 | DAMER TERRACE (8) | 158509 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution boards and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building or for the tenanted flat. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of this building were last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. Also when was the fixed wiring for flat A last undertaken please this should have been within the last 10 years. | A & R Contract Management | Alex Bosman |  | 18/08/2014 - Completed - Certificate held in keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-08-22 12:00 | 2014-09-12 12:03 | 2014-08-22 12:00 | 2015-08-25 16:27 | -21 | In target
8 DAMER TERRACE - 2014.08.14 | 2014-08-22 12:06 | S217001400005 | DAMER TERRACE (8) | 158515 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within flat A of this building, hardwired detector/sounders are installed in flat B. | A copy of the new LFB leaflet on fitting domestic fire alarm detectors/sounders was left for the occupants of flat A. The resident can contact the LFB if they want to and arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | A & R Contract Management | Alex Bosman |  | Hard wired detectors to be installed during 5 year PIR testing program | 2015-03-23 | Fully Completed |  |  |  | 2014-08-22 12:06 | 2015-03-24 16:59
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 15:01 | S217002110009 | FINBOROUGH ROAD (80) | 122196 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building, but none were fitted within flat 3. | Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building and one given to the occupant of flat 3. The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2004. | A & R Contract Management | Alex Bosman |  | Hard wired heat & smoke detectors to be fitted during PIR testing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-12-31 15:01 | 2014-06-29 15:02 | 2013-12-31 15:01 | 2014-04-23 16:56 | -180 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 15:02 | S217002110009 | FINBOROUGH ROAD (80) | 122197 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircase and in the entrance hall area of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to asset register for servicing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-12-31 15:02 | 2014-01-21 15:03 | 2013-12-31 15:02 | 2014-04-23 16:59 | -21 | In target
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 10:56 | S217002110010 | FINBOROUGH ROAD (82) | 239727 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, in the entrance hall area and on the staircase landing. Also in the electrical room. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-25
82 REDCLIFFE SQUARE, LONDON SW10 9BL - 2015.11.30 | 2016-01-28 12:23 | S217004540001 | REDCLIFFE SQUARE 82 A-E | 240036 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, in the entrance hall area and on each of the staircase landing. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-26
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 09:41 | S217010567703 | LONGLANDS COURT (82-87) | 103414 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | block included in 14/15 communal testing program | 2014-04-22 | Fully Completed | Alex Bosman | 2013-08-23 09:41 | 2013-09-13 09:58 | 2013-08-23 09:41 | 2014-04-23 17:00 | -21 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 09:58 | S217010567703 | LONGLANDS COURT (82-87) | 103423 | Completed | 7 | Medium | Lightning Protection | From what I can see there is no lightning protection system installed on this building, but the asset list given to me by the TMO electrical engineer states that there is a lightning protection system fitted and that this system is tested and serviced on a planned preventive maintenance schedule by an external contractor. | Can it be confirmed by a suitably qualified person if there is a lightning protection system installed on this building? If there is no further action needs to be taken except confirm that any testing and servicing is being undertaken. If there is no system fitted I would recommend that the asset register is amended and the external contractor informed. | A & R Contract Management | Alex Bosman |  | we confirm the presence of the lightning protection and a compliant cert | 2015-11-17 | Fully Completed | Maria Ares | 2013-08-23 09:58 | 2013-10-22 09:59 | 2013-08-23 09:58 | 2015-11-18 13:22 | -60 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:07 | S217010567703 | LONGLANDS COURT (82-87) | 103430 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Automatic domestic detection was fitted within flat 86. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | hard wired heat & smoke detectors fitted during PIR testing | 2014-04-22 | Fully Completed |  |  |  | 2013-08-23 10:07 | 2014-04-23 17:01
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:09 | S217010567703 | LONGLANDS COURT (82-87) | 103431 | Completed | 23a | High | Emergency Lighting | The emergency lighting system currently installed in the staircase enclosure of the building and covering the lower ground floor level areas does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | added to asset register for service | 2014-04-22 | Fully Completed | Alex Bosman | 2013-08-23 10:09 | 2013-09-13 10:10 | 2013-08-23 10:09 | 2014-04-23 17:02 | -21 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:10 | S217010567703 | LONGLANDS COURT (82-87) | 103433 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-23 10:10 | 2013-09-13 10:11 | 2013-08-23 10:10 | 2014-04-23 17:02 | -21 | In target
84 EDITH GROVE - 2015.11.11 | 2015-11-16 14:52 | S217001780004 | EDITH GROVE (84) | 227915 | Completed | 4 | High | Miscellaneous | The gas meters for the individual apartments are wall mounted and located in the basement lobby area outside of the basement flats entrance door, near to the electrical meters. The Building Regulations states that "Gas services, installations or meters should not be incorporated within a protected staircase/route unless the gas installation is in accordance with the Gas Safety (Installation and Use) Regulations 1998. | Can it be confirmed that the wall mounted gas meters located in the entrance hall area of this building comply with the requirements of the Gas Safety (Installation and Use) Regulations 1998. Have there been any comments about the gas and electrical meters being located next to each other by the contractors undertaking the buildings annual gas safety checks? | A & R Contract Management | Alex Bosman |  | Current regualtion is not retrospective. Meters can remain in current location. | 2015-12-14 | Fully Completed | Maria Ares | 2015-11-16 14:52 | 2015-12-07 14:54 | 2015-11-16 14:52 | 2015-12-15 10:47 | -21 | In target
84 REDCLIFFE SQUARE, LONDON SW10 9BL - 2015.11.30 | 2016-01-28 12:50 | S217004540002 | REDCLIFFE SQUARE 84 A-F | 240049 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, in the entrance hall area and on each of the staircase landing. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-26
85 LADBROKE GROVE, LONDON W10 2HB - 2015.11.03 | 2016-01-25 16:14 | S217009120005 | LADBROKE GROVE (85) | 239419 | Active | 23a | High | Emergency Lighting | There are emergency lighting units/system installed in this building, in the entrance hall area and on the landings of the staircase. Keystone has been checked and there are no records of any annual emergency lighting servicing by any contractors and the TMO's asset register do not show any emergency lighting installed within this building. | It must be assumed that the installed emergency lighting system/units in this building has not been serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. A test/service of the installed emergency lighting system should undertaken immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Records should be kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-22
86 ELM PARK GARDENS - 2015.06.10 | 2015-06-15 10:55 | S217001880031 | ELM PARK GARDENS (86) | 201461 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed and have been replaced with just pendant lights. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-15 10:55 | 2015-07-06 10:56 | 2015-06-15 10:55 | 2015-12-15 10:49 | -21 | In target
86 ELM PARK GARDENS - 2015.06.10 | 2015-06-15 10:57 | S217001880031 | ELM PARK GARDENS (86) | 201462 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide and dry powder fire extinguishers located in the lift motor room and the boiler room of this building are out of service/test date according to the contractors servicing labels attached to them. The last test date on these RGE service labels was July 2013. | These portable fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 10:57 | 2015-07-06 10:58 | 2015-06-15 10:57 | 2015-12-02 13:15 | -21 | In target
86 ELM PARK GARDENS - 2015.06.10 | 2015-06-15 10:58 | S217001880031 | ELM PARK GARDENS (86) | 201464 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 18.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-15 10:58 | 2015-07-06 10:59 | 2015-06-15 10:58 | 2015-11-27 09:58 | -21 | In target
86 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:25 | S217002110012 | FINBOROUGH ROAD (86) | 239752 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, in the entrance hall area and on the staircase landing. Also in the electrical room. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be confirmed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-25
88 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:31 | S217002110013 | FINBOROUGH ROAD (88) | 239758 | Active | 23a | High | Emergency Lighting | There are emergency escape lighting units installed in this building, in the entrance hall area and on the staircase landing. Also in the electrical room. Are the installed emergency lighting units being serviced, tested and maintained? Keystone checked. | Can it please be conformed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-02-25
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:15 | S217010567704 | LONGLANDS COURT (88-93) | 103105 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-21 14:15 | 2013-09-11 14:17 | 2013-08-21 14:15 | 2014-03-21 17:01 | -21 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:33 | S217010567704 | LONGLANDS COURT (88-93) | 103112 | Completed | 7 | Medium | Lightning Protection | From what I can see there is no lightning protection system installed on this building, but the asset list given to me by the TMO electrical engineer states that there is a lightning protection system fitted and that this system is tested and serviced on a planned preventive maintenance schedule by an external contractor. | Can it be confirmed by a suitably qualified person if there is a lightning protection system installed on this building? If there is no further action needs to be taken except confirm that any testing and servicing is being undertaken. If there is no system fitted I would recommend that the asset register is amended and the external contractor informed. | A & R Contract Management | Alex Bosman |  | Site to be included in 13/14 testing program and asset register to be updated as required following visit | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-21 14:33 | 2013-10-20 14:34 | 2013-08-21 14:33 | 2013-12-10 17:49 | -60 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:37 | S217010567704 | LONGLANDS COURT (88-93) | 103115 | Completed | 12a | High | Flat Door | The entrance door to flat 93 appears to have recently been changed from the originally fitted door, because the door has not been stained or painted in anyway. | Can it be confirmed that this flats entrance door is a 30 minute fire rated door fitted with a self closing device capable of shutting the door fully on to its stops. | A & R Contract Management | Alex Bosman |  | Asked Carl Stokes to assess & report back. Tenant's name and contact details provided - 2nd Jan 2014 - but dewspite repeated attempts at access none forthcoming, therefore, order - 201544328 - raised for replacement self closing FD30 door on 26th Nov 2015 | 2015-12-02 | Fully Completed | Janice Wray | 2013-08-21 14:37 | 2013-09-11 14:40 | 2013-08-21 14:37 | 2015-12-03 20:16 | -21 | In target | 2013-08-21 14:37 | 2015-12-03 16:35 | Janice Wray
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:42 | S217010567704 | LONGLANDS COURT (88-93) | 103117 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | included in 14/15 inspection program | 2014-03-20 | Fully Completed |  |  |  | 2013-08-21 14:42 | 2014-03-24 13:06 |  |  | 2013-08-21 14:42 | 2014-03-28 13:05 | Janice Wray
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:44 | S217010567704 | LONGLANDS COURT (88-93) | 103118 | Completed | 23a | High | Emergency Lighting | 23a High Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-21 14:44 | 2013-09-11 14:45 | 2013-08-21 14:44 | 2014-04-23 17:03 | -21 | In target
9 COLVILLE SQUARE, LONDON W11 2BD - 2016.02.02 | 2016-02-19 16:33 | S217008450001 | COLVILLE SQUARE (9) | 244698 | Active | 23 | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building, on the landings of the staircase and in the entrance hall area. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-21
92 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 11:30 | S217001880032 | ELM PARK GARDENS (92) | 201479 | Completed | 15a | High | Emergency Lighting | 1A new emergency lighting system has been installed in this building, on the staircase landings and in the entrance hall area. But the old emergency lighting units are still installed in the lift motor. | Can it please be confirmed that the presently installed emergency lighting units in the lift motor room and roof space area were tested and checked as being fully functional as part of the design criteria for the installation of the new emergency lighting system? Is there a written record of these checks and the results of them? | A & R Contract Management | Alex Bosman |  | lighting present and working correctly | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-15 11:30 | 2015-07-06 11:31 | 2015-06-15 11:30 | 2015-11-18 13:20 | -21 | In target
92 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 11:39 | S217001880032 | ELM PARK GARDENS (92) | 201480 | Completed | 15b | High | Emergency Lighting | A new emergency lighting system has been installed in this building. | Installation and/or commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | CERTIFICATES SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-15 11:39 | 2015-07-06 11:41 | 2015-06-15 11:39 | 2015-11-18 13:23 | -21 | In target
92 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 11:41 | S217001880032 | ELM PARK GARDENS (92) | 201482 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-15 11:41 | 2015-07-06 11:42 | 2015-06-15 11:41 | 2015-12-02 13:19 | -21 | In target
92 ELM PARK GARDENS - 2015.06.11 | 2015-06-15 11:43 | S217001880032 | ELM PARK GARDENS (92) | 201483 | Completed | 23b | High | Emergency Lighting | There is a new emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Please can it confirmed that the newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this emergency lighting system? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 18.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-15 11:43 | 2015-07-06 11:44 | 2015-06-15 11:43 | 2015-11-27 09:59 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:10 | S217001880008 | ELM PARK GARDENS (93) | 102490 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I would recommend that a copy of the LFB leaflet on fitting domestic fire alarm detectors/sounders is delivered to each flat in this building. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB. | A & R Contract Management | Alex Bosman |  | Properties included in 10 year PIR program which includes instillation of hardwired fire alarms | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 13:10 | 2014-02-15 13:11 | 2013-08-19 13:10 | 2013-10-02 17:06 | -180 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:12 | S217001880008 | ELM PARK GARDENS (93) | 102493 | Completed | 18 | Information Only | Fire Extinguisher | There is a carbon dioxide fire extinguishers provided in each of the 4 ground floor level riser cupboards, two cupboards in each part of the building. It is the TMO policy not to have fire extinguishers locked away in very small riser cupboards. | I would recommend that these carbon dioxide fire extinguishers are removed from these ground floor riser cupboards. | A & R Contract Management | Alex Bosman | [7 empty] | 2013-08-19 13:12 | 2013-10-02 17:06
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:14 | S217001880008 | ELM PARK GARDENS (93) | 102495 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the landings of the staircases, on the flat/lift lobby areas, the storage areas and in the roof level areas of this building do not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 13:14 | 2013-09-09 13:15 | 2013-08-19 13:14 | 2013-10-02 17:07 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:16 | S217001880008 | ELM PARK GARDENS (93) | 102496 | Completed | 23b | High | Fire Extinguisher | The carbon dioxide portable fire extinguishers located in the four ground floor riser cupboards are out of test date according to the servicing labels attached to them. The last test dates being March 2009. | The carbon dioxide portable fire extinguishers located in the four ground floor level riser cupboards should be serviced immediately and it confirmed that they are on the external contractors maintenance schedule. Alternatively they could be removed from the building and not serviced etc or replaced, the external contractor's maintenance schedule should be amended to show this change. | A & R Contract Management | Alex Bosman |  | Added to RGE asset register to be included in service program | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-19 13:16 | 2013-09-09 13:17 | 2013-08-19 13:16 | 2013-12-10 17:41 | -21 | In target
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 10:13 | S217009120002 | LADBROKE GROVE (94) | 101648 | Completed | 1 | High | Communal Lighting | The covers of the lighting units in the common parts of the building are dirty, thus affecting the level of illumination from the bulb of the light unit. Please also see item 15 below reference any emergency lighting within this building. | I would recommend that the covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircase | A & R Contract Management | Alex Bosman | 2013-09-04 | Lights previously cleaned, currently non emergency fitings. qoute requested from RGE to upgrade to emergency fittings | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-14 10:13 | 2013-09-04 11:20 | 2013-08-14 10:13 | 2013-12-10 17:28 | -21 | In target
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 15:04 | S217009120002 | LADBROKE GROVE (94) | 101769 | Completed | 15 | Medium | Emergency Lighting | It is not known if any emergency lighting is installed on the landings of the staircase of this building, ie the common parts of this building. There are bulkhead type lighting units in the building which are similar to emergency lighting units, but the lighting units covers are dirty and no neon indicator/charging lights can be seen. | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units. If any emergency lighting units are found to be installed within this building or externally these should be tested and serviced immediately with a discharge test carried out. Any defects and/or problems highlighted as a result of this testing and servicing should be rectified. If it is found that there are no emergency lighting units installed within the common parts of this building I would recommend that if work is undertaken on the lighting circuit or the lighting units of the staircase enclosure then | A & R Contract Management | Alex Bosman | 2013-10-14 | No Emergency lighting installed, quote requested from RGE to install emergency lighting | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-14 15:04 | 2013-10-13 15:15 | 2013-08-14 15:04 | 2013-12-10 17:27 | -60 | In target
94 LADBROKE GROVE, LONDON W11 2HE - 2016.03.04 | 2016-04-04 16:07 | S217009120002 | LADBROKE GROVE (94) | 252408 | Active | 15 & 23 | High | Emergency Lighting | It is not known if any emergency lighting is installed on the landings of the staircase of this building, ie the common parts of this building. There are bulkhead type lighting units in the building which are similar to emergency lighting units, but the lighting units covers are dirty and no neon indicator/charging lights can be seen. NO REFERENCE TO EL ON KEYSTONE | I would recommend that the TMO electrical engineer is asked to check the lighting units in this building to ascertain if any are combined emergency lighting units. If any emergency lighting units are found to be installed within this building or externally these should be tested and serviced immediately with a discharge test carried out. They should be added to asset register and the contractor's maintenance schedule. Monthly occupiers tests must be undertaken.& recorded. Any defects and/or problems highlighted as a result of this testing and servicing should be rectified. If it is found that there are no emergency lighting units installed within the common parts of this building I would recommend that if work is undertaken on the lighting circuit or the lighting units of the staircase enclosure then consideration is given to the installation of combined normal and emergency lighting lights. Any installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman | 2016-05-09
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:23 | S217010567705 | LONGLANDS COURT (94-102) | 103365 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Block included in 14/15 communal testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-22 16:23 | 2013-09-12 16:24 | 2013-08-22 16:23 | 2014-03-21 17:07 | -21 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:24 | S217010567705 | LONGLANDS COURT (94-102) | 103368 | Completed | 1b | High | Emergency Lighting | Some of the covers of the lighting units in the lower ground floor area of this building are dirty, thus affecting the level of illuminating from the bulb. | I would recommend that the covers of the lighting units in the lower ground floor area of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels from the light bulbs. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2013-08-22 16:24 | 2013-09-12 16:25 | 2013-08-22 16:24 | 2015-04-14 10:10 | -21 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:26 | S217010567705 | LONGLANDS COURT (94-102) | 103370 | Completed | 7 | Medium | Lightning Protection | From what I can see there is no lightning protection system installed on this building, but the asset list given to me by the TMO electrical engineer states that there is a lightning protection system fitted and that this system is tested and serviced on a planned preventive maintenance schedule by an external contractor. | Can it be confirmed by a suitably qualified person if there is a lightning protection system installed on this building? If there is no further action needs to be taken except confirm that any testing and servicing is being undertaken. If there is no system fitted I would recommend that the asset register is amended and the external contractor informed. | A & R Contract Management | Alex Bosman |  | we confirm the presence of lightning protection and a compliant certificate | 2015-11-17 | Fully Completed | Maria Ares | 2013-08-22 16:26 | 2013-10-21 16:27 | 2013-08-22 16:26 | 2015-11-18 13:24 | -60 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:34 | S217010567705 | LONGLANDS COURT (94-102) | 103379 | Completed | 15 | Medium | Emergency Lighting | There appears to be no emergency lighting units covering the lower ground floor level central corridor where the bin store is located off and the two of the resident's storage areas. | I would recommend that this lower ground floor level central corridor area is checked to see if any emergency lighting units are installed covering this corridor. If it is not I would recommend that suitable emergency lighting is installed to cover this area including the rear exit door. | A & R Contract Management | Alex Bosman |  | RMA confirmed all works complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2013-08-22 16:34 | 2013-10-21 16:36 | 2013-08-22 16:34 | 2015-12-15 10:50 | -60 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:36 | S217010567705 | LONGLANDS COURT (94-102) | 103383 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | hardwired heat & smoke detectors installed during PIR testing | 2014-05-12 | Fully Completed |  |  |  | 2013-08-22 16:36 | 2014-05-13 17:10
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:37 | S217010567705 | LONGLANDS COURT (94-102) | 103385 | Completed | 23a | High | Emergency Lighting | The emergency lighting system currently installed in the staircase enclosures of this building and covering the lower ground floor level electrical room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | added to asset register for servicing | 2014-04-22 | Fully Completed | Alex Bosman | 2013-08-22 16:37 | 2013-09-12 16:40 | 2013-08-22 16:37 | 2014-04-23 17:06 | -21 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:41 | S217010567705 | LONGLANDS COURT (94-102) | 103387 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-22 16:41 | 2013-09-12 16:42 | 2013-08-22 16:41 | 2014-04-23 17:06 | -21 | In target
96 - 98 BLENHEIM CRESCENT - 2015.06.16 | 2015-06-26 12:34 | S217008160001 | BLENHEIM CRESCENT (96) | 203584 | Completed | 1 | High | Electrical Wire Check | There was no contractors label on the electrical supply/distribution board located in the ground floor level electrical room/cupboard of number 96 showing the dates of the last 5 year fixed electrical wiring test. | Can it be confirmed with the TMO electrical engineer if the landlords fixed electrical wiring in this part of the building has been tested in the last 5 years? If it has not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. KEYSTONE - TEST RECORDED AS 12/6/2015 BUT NO CERTIFICATE | A & R Contract Management | Alex Bosman |  | 27/01/2015 - Completed - Certificate held in keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-06-26 12:34 | 2015-07-17 12:36 | 2015-06-26 12:34 | 2015-08-25 16:28 | -21 | In target
98 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:05 | S217001880033 | ELM PARK GARDENS (98) | 201699 | Completed | 15 | High | Emergency Lighting | Some of the individual units of this emergency lighting system have failed and have been replaced with just pendant lights. It appears that the installed emergency lighting system in this building is not in full working order. | If the currently installed emergency lighting system in this building is not working correctly with units having failed etc then the installed emergency lighting system should be replaced immediately. Any newly installed emergency lighting system should be to the requirements of BS 5266 Part 1 2011. So this will include installing an emergency lighting unit in the basement boiler area where there appears to be no emergency lighting unit presently installed and checking the emergency lights presently installed in the roof level lift and water tank rooms. Installation and commissioning certificates should be obtained from the contractors who installed the new emergency lighting units/system. | A & R Contract Management | Alex Bosman |  | new emegrency lighting installed and certs supplied | 2015-11-17 | Fully Completed | Maria Ares | 2015-06-16 10:05 | 2015-07-07 10:08 | 2015-06-16 10:05 | 2015-11-18 13:25 | -21 | In target
98 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:08 | S217001880033 | ELM PARK GARDENS (98) | 201700 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this buildings roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-16 10:08 | 2015-07-07 10:10 | 2015-06-16 10:08 | 2015-12-02 13:17 | -21 | In target
98 ELM PARK GARDENS - 2015.06.11 | 2015-06-16 10:11 | S217001880033 | ELM PARK GARDENS (98) | 201701 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO REFERENCE TO EL ON KEYSTONE SERVICING RECORD | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 18.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-16 10:11 | 2015-07-07 10:12 | 2015-06-16 10:11 | 2015-11-27 10:00 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 11:29 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214894 | Completed | 15 | High | Emergency Lighting | There are some emergency escape lighting units installed in this building but the locations of these units and there positioning appears to be random and haphazard. | I would recommend that a full survey of the as installed emergency escape lighting system in this building is undertaken. This should then be compared to the requirements of BS 5266 Part 1 2011 and any deficiencies or lack of coverage then rectified with additional units being installed. | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-04 11:29 | 2015-09-25 11:30 | 2015-09-04 11:29 | 2015-12-15 10:50 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 11:32 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214896 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units/system installed in this building, in the boiler and electrical rooms as well as in the 2 lift motor rooms. Some emergency lighting may also be installed on the means of escape routes. | Can it please be confirmed when the installed emergency lighting system/units in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP inspection complete no EL on site; keystone updated to include in 15/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-04 11:32 | 2015-09-25 12:12 | 2015-09-04 11:32 | 2015-12-15 10:51 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 12:13 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214921 | Completed | 23c | High | Fire Extinguisher | All of the fire extinguishers located in this building, in the lift motor rooms, in the electrical rooms and in the boiler room are out of service/test date according to the RGE contractors service labels on them. The last service date was either July 2011 for the lift motor room ones or January 2014 for the other ones. | All the fire extinguishers located in this building should be serviced/tested immediately and it confirmed that they are on the external contractors maintenance schedule for servicing next year. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-04 12:13 | 2015-09-25 12:15 | 2015-09-04 12:13 | 2015-12-02 13:21 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:25 | S217007970002 | ADAIR TOWER | 133558 | Completed | 17b | Low | Fire Alarm | The boiler room of this building is fitted with a full fire alarm detection and warning system, there are no TMO employees who work in this area. | I would recommend that the fire alarm system in this building is connected to a monitoring station/service so in the event of an activation of the fire alarm system the fire service or an on duty caretaker is informed. | A & R Contract Management | Alex Bosman |  | Potential to remove system due to area being secured and forming low fire risk. Awaiting feedback from FRA & LFB which is due mid December | 2015-12-14 | Fully Completed | Maria Ares | 2014-03-07 11:25 | 2014-09-03 11:26 | 2014-03-07 11:25 | 2015-12-15 10:52 | -180 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:26 | S217007970002 | ADAIR TOWER | 133559 | Completed | 18a | High | Fire Extinguisher | Very Dange-rous The horn on the carbon dioxide fire extinguisher in the ground floor level water pump room was not screwed up tightly. If a person were to use this fire extinguisher then they could suffer serious cold burns. | RGE should service this fire extinguisher again correctly. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-07 11:26 | 2014-03-28 11:28 | 2014-03-07 11:26 | 2015-09-29 17:19 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:28 | S217007970002 | ADAIR TOWER | 133562 | Completed | 18b | Information Only | Fire Extinguisher | There are 2 x water, 1 x 5 kg carbon dioxide and 1 x 4.5 kg Dry powder fire extinguishers in the small plant room next to the boiler room. | There is over provision of fire extinguishers in this small plant room - RGE to b e instructed to address. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed |  |  |  | 2014-03-07 11:28 | 2015-09-29 17:20
ADAIR TOWER - 2014.02.20 | 2014-03-07 12:13 | S217007970002 | ADAIR TOWER | 133593 | Active | 23a | High | Fire Alarm | Are the weekly occupier's tests of the fire alarm and warning system installed in the boiler etc being undertaken? | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | A & R Contract Management | Alex Bosman
ADAIR TOWER - 2014.02.20 | 2014-03-07 12:14 | S217007970002 | ADAIR TOWER | 133594 | Completed | 23b | High | Fire Alarm | The fire alarm system currently installed in the boiler room of this building does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed fire alarm system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to asset register for serviceing | 2014-04-22 | Fully Completed | Alex Bosman | 2014-03-07 12:14 | 2014-03-28 12:39 | 2014-03-07 12:14 | 2014-04-23 17:08 | -21 | In target
AGNES HOUSE - 2014.08.14 | 2014-08-20 11:00 | S217010050010 | AGNES HOUSE | 158174 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. | The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB if required. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | Hard wired detectors to be installed during 5 year PIR program | 2015-03-23 | Fully Completed |  |  |  | 2014-08-20 11:00 | 2015-03-24 17:01
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 10:36 | S217008190003 | APPLEFORD HOUSE 1-12 | 204471 | Completed | 3 | High | Miscellaneous | At the head of the staircase, by flat 5 at the 3rd floor level, there is a small room which contains extraction units for the dwellings of this building. According to the Cofley servicing and maintenance book in this room the last service on this extraction system was on the 22nd September 2014.There were monthly service visits noted before this last service date. | Please can it be confirmed that this extraction system is being serviced and maintained correctly on a planned preventive maintenance programme? If they are not then I would recommend that the TMO contractor, Cofley is asked to check/ service this extraction system and any defects found should be rectified. | A & R Contract Management | Anthony Cheney |  | This extraction system ( Woods, Aerofoil) is included within the PPM schedule as confrimed to JW of H&S 17/7/15 in line with CIBSE recommendations | 2015-12-01 | Fully Completed | Maria Ares | 2015-07-02 10:36 | 2015-07-23 10:39 | 2015-07-02 10:36 | 2015-12-02 13:24 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 11:42 | S217008190003 | APPLEFORD HOUSE 1-12 | 204535 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on each of the staircase landings of this building, the means of escape routes from the building. | Can it please be conformed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Keystone - listed as asset but no current Cert | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 16/07/2015 | 2015-07-16 | Fully Completed | Gillian Kennedy | 2015-07-02 11:42 | 2015-07-23 11:43 | 2015-07-02 11:42 | 2015-08-25 15:09 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:23 | S217007970004 | APPLEFORD HOUSE 13-28 | 206056 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on each of the staircase landings of this building, the means of escape routes from the building. | Can it please be confirmed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE SHOWS " LAST OUTCOME DATE" as 10/13 - BUT NO DOCUMENTATION | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 15/07/2015 | 2015-07-15 | Fully Completed | Gillian Kennedy | 2015-07-10 13:23 | 2015-07-31 13:25 | 2015-07-10 13:23 | 2015-08-25 15:10 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:27 | S217007970004 | APPLEFORD HOUSE 13-28 | 206059 | Completed | 23c | High | Lightning Protection | There appears to be a lightning protection system installed on this building, but this system does not appear on the asset register of lightning protection systems which are subject to a maintenance contract by the TMO contractor. | Please can it be confirmed that the lightning protection system installed on this building is being maintained and serviced with records kept. If it is not being serviced etc then I would recommend that the TMO contractor who undertakes the lightning protection system servicing is asked to check this installed system and any defects found should be rectified. | A & R Contract Management | Janice Wray |  | Updated list provided by A&R confirms this block on list. | 2015-07-28 | Fully Completed | Janice Wray | 2015-07-10 13:27 | 2015-07-31 13:29 | 2015-07-10 13:27 | 2015-07-29 14:41 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 10:58 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101939 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-05 | Included in Communal Electrical testing program 13/14 Being Actioned | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-15 10:58 | 2013-09-05 11:30 | 2013-08-15 10:58 | 2015-11-27 12:38 | -21 | In target | 2013-08-15 10:58 | 2015-12-03 10:51 | Janice Wray
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 13:01 | S217012740012 | ASHBURNHAM TOWER 1-50 | 102000 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed on the landings of the staircase and in the lift motor room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that confirmation is obtained from the electrical contractor that the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-05 | Asset register update for inclusion in servicing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-15 13:01 | 2013-09-05 13:04 | 2013-08-15 13:01 | 2013-10-02 16:27 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 13:06 | S217012740012 | ASHBURNHAM TOWER 1-50 | 102006 | Completed | 23b | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-05 | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-15 13:06 | 2013-09-05 13:08 | 2013-08-15 13:06 | 2014-04-23 17:09 | -21 | In target
BALFOUR HOUSE - 2015.07.27 | 2015-09-02 12:16 | S217010080002 | BALFOUR HOUSE | 214514 | Completed | 17 | High | Miscellaneous | It is not known if interlinked electrically powered / operated domestic smoke/heat detection is fitted within flat 4. | Please can it be confirmed that interlinked electrically powered / operated domestic smoke/heat detection/alarms are fitted within flat 4. If they are not I would recommend that domestic smoke and heat detection/ alarms are fitted in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | complete - previously confirmed hard wired heat and smoke detectors are installed during PIR program current at 94% | 2015-11-17 | Fully Completed | Maria Ares | 2015-09-02 12:16 | 2015-09-23 12:17 | 2015-09-02 12:16 | 2015-11-18 13:30 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 14:08 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 171956 | Completed | 1b | Information Only | Miscellaneous | There are no contractor's labels on the electrical supply/distribution boards in electrical intake rooms 2 to 4 this building stating the last 5 year periodic test date and the retest date. The electrical asset list states that the fixed electrical wiring was last tested in November 2010 and is due for retesting in November 2015. | I would recommend that when the next electrical fixed wiring test is undertaken on the common parts electrical wiring in this building that the electrical contractors are asked to display contractors labels on each of the electrical supply/distribution boards in electrical intake rooms with the test and retest dates. | A & R Contract Management | Alex Bosman |  | complete as per 2015 communal testing program | 2015-08-11 | Fully Completed |  |  |  | 2014-11-28 14:08 | 2015-08-12 12:20
BARANDON WALK - 2014.11.6 | 2014-11-28 14:45 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 171972 | Completed | 3 | Low | Miscellaneous | There is no fire fighter entry over ride device fitted to the storey entrance/exit door between sections 4 and 5 by Grenfell Road on the 1st floor level close to flat 507. | For consistency I would recommend that a fire fighter entry over ride switch/device is fitted to this storey entrance/exit door on the staircase side. All of the other entrance doors and storey entrance doors have them fitted. | A & R Contract Management | Alex Bosman |  | complete - considered as information only to be include when system is renewed | 2015-11-17 | Fully Completed | Maria Ares | 2014-11-28 14:45 | 2015-05-27 14:47 | 2014-11-28 14:45 | 2015-11-18 13:43 | -180 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 14:55 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172003 | Completed | 15a | High | Emergency Lighting | There is presently an emergency escape lighting system installed in this building but the locations of these units and their positioning appears to be random and haphazard. | I would recommend that a full survey of the as installed emergency escape lighting system in this building is undertaken. This should then be compared to the requirements of BS 5266 and any deficiencies or lack of coverage then rectified. | A & R Contract Management | Alex Bosman |  | RMA inspection complete current system confirmed as designed; upgrade works to current standards submitted for future consideration | 2015-12-14 | Fully Completed | Maria Ares | 2014-11-28 14:55 | 2014-12-19 14:56 | 2014-11-28 14:55 | 2015-12-15 11:00 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:21 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172030 | Completed | 15b | High | Emergency Lighting | The covers of some of the emergency lighting units currently installed in this building are dirty. This means that the charger indicator light is not clearly visible as required by the British Standard. | I would recommend that the covers of the emergency lighting units currently installed in the building are cleaned, replaced or the charger indicator lights are replaced with brighter ones so that the neon indicators are easily seen. This will help the caretakers to undertake the monthly checking of the emergency lighting system. | A & R Contract Management | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2014-11-28 15:21 | 2014-12-19 15:22 | 2014-11-28 15:21 | 2015-11-18 13:44 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:24 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172033 | Completed | 17a | High | Fire Alarm | There is a fire alarm system installed in this building, which is limited to two different areas of the building, the electrical intake rooms and the roof areas. The automatic detectors operate the smoke vents in the roofs and cover the electrical intake rooms. There is no warning system and the locations of these installed devices and their positioning indicates that they are for a bespoke reason only. The control panel for this installed fire alarm system is located in the now disused reception area of Grenfell Tower. It is a serious offence under the Fire Safety Order not to maintain an installed fire alarm system. | 1.The reception area of Grenfell Tower is being refurbished, how is access to the fire alarm control panel being maintained? 2.It is assumed that the present fire alarm system is fully operational, if it is not repairs to the installed fire alarm system must be undertaken immediately. 3.Will the fire alarm control panel be relocated in the future? 4.To comply with the requirements of the Building Regulations the smoke vents located in the glazed roof areas of this building must be linked to local automatic smoke detection, how will this requirement be achieved? 5.How will the fire alarm system devices installed in the electrical intake rooms be controlled and monitored? | A & R Contract Management | Alex Bosman |  | No longer relavant systems removered during works and new system installed during refurb. Interim arrangements in place agreed with contractors, LFB and TMO H&S | 2015-12-01 | Fully Completed | Maria Ares | 2014-11-28 15:24 | 2014-12-19 15:26 | 2014-11-28 15:24 | 2015-12-02 13:27 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:26 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172034 | Active | 17b | High | Fire Alarm | How is the fire alarm system in this building being monitored now that the Grenfell Tower reception is not in existence. | I would recommend that the fire alarm control panel for the detectors of the smoke vents is connected to a monitoring stationed so in the event of an activation of the system the fire service or on duty caretaker can be informed. | A & R Contract Management | Alex Bosman
BARANDON WALK - 2014.11.6 | 2014-11-28 15:29 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172036 | Active | 19a | High | Miscellaneous | The last service and test on the water ring main was undertaken by M and P Fire Protection Limited on the 29th November 2013 according to the contractors label fixed inside the ring main box located under Grenfell Walk. But the last service date on the contractors labels on the ring main box doors in this building was the 8th September 2012 | Please can it be confirmed that when the contractor serviced the water ring main in the lower ground floor level of this building in November 2013, all the other ring main outlets were tested and dated November 2013. If he did not then the ring main in this building should be serviced and tested immediately with any defects found rectified. Alex | A & R Contract Management | Alex Bosman
BARANDON WALK - 2014.11.6 | 2014-11-28 15:31 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172039 | Completed | 19b | High | Dry or Wet Riser | There are dry riser mains in this building in light of the above can the contractor M and P Fire Protection Limited, confirm the last service date of these items, the dry riser for Grenfell Walk was last serviced/tested on 30th December 2013. | Can the contractor please supply the test records for the dry risers numbered 1 to 4 to confirm that they were tested and serviced along with the other dry rising main on this estate. If it is found that the dry risers numbers 1 to 4 were not last serviced/tested on 30th December 2013 they must be tested and serviced immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | completed 05.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-11-28 15:31 | 2014-12-19 15:32 | 2014-11-28 15:31 | 2015-11-20 11:16 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:34 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172041 | Completed | 19d | High | Miscellaneous | There are automatic opening vents in the glazed ceiling of this building operated by smoke detectors. It is a serious offence under the Fire Safety Order not to maintain an installed fixed fire system. | Can it please be confirmed that these automatic opening vents are fully functional and in good working order? If they are not then a contractor should repair these automatic opening vents immediately. | A & R Contract Management | Alex Bosman | 2016-02-16 | Certification received confirming all in nworking condition COLT | 2016-02-16 | Fully Completed | Maria Ares | 2014-11-28 15:34 | 2014-12-19 15:35 | 2014-11-28 15:34 | 2016-02-17 10:22 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:35 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172042 | Completed | 19e | High | Miscellaneous | The reception area of Grenfell Tower is being refurbished and the control panel for the automatic opening vents in the glazed ceiling of this building and the other 2 nearby ones repositioned. | In the interim I would recommend that the fire service manual control switches located by the entrance door to each section of this building are checked to ensure they are operational and these are used to open the roof vents if needed. When the control panel for all of the automatic opening vents is repositioned then it should be fully tested before a commissioning certificate issue for it by the contractor. The control panel must be located/positioned so that it can easily be used and accessed but must not be in a location where it will be vandalised | A & R Contract Management | Alex Bosman | 2016-02-16 | Necessary works carried out by Colt, confirmed firmans switches in working condition | 2016-02-16 | Fully Completed | Maria Ares | 2014-11-28 15:35 | 2014-12-19 15:37 | 2014-11-28 15:35 | 2016-02-17 10:23 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:39 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172054 | Completed | 19g | High | Dry or Wet Riser | The door and box of the dry riser outlet located on the 1st floor level of the 400 section, riser number 3, by flat 412, is damaged. Are the ppm contractors responsible for this? | This damaged dry riser box and the door to it should be repaired or replaced. | A & R Contract Management | Alex Bosman |  | completed 05.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-11-28 15:39 | 2014-12-19 15:40 | 2014-11-28 15:39 | 2015-11-20 11:17 | -21 | In target
BARANDON WALK - 2014.11.6 | 2014-11-28 15:40 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172065 | Active | 21 | High | Miscellaneous | There are automatic ventilation systems installed in this building. | Have the caretakers and any duty or on call managers/housing officers etc been given specific instructions on how to use the installed smoke ventilation system of this building? This instruction should also be included how to use the fire service manual control boxes located by the entrance doors to each section of this building. | A & R Contract Management | Alex Bosman
BARANDON WALK - 2014.11.6 | 2014-11-28 15:46 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172069 | Active | 23a | High | Fire Alarm | There is a fire alarm system installed in this building. | Can the TMO electrical engineer and the electrical contractor please confirm that the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc found rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman
BARANDON WALK - 2014.11.6 | 2014-11-28 15:48 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172082 | Completed | 23c | High | Miscellaneous | There are automatic smoke ventilation systems installed in this building. | Are the automatic ventilation systems installed in this building being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2016-02-16 | Colt commisioned to carry out servicing of ventillation system. | 2016-02-16 | Fully Completed | Maria Ares | 2014-11-28 15:48 | 2014-12-19 15:49 | 2014-11-28 15:48 | 2016-02-17 10:32 | -21 | In target
BARKIS HOUES - 2014.7.22 | 2014-08-04 13:10 | S217010050002 | BARKIS HOUSE | 155842 | Completed | 1 | High | Electrical Wire Check | 1There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | complete as per 2015 communal testing program | 2015-08-11 | Fully Completed | Gillian Kennedy | 2014-08-04 13:10 | 2014-08-25 13:11 | 2014-08-04 13:10 | 2015-08-12 12:21 | -21 | In target
BARKIS HOUES - 2014.7.22 | 2014-08-04 13:12 | S217010050002 | BARKIS HOUSE | 155844 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building, these do not appear on the electrical asset list as supplied by the TMO electrical engineers. | Are the installed emergency lighting units/system being serviced, tested and maintained. Can it please be confirmed that the emergency lighting units/system installed within this building are being serviced, tested and maintained by an electrical contractor. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirm service complete and added to asset register 7.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-08-04 13:12 | 2014-08-25 13:14 | 2014-08-04 13:12 | 2016-01-22 12:57 | -21 | In target
BEAUFORT HOUSE - 2015.06.15 | 2015-06-25 14:25 | S217000310007 | BEAUFORT HOUSE | 203357 | Completed | 15 | Low | Emergency Lighting | There is presently no emergency escape lighting installed in this building, on the staircase, the landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. This is the way the building was converted/ constructed ie without emergency lighting. | I would recommend that emergency lighting units are installed on the landings, on the staircase and in the entrance lobby area as soon as financially possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17. Action entered into a porgramme of works | 2015-11-19 | Fully Completed | Maria Ares | 2015-06-25 14:25 | 2015-12-22 14:27 | 2015-06-25 14:25 | 2015-11-23 15:03 | -180 | In target | 2015-06-25 14:25 | 2015-11-29 15:03 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:12 | S217012740002 | BERENGER TOWER 1-51 | 102369 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-09 | Information received to date - Included in Communal Electrical testing program 13/14 BEING ACTIONED | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 09:12 | 2013-09-09 09:15 | 2013-08-19 09:12 | 2015-11-27 12:49 | -21 | In target | 2013-08-19 09:12 | 2015-12-03 12:49 | Janice Wray
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:15 | S217012740002 | BERENGER TOWER 1-51 | 102370 | Completed | 5 | Low | Lifts | In all other TMO buildings with lifts there is a record book kept for each lift in the lift motor room showing the servicing and maintenance dates and any other comments of each lift? I could not find one of the lift record books. | Is there a lift record book for each of the two lifts in this building? I would recommend that record book is provided for each lift because these show the servicing and maintenance dates along with any other comments etc. | A & R Contract Management | Alex Bosman | 2013-11-29 | servicing records kept electronically by current contractor, insurance certs kept electronically by TMO on Keystone | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-19 09:15 | 2014-02-15 09:17 | 2013-08-19 09:15 | 2013-12-10 17:48 | -180 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:49 | S217012740002 | BERENGER TOWER 1-51 | 102387 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed in the landings of the staircase, in the lift motor room and in the electrical room do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-09 | Added to the Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 09:49 | 2013-09-09 09:51 | 2013-08-19 09:49 | 2013-10-02 16:53 | -21 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:51 | S217012740002 | BERENGER TOWER 1-51 | 102391 | Completed | 23b | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-09 | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-19 09:51 | 2013-09-09 09:53 | 2013-08-19 09:51 | 2014-04-23 17:10 | -21 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:05 | S217012740014 | BLANTYRE TOWER 1-65 | 102162 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-06 | Block included on 13/14 communal block testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 07:05 | 2013-09-06 07:09 | 2013-08-16 07:05 | 2015-11-27 12:40 | -21 | In target | 2013-08-16 07:05 | 2015-12-03 10:53 | Janice Wray
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:40 | S217012740014 | BLANTYRE TOWER 1-65 | 102169 | Completed | 19 | High | Dry or Wet Riser | The leather securing straps are damaged on the dry riser outlets on the 1st and 5th floor level dry riser outlets. | New leather securing straps should be fitted to these two dry riser outlets as soon as possible. | A & R Contract Management | Alex Bosman | 2013-09-06 | Order raised with RGE | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-16 07:40 | 2013-09-06 07:41 | 2013-08-16 07:40 | 2013-12-10 17:52 | -21 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:42 | S217012740014 | BLANTYRE TOWER 1-65 | 102170 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed on the landings of the staircase and in the lift motor room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-06 | Keystone asset register updated for inclusion in servicing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 07:42 | 2013-09-06 07:45 | 2013-08-16 07:42 | 2013-10-02 16:38 | -21 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:46 | S217012740014 | BLANTYRE TOWER 1-65 | 102171 | Completed | 23b | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-06 | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-16 07:46 | 2013-09-06 07:49 | 2013-08-16 07:46 | 2014-04-23 17:11 | -21 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 14:59 | S217009090001 | BLECHYNDEN HOUSE | 142410 | Completed | 18a | High | Fire Extinguisher | The water fire extinguisher is missing from its wall bracket in the first floor level, there is a water fire extinguisher located on the other floor levels. | A water fire extinguisher should located here if this building is classed as sheltered Housing. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-05-06 14:59 | 2014-05-27 15:01 | 2014-05-06 14:59 | 2015-09-29 17:21 | -21 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 15:01 | S217009090001 | BLECHYNDEN HOUSE | 142411 | Completed | 18b | High | Fire Extinguisher | The Carbon Dioxide fire extinguisher in the ground floor level electrical room was last serviced on the 1st March 2013 according to the information on the RGE contractors label. | This Carbon Dioxide fire extinguisher should be serviced immediately and it confirmed that it is on the external contractors maintenance schedule, if this building is classed as sheltered Housing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complet 17.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-05-06 15:01 | 2014-05-27 15:02 | 2014-05-06 15:01 | 2015-12-02 13:28 | -21 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 15:04 | S217009090001 | BLECHYNDEN HOUSE | 142417 | Completed | 23a | High | Miscellaneous | There are automatic ventilation units, smoke control, installed on the windows in the corridors of this building, also in the walls and in the top floor level corridor ceiling. | Is the ventilation system installed in the building being serviced, tested and maintained by a contractor as per the manufactures instructions? If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-05-06 15:04 | 2014-05-27 15:06 | 2014-05-06 15:04 | 2015-11-27 10:01 | -21 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 15:06 | S217009090001 | BLECHYNDEN HOUSE | 142419 | Completed | 23b | High | Fire Alarm | The fire alarm system in this building extends into the private flats. | Can it please be confirmed by the TMO electrical engineer and the fire alarm maintenance company that the devices of the fire alarm system installed in the private flats/dwellings are all being serviced and maintained at the same time as the devices in the common parts of the building? | A & R Contract Management | Alex Bosman |  | Report Completed. AP confirmed servicing complete 19.11.2015 | 2015-11-26 | Fully Completed | Gillian Kennedy | 2014-05-06 15:06 | 2014-05-27 15:08 | 2014-05-06 15:06 | 2015-11-27 10:05 | -21 | In target | 2014-05-06 15:06 | 2015-10-07 12:26 | Maria Ares
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:57 | S217008190001 | BOSWORTH HOUSE | 184213 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape routes of this building, on the staircase landings and on the balconies. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 16/07/2015 | 2015-07-16 | Fully Completed | Gillian Kennedy | 2015-02-18 09:57 | 2015-03-11 09:58 | 2015-02-18 09:57 | 2015-08-25 15:11 | -21 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 14:05 | S217008220002 | BRAMLEY HOUSE | 199113 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system currently installed on the means of escape routes of this building, | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? On Keystone (Asset Register) but last inspection / servicing document dated Dec 2010 Please see comment | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 30/07/2015 | 2015-07-30 | Fully Completed | Gillian Kennedy | 2015-05-28 14:05 | 2015-06-18 14:07 | 2015-05-28 14:05 | 2015-08-25 15:13 | -21 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:22 | S217011160001 | BROADWOOD TERRACE 1-24 | 186478 | Completed | 1 | High | Electrical Wire Check | There are no electrical contractors labels on the electrical supply boards etc in the ground floor level lift motor room indicating when the last periodic electrical fixed wiring test was undertaken. There is no information on the TMO electrical engineers list either. | Can it be confirmed with the TMO electrical engineer when the last electrical wiring test on the fixed wiring for the common parts of the residential areas of this building was last undertaken? If this more that 5 years ago then a periodic electrical wiring test should be undertaken with any defects highlighted rectified and then placed on the contractor's maintenance schedule for future testing. | A & R Contract Management | Alex Bosman |  | 30/04/2015 - Completed - Certificate held in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-03-04 16:22 | 2015-03-25 16:24 | 2015-03-04 16:22 | 2015-08-25 16:30 | -21 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:26 | S217011160001 | BROADWOOD TERRACE 1-24 | 186481 | Completed | 15 | Medium | Emergency Lighting | I cannot be certain that there are emergency lighting units installed on the landings of the two exit staircases from the residential area down to Warwick Road. | I would recommend that the lighting in these two staircases is checked to see if any of the lighting units are also emergency lighting units. The installed system should then be compared to the requirements of BS 5266 Part 1, then any deficiencies found against the BS5266 layout requirements should be rectified by the installation of new emergency lighting units. | A & R Contract Management | Alex Bosman | 2016-01-13 | Survey completed and variation submitted | 2016-01-13 | Fully Completed | Maria Ares | 2015-03-04 16:26 | 2015-05-03 16:30 | 2015-03-04 16:26 | 2016-01-14 15:35 | -60 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:32 | S217011160001 | BROADWOOD TERRACE 1-24 | 186487 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed on the ramp in the tower, in the lift motor room and in the areas by the residents storage sheds/cupboards does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 10.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-03-04 16:32 | 2015-03-25 16:33 | 2015-03-04 16:32 | 2015-11-20 11:19 | -21 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:34 | S217011160001 | BROADWOOD TERRACE 1-24 | 186490 | Completed | 23c | High | Fire Extinguisher | The fire extinguishers in the lift motor room are out of test date according to the RGE servicing labels on them, the last test date on the contractor's label being July 2013. | These fire extinguishers should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed service complete 16.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2015-03-04 16:34 | 2015-03-25 16:36 | 2015-03-04 16:34 | 2016-01-22 12:59 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:55 | S217000980001 | BRUNEL HOUSE | 181587 | Completed | 23a | High | Emergency Lighting | The emergency lighting system/units currently installed in the staircase enclosure of this building do not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained with a full discharge test undertaken? | I would recommend that the TMO electrical engineers or the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained and a discharge test undertaken to BS 5266 Part 1 2011. If it is not, testing and servicing etc should be undertaken immediately and any defects found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | serviced by chubb 29.5.2015 confirmed ok | 2015-08-11 | Fully Completed | Gillian Kennedy | 2015-02-03 11:55 | 2015-02-24 11:56 | 2015-02-03 11:55 | 2015-08-12 12:22 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:57 | S217000980001 | BRUNEL HOUSE | 181589 | Completed | 23b | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the roof level lift motor room is out of test date according to the contractors servicing label attached to it. The last test date on the RGE service label is April 2013. | The carbon dioxide portable fire extinguisher located in the roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | Completed by Allied Protection 20/07/2015 | 2015-07-20 | Fully Completed | Gillian Kennedy | 2015-02-03 11:57 | 2015-02-24 11:58 | 2015-02-03 11:57 | 2015-08-25 15:13 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:14 | S217010650001 | BURGESS FIELDS | 104211 | Completed | 1a | High |  | It is not known if the washing machines and tumble dryers in the laundry are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-30 14:14 | 2013-09-20 14:16 | 2013-08-30 14:14 | 2015-02-27 14:42 | -21 | In target
BURGESSFIELD-2013.06.20 | 2013-08-30 14:59 | S217010650001 | BURGESS FIELDS | 104237 | Completed | 23c | High | Emergency Lighting | There are no records of the monthly occupiers tests and inspections of the emergency lighting system, fire extinguishers etc , these tests are being undertaken by the caretaker according to the manager. | Can it be confirmed that all the monthly occupiers tests and inspections are being undertaken as per the caretakers checklist? | A & R Contract Management | Alex Bosman |  | ESA training booked for 23rd & 24th April 2014 | 2014-04-24 | Fully Completed | Alex Bosman | 2013-08-30 14:59 | 2013-09-20 15:00 | 2013-08-30 14:59 | 2014-04-23 17:12 | -21 | In target
BURLEIGH HOUSE, BEAUFORT STREET, LONDON SW3 5BE - 2016.02.11 | 2016-04-04 15:30 | S217000310002 | BURLEIGH HOUSE BEAUFORT STREET | 252378 | Active | 5a & b | High | Miscellaneous | On the top floor level landing of each of the staircases there is a wall mounted box which has marked on it "Fan Switch/Ventilation". On the top floor level landing of each of the staircases there is a wall mounted box which has marked on it "Fan Switch/Ventilation". | Can it be confirmed what this switch is for, is it for or connected with the extraction equipment in the roof space areas? Can it also be confirmed that any maintenance or servicing is being undertaken as per the manufactures requirements for the roof space extraction systems. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman | 2016-05-09
BURLEIGH HOUSE, BEAUFORT STREET, LONDON SW3 5BE - 2016.02.11 | 2016-04-04 15:56 | S217000310002 | BURLEIGH HOUSE BEAUFORT STREET | 252395 | Active | 14 | High | Miscellaneous | Are there any fire dampers or filters installed in the extraction units located in the roof space areas? | If any dampeners or filters are installed within the roof space area extraction systems are these on a maintenance and servicing contract, if applicable? | A & R Contract Management | Alex Bosman | 2016-05-09
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:29 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134508 | Completed | 1a | High | Wiring Inspection | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. This electrical wiring testing includes the boiler room. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-05-12 | Fully Completed | Alex Bosman | 2014-03-13 15:29 | 2014-04-03 15:30 | 2014-03-13 15:29 | 2014-05-13 17:11 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:54 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134537 | Completed | 17 | Low | Fire Alarm | The boiler room of this building is fitted with a full fire alarm detection and warning system, there are no TMO employees who work in this area. | I would recommend that the fire alarm system in this building is connected to a monitoring station/service so in the event of an activation of the fire alarm system the fire service or an on duty caretaker is informed. | A & R Contract Management | Alex Bosman |  | Potential to remove system due to area being secured and forming low fire risk. Awaiting feedback from FRA & LFB which is due mid December | 2015-12-14 | Fully Completed | Maria Ares | 2014-03-13 15:54 | 2014-09-09 15:56 | 2014-03-13 15:54 | 2015-12-15 11:01 | -180 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:00 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134541 | Active | 23a | High | Fire Alarm | The fire alarm system currently installed in the boiler room of this building does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed fire alarm system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  |  |  |  | Cyril Morris | 2014-03-13 16:00 | 2014-04-03 16:01 |  |  | 734 | 734 days overdue
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:04 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134544 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the ground floor electrical cupboard is out of test date according to the RGE servicing label attached to it. The last test date being November 2011. | RECOMMENDED ACTION - Please see item 18 above, the carbon dioxide portable fire extinguishers located in the electrical cupboard of this building could be removed and the external contractor's maintenance schedule amended to show this change. Alternative Action8 Alternatively the carbon dioxide portable fire extinguisher located in the ground floor electrical cupboard could be serviced immediately and it confirmed that it is on the external contractors maintenance schedule. NOTE: THIS APPLIES TO BOTH BLOCKS | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-13 16:04 | 2014-04-03 16:07 | 2014-03-13 16:04 | 2015-09-30 09:38 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:07 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134545 | Completed | 23d | High | Fire Extinguisher | In the boiler room some of the fire extinguishers have been annually serviced by RGE and others have not. The last test date according to the RGE servicing label attached to the ones out of test date was January 2012 other were last serviced in January 2013. | All the fire extinguishers located in the boiler room should be checked to see if they are in test date, if they are not they should be serviced immediately and it confirmed that they are on the RGE contractors maintenance schedule. NOTE: THIS APPLIES TO BOTH BLOCKS | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-13 16:07 | 2014-04-03 16:09 | 2014-03-13 16:07 | 2015-09-30 09:40 | -21 | In target
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 15:45 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125353 | Completed | 5 | High | Miscellaneous | 5There is a mechanical air/exhaust extraction system installed in this basement level car park. The control panel/switches for this extraction system is wall mounted and the extraction system discharges out via a shaft to the garden area at the rear of the residential building. | Can it be confirmed that any maintenance or servicing is being undertaken as per the manufacturers requirements on a planned preventive maintenance contract for this extraction system including any filters being changed. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman |  | RMA confirmed serviced december 2014. order 201443197 | 2015-12-01 | Fully Completed | Maria Ares | 2014-01-21 15:45 | 2014-02-11 15:47 | 2014-01-21 15:45 | 2015-12-02 13:30 | -21 | In target
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 15:47 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125355 | Completed | 15 | Medium | Emergency Lighting | The presently installed emergency lighting system in this car park is not to a recognised standard. Emergency lighting units appear to just be randomly fitted. | When possible I would recommend that new or additional emergency lighting units are installed in this car park to the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman | 2015-07-22 | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2014-01-21 15:47 | 2014-03-22 15:49 | 2014-01-21 15:47 | 2016-01-19 16:10 | -60 | In target | 2014-01-21 15:47 | 2016-01-25 16:09 | Janice Wray
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 15:49 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125356 | Completed | 18 | Information Only | Fire Extinguisher | There are fire extinguishers provided in this car park, this car park does not have anybody employed to work in it and it is full covered by an automatic water sprinkler system. | RECOMMENDED ACTION All the fire extinguishers in this car park could be removed from this car park as this area is covered by an automatic water sprinkler system. | A & R Contract Management | Alex Bosman |  | AP confirmed not present 20.7.2015 | 2015-11-26 | Fully Completed |  |  |  | 2014-01-21 15:49 | 2015-11-27 10:05
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 16:32 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125372 | Completed | 19 | Information Only | Hose Reels | There are two water hose reels provided in this car park, this car park does not have anybody employed to work in it and it is fully covered by an automatic water sprinkler system. | RECOMMENDED ACTION These two fire fighting hose reels are not required in this car park as this car park is covered by an automatic water sprinkler system. The fire signage on the water hose reels in this car park should be removed so that they are just normal hose reels which could be used for washing down etc OR the hose reels could be removed completely. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed |  |  |  | 2014-01-21 16:32 | 2015-09-30 09:41
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 16:36 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125376 | Completed | 23b | High |  | The emergency lighting units/system currently installed in this car park does not appear on the electrical asset list as supplied by the TMO electrical engineer and there are no documents on site indicating that contractor servicing etc has been undertaken. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 17.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-01-21 16:36 | 2014-02-11 16:37 | 2014-01-21 16:36 | 2015-11-27 10:06 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 12:58 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127444 | Completed | 5 | High | Miscellaneous | There is a mechanical air/exhaust extraction system installed in this basement level car park. The control panel/switches for this extraction system is wall mounted and the extraction system discharges out via shafts to the garden area at the rear of the residential building. | Can it be confirmed that any maintenance or servicing is being undertaken as per the manufactures requirements on a planned preventive maintenance contract for this extraction system including any filters being changed. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman |  | RMA confirmed serviced July 2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-01-31 12:58 | 2014-02-21 12:59 | 2014-01-31 12:58 | 2015-12-02 13:30 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:13 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127459 | Completed | 15 | Medium | Emergency Lighting | The presently installed emergency lighting system in this car park is not to a recognised standard. Emergency lighting units appear to just be randomly fitted and this is a large open plan area. | As soon as possible I would recommend that new or additional emergency lighting units are installed in this car park to the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2014-01-31 13:13 | 2014-04-01 13:15 | 2014-01-31 13:13 | 2015-12-15 11:14 | -60 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:21 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127468 | Completed | 18 | Information Only | Fire Extinguisher | There are fire extinguishers provided in this car park, this car park does not have anybody employed to work in it and it is full covered by an automatic water sprinkler system. | All the fire extinguishers in this car park could I believe be removed from this car park as this area is covered by an automatic water sprinkler system. RCOMMENDED ACTION Please remove fire extinguishers | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed |  |  |  | 2014-01-31 13:21 | 2015-09-30 09:41
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 13:23 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127470 | Completed | 19 | High | Hose Reels | There are two water hose reels provided in this car park, this car park does not have anybody employed to work in it and it is fully covered by an automatic water sprinkler system. | These two hose reels were last serviced and tested in November 2009 according to the RGE contractors servicing labels on them. These two fire fighting hose reels are not required in this car park as this car park is covered by an automatic water sprinkler system. The fire signage on the water hose reels in this car park could be removed so that they are just normal hose reels which could be used for washing down etc or the hose reels could be removed completely. PLEASE REMOVE FIRE SIGNAGE FROM HOSE REELS. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-01-31 13:23 | 2014-02-21 13:25 | 2014-01-31 13:23 | 2015-12-02 13:31 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 14:32 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127516 | Completed | 23a | High | Fire Extinguisher | The fire extinguishers and the hose reels located in this basement level car park are all out of test date according to the servicing labels attached to them. The last test date being in November 2009. | Please see items 18 and 19 above before these fire extinguishers and hose reels are serviced and tested. If these fire extinguishers and / or hose reels are to remain they must be serviced and tested immediately | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed removed from site. 23.11.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-01-31 14:32 | 2014-02-21 14:34 | 2014-01-31 14:32 | 2016-01-22 13:01 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 14:36 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127520 | Completed | 23c | High | Emergency Lighting | The emergency lighting units/system currently installed in this car park does not appear on the electrical asset list as supplied by the TMO electrical engineer and there are no documents on site indicating that contractor servicing etc has been undertaken. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 28.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-01-31 14:36 | 2014-02-21 14:37 | 2014-01-31 14:36 | 2015-11-20 11:56 | -21 | In target
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:28 | S217010050007 | CARTON HOUSE | 143684 | Active | 15a | High | Emergency Lighting | This building underwent a refurbishment in 2010/11, Marley House next to this building had an emergency lighting system installed as part of these works. But it appears that there were no emergency lighting units/system installed on the staircases or means of escape routes in this building. | I would recommend that the scope of the refurbishment work undertaken in this building is checked to see why no new emergency lighting units/system was installed in this building. | A & R Contract Management | Alex Bosman | 2014-05-30 | Passed to contracts team for assessment | 2014-05-15 | Partially Completed | David Gibson | 2014-05-14 11:28 | 2014-06-04 11:52 | 2014-05-14 11:28 | 2014-05-16 16:12 | -21 | In target | 2014-05-14 11:28 | 2014-05-23 13:36 | Maria Ares
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:53 | S217010050007 | CARTON HOUSE | 143693 | Completed | 15b | High | Emergency Lighting | There appears to be no emergency lighting system/units installed on the landings of the staircases or in the entrance hall area ie the common parts of this building. This is a ten storey high building which has had refurbishment work undertaken in it in the last couple of years. | Please see item 15a above. I would recommend that emergency lighting units are is installed to cover the means of escape routes in this building as soon as possible. That is the common parts of the building. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman | 2014-05-30 | Will be included into this years programme if there is capacity. If not budget year 16/17. Action netered into a programme of works | 2015-11-19 | Fully Completed | David Gibson | 2014-05-14 11:53 | 2014-06-04 11:54 | 2014-05-14 11:53 | 2015-11-23 14:23 | -21 | In target | 2014-05-14 11:53 | 2015-11-29 14:23 | Janice Wray
CARTON HOUSE - 2014.4.22 | 2014-05-14 12:03 | S217010050007 | CARTON HOUSE | 143701 | Completed | 23a | High | Emergency Lighting | The few emergency lighting units presently installed in this building, roof space etc do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are these installed emergency lighting units being serviced, tested and maintained. | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting units in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 17.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-05-14 12:03 | 2014-06-04 12:04 | 2014-05-14 12:03 | 2015-11-20 12:02 | -21 | In target
CHELSEA FARM HOUSE - 2013.06.01 | 2013-09-23 16:32 | S217012760007 | CHELSEA FARM HOUSE | 107314 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO contract manager confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-10-21 | Block included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2013-09-23 16:32 | 2013-10-14 16:41 | 2013-09-23 16:32 | 2014-07-15 15:52 | -21 | In target
CHELSEA MANOR COURT FLATS 27 TO 76 - 2015.07.07 | 2015-09-01 09:47 | S217000830004 | CHELSEA MANOR COURT 27-54 | 214232 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency escape lighting installed in this building on the 2nd floor level external walkway/balcony or on the staircase landings. | I would recommend that if any work is undertaken on the lighting units within this building on the means of escape routes then consideration is given to fitting emergency escape lighting. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Included into current programme on this scheme, start Q4 15/16 | 2015-11-19 | Fully Completed |  |  |  | 2015-09-01 09:47 | 2015-11-23 16:24 |  |  | 2015-09-01 09:47 | 2015-11-29 16:24 | Janice Wray
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 15:35 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102299 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-06 | Block added to 13/14 electrical block testing program | 2013-10-01 | Partially Completed | Alex Bosman | 2013-08-16 15:35 | 2013-09-06 15:46 | 2013-08-16 15:35 | 2013-10-02 16:42 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 17:07 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102360 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed on the landings of the staircase and in the lift motor room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-06 | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 17:07 | 2013-09-06 17:09 | 2013-08-16 17:07 | 2013-10-02 16:51 | -21 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 17:10 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102362 | Completed | 23b | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-06 | Grateful if you could confirm when the ESA trg will be taking place to enable this inspection regime to commence. Traingin completed. ongoing refreshers to be arranged by H&S / team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-08-16 17:10 | 2013-09-06 17:13 | 2013-08-16 17:10 | 2014-07-15 16:13 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 12:27 | S217010570001 | CLYDESDALE HOUSE | 102819 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | included in 13/14 block electrical testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 12:27 | 2013-09-10 13:19 | 2013-08-20 12:27 | 2015-11-27 13:09 | -21 | In target | 2013-08-20 12:27 | 2015-12-03 10:54 | Janice Wray
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:00 | S217010570001 | CLYDESDALE HOUSE | 102850 | Active | 15 | High | Emergency Lighting | The covers of the emergency lighting units currently installed in the building are not clear so it is hard to see the charger indicator light clearly. | I would recommend that the covers of the emergency lighting units currently installed in the building are replaced so that the charger indicator light can be seen more easily. Or a brighter charger indicator light bulb is fitted this will help the caretakers to undertake the monthly checking of the emergency lighting. If it is found that there are not any emergency lighting units installed/sited in some areas as required by BS 5266 Part 1 then new units should be installed in these locations as soon as possible. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2013-08-20 14:00 | 2013-09-10 14:02 |  |  | 939 | 939 days overdue
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:04 | S217010570001 | CLYDESDALE HOUSE | 102853 | Completed | 17 | Low | Smoke Alarms | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Automatic domestic detection was not fitted in one flat visited, but battery powered devices were fitted in another one. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. I would recommend that the caretaker is instructed to put a copy of the LFB leaflet through each flats letter box. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | Hard wired detectors fitted to all properties during PIR testing | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-20 14:04 | 2014-02-16 14:06 | 2013-08-20 14:04 | 2013-12-10 17:53 | -180 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:07 | S217010570001 | CLYDESDALE HOUSE | 102854 | Completed | 23a | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. Is the installed lightning protection system being serviced, tested and maintained. | I would recommend that the TMO engineer is asked if the installed lightning protection system is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 14:07 | 2013-09-10 14:11 | 2013-08-20 14:07 | 2013-10-02 17:14 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:11 | S217010570001 | CLYDESDALE HOUSE | 102858 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Emergency lighting equipment added to asset register for future testing | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-20 14:11 | 2013-09-10 14:15 | 2013-08-20 14:11 | 2013-12-10 17:31 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:15 | S217010570001 | CLYDESDALE HOUSE | 102860 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 14:15 | 2013-09-10 14:16 | 2013-08-20 14:15 | 2013-10-02 17:15 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:17 | S217010570001 | CLYDESDALE HOUSE | 102861 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-20 14:17 | 2013-09-10 14:18 | 2013-08-20 14:17 | 2015-02-27 14:45 | -21 | In target
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 09:58 | S217010050003 | COPPERFIELD HOUSE | 157991 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building, but none were fitted within flat 5. Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building and one given to the occupant of flat 5. | The residents can now contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. Alternatively the TMO could fit hard wired electrical domestic detectors/ sounders within each flat without them in accordance with the requirements of BS 5839 Part 6 :2013. | A & R Contract Management | Alex Bosman |  | Hard wired detectors installed during 5 year PIR program | 2015-03-23 | Fully Completed | Alex Bosman | 2014-08-19 09:58 | 2015-02-15 10:01 | 2014-08-19 09:58 | 2015-03-24 17:03 | -180 | In target
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 10:01 | S217010050003 | COPPERFIELD HOUSE | 157993 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed in each staircase enclosure of this building appears to have been installed in the last couple of years and these units do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are the installed emergency lighting systems being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting systems in this building are being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately including a discharge test and any defects etc rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-08-19 10:01 | 2014-09-09 10:03 | 2014-08-19 10:01 | 2015-12-15 11:16 | -21 | In target
CORBETT HOUSE - 2015.06.11 | 2015-06-15 11:14 | S217000750001 | CORBETT HOUSE | 201475 | Completed | 15 | High | Emergency Lighting | New lighting units have been installed in one of the two entrance hall/lobby areas and on 5 of the 6 staircase landings. So in 5 of the 8 areas of this building, these are not emergency lighting units. The Building Regulations asks for emergency lighting in the common parts of residential buildings over two storeys in height. | I would recommend that these newly installed lighting units are removed and combined normal and emergency lighting units are installed in this building. This is to comply with the requirements of the Building Regulations. The new emergency lighting units/system should be installed as required by BS 5266 Part 1 2011. With the contractors providing installation and/or commissioning certificates as required by BS 5266 Part 1 2011. DOES NOT APPEAR TO BE IN SERVICING SECTION OF KEYSTONE | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-15 11:14 | 2015-07-06 11:16 | 2015-06-15 11:14 | 2015-12-15 11:16 | -21 | In target
CORBETT HOUSE - 2015.06.11 | 2015-06-15 11:17 | S217000750001 | CORBETT HOUSE | 201476 | Completed | 23a | High | Lightning Protection | The lightening protection system currently installed on this building does not appear on the TMO asset list as supplied by the TMO engineers. Is the installed lightening protection system being serviced, tested and maintained? | I would recommend that the TMO engineer is asked if the installed lightening protection system on this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA test complete Dec 15. | 2016-01-13 | Fully Completed | Maria Ares | 2015-06-15 11:17 | 2015-07-06 11:18 | 2015-06-15 11:17 | 2016-01-14 15:41 | -21 | In target
CRAIGIE VILLAS, TADEMA ROAD, LONDON SW10 0PZ - 2015.12.15 | 2016-02-08 16:49 | S217005360017 | CRAIGIE VILLAS | 242040 | Active | 23a | High | Emergency Lighting | There is an emergency lighting system/unit installed in this building, on the staircase first floor level landing and in the electrical cupboard. Is the installed emergency lighting unit being serviced, tested and maintained. Keystone has been checked. | Can it please be confirmed when the installed emergency lighting unit in this building was last serviced, tested and a discharge test of the unit's batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting unit should be serviced/tested immediately with any defects etc found rectified and then the unit with its location etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken of this emergency lighting unit? | A & R Contract Management | Alex Bosman | 2016-03-01
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 14:52 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103565 | Completed | 1a | High | Electrical Wire Check | The retest date for some of the portable electrical appliances is overdue according to the contractors test labels fixed to the items. Other the portable electrical appliances do not have portable appliance testing labels attached to them at all. | I would recommend that all the portable electrical appliance in this building are testing by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. For your information 2 year testing is now the normal time period not annually. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-23 14:52 | 2013-09-13 15:02 | 2013-08-23 14:52 | 2015-02-27 14:46 | -21 | In target
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:02 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103567 | Completed | 4a | High | Boiler | There appears to be no information held on site or contractors labels fixed to the buildings boiler giving the last servicing or maintenance date of this heating system. Undertaking planned preventative maintenance and regular servicing could prevent fires occurring because of defects. | I would recommend that the buildings and/or the contractors records are checked to see when the last servicing/maintenance date was for the boiler in this building. It should be on a planned preventative maintenance schedule with records kept, if the last service is found to be lore that over 1 year ago a service should be undertaken immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | Boiler included inservicing contract with valid cert held in keystone | 2014-10-08 | Fully Completed | Alex Bosman | 2013-08-23 15:02 | 2013-09-13 15:04 | 2013-08-23 15:02 | 2014-10-09 14:40 | -21 | In target
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:08 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103570 | Completed | 4b | High | Miscellaneous | There appears to be no information held on site or contractors labels fixed to the gas cooker in the kitchen giving the last servicing or maintenance date. | Can it be confirmed that the gas cooker in the kitchen is on an servicing contract, if it is not I would recommend that a check of the cooker is undertaken immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | LGSR issued 05/11/15 | 2015-11-20 | Fully Completed | Maria Ares | 2013-08-23 15:08 | 2013-09-13 15:09 | 2013-08-23 15:08 | 2015-11-23 13:16 | -21 | In target
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:09 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103571 | Completed | 6 | High | Miscellaneous | It is not known if the washing machine and the tumble dryer in the laundry are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-23 15:09 | 2013-09-13 15:10 | 2013-08-23 15:09 | 2015-02-27 14:47 | -21 | In target
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:16 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103575 | Completed | 18 | Information Only | Fire Extinguisher | There are presently carbon dioxide fire extinguishers located in nearly even room in this building, including in the externally accessed cupboards at the front of this building. | If there was a carbon dioxide and water fire extinguisher located in both the front and rear entrance lobby area of this building I believe that this would be a sufficient number of portable fire fighting appliances for this building. The fire blanket located in the kitchen should remain in situ. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-14 | Fully Completed |  |  |  | 2013-08-23 15:16 | 2015-12-15 11:17
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:18 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103577 | Active | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed in this building does not appear on the electrical asset list as supplied by the TMO electrical engineer and there are no documents on site indicating that contractor servicing etc has been undertaken. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2013-08-23 15:18 | 2013-09-13 15:18 |  |  | 936 | 936 days overdue
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 14:03 | S217003310001 | CURRAN HOUSE | 200510 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency escape lighting installed in this building on the external walkways/balconies. | I would recommend that if any work is undertaken on the lighting units within this building then consideration is given to fitting emergency escape lighting. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. Alex | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-06-08 14:03 | 2015-11-23 14:58 |  |  | 2015-06-08 14:03 | 2015-11-29 14:57 | Janice Wray
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 14:05 | S217003310001 | CURRAN HOUSE | 200512 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the roof level lift motor room and the 2 fire extinguishers at the basement level are out of test date according to the contractors servicing label attached to them. The last test date according to the RGE service labels was January 2013. | These fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing 16.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-08 14:05 | 2015-06-29 14:07 | 2015-06-08 14:05 | 2015-11-27 10:56 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:41 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181404 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this area was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Adrian Bowman | 2016-02-16 | Confirmed test and all necessary works completed on 201553419 | 2016-02-16 | Fully Completed | Maria Ares | 2015-02-02 15:41 | 2015-02-23 15:42 | 2015-02-02 15:41 | 2016-02-17 11:56 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:42 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181406 | Completed | 1b | High | Miscellaneous | There is an electrical water heater located in the kitchen, it is not known if this electrical item needs to be inspected/serviced as it is not used that frequently. | Can it please be confirmed that if this electrical water heater needs to be tested/serviced/inspected as per any manufactures guidance that it is? | A & R Contract Management | Alex Bosman |  | Complete - protected by circuit. Circuit tested during PIR no further servicing required | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-02 15:42 | 2015-02-23 15:43 | 2015-02-02 15:42 | 2015-12-02 14:43 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:44 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181407 | Completed | 4 | High | Boiler | It is not known if the gas boiler in this area has been serviced annually. | Can it please be confirmed if the gas boiler located in the cupboard in the toilets has been annually serviced by a "gas safe" contractor? If it has not then I would recommend that a service is undertaken immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | 23/07/2015 - Completed by K&T Heating | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-02-02 15:44 | 2015-02-23 15:45 | 2015-02-02 15:44 | 2015-08-25 16:31 | -21 | In target
DARFIELD WAY FLATS 2 TO 27 - 2015.08.13 | 2015-09-02 14:54 | S217008566606 | DARFIELD WAY 2-9 | 214589 | Completed | 23a | High | Fire Extinguisher | The fire extinguishers in the boiler room and the gas meter room are out of service/test date according to the RGE contractors servicing labels attached to them. The last test date on these service labels is July 2012. It appears that the caretaker is not undertaking the monthly occupiers inspections of the fire fighting equipment in these buildings. | These fire extinguishers should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-02 14:54 | 2015-09-23 14:56 | 2015-09-02 14:54 | 2015-12-02 13:32 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:51 | S217012740006 | DARTREY TOWER 1-49 | 102975 | Completed | 23b | High | Emergency Lighting | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-10 | ESA training now complete - ongoing refresher to be organised by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-08-20 16:51 | 2013-09-10 16:53 | 2013-08-20 16:51 | 2014-07-15 16:30 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:49 | S217012740006 | DARTREY TOWER 1-49 | 102969 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed in the landings of the staircase, in the lift motor room and in the electrical room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-10 | serviced by chubb 22.5.2015 confirmed ok | 2015-08-11 | Fully Completed | Gillian Kennedy | 2013-08-20 16:49 | 2013-09-10 16:51 | 2013-08-20 16:49 | 2015-08-12 12:22 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 16:46 | S217012740006 | DARTREY TOWER 1-49 | 102966 | Completed | 19 | High | Dry or Wet Riser | The hasps used for the padlocks to secure the dry riser outlet boxes are broken on 7th, 12th and 13th floor levels. The dry riser outlets are now not secure and could be vandalised or damaged. | I would recommend that new hasps and padlocks are fitted to these dry riser outlet boxes so that the dry riser outlets are secured and therefore the fixed fire system is safe from vandalism or damage. | A & R Contract Management | Alex Bosman | 2013-09-10 | The following orders were raised to address this - please confirm that they have been completed. 13th flr - dry riser catch broken - order 201305184 12th flr - dry riser catch broken - order 201305168 7th flr - dry riser catch broken - 201305184 | 2015-11-19 | Fully Completed | Janice Wray | 2013-08-20 16:46 | 2013-09-10 16:48 | 2013-08-20 16:46 | 2015-11-30 17:29 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 15:17 | S217012740006 | DARTREY TOWER 1-49 | 102900 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-10 | Block included in 13/14 block electrical testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 15:17 | 2013-09-10 15:23 | 2013-08-20 15:17 | 2014-01-03 10:20 | -21 | In target | 2013-08-20 15:17 | 2014-01-09 10:19 | Janice Wray
DARTREY TOWER - 2013.03.01 | 2013-08-20 15:24 | S217012740006 | DARTREY TOWER 1-49 | 102903 | Completed | 5 | Low | Lifts | In all other TMO buildings with lifts there is a record book kept in the lift motor room showing the servicing and maintenance dates and any other comments of each lift? I could not find neither of the lift record books in this building's lift motor room. | Are there lift record books for the two lifts in this building? I would recommend that record books are provided because these show the servicing and maintenance dates along with any other comments etc. | A & R Contract Management | Alex Bosman | 2014-02-04 | Servcing records to be maintained and monitoured on keystone | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-20 15:24 | 2014-02-16 15:26 | 2013-08-20 15:24 | 2014-03-21 16:53 | -180 | In target
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:15 | S217012270003 | DENBIGH HOUSE | 189972 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the water pump room which abuts this building is out of service/test date according to the contractors servicing label attached to it. The last test date on the service label is November 2011. | The carbon dioxide portable fire extinguisher located in the water pump room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-01-13 | AP confirmed service complete 4.12.2015 | 2016-01-13 | Fully Completed | Maria Ares | 2015-03-26 13:15 | 2015-04-16 13:16 | 2015-03-26 13:15 | 2016-01-14 15:43 | -21 | In target
DENBIGH HOUSE -2015.02.26 | 2015-03-26 13:17 | S217012270003 | DENBIGH HOUSE | 189974 | Completed | 23b | Medium | Fire Extinguisher | The fire extinguisher in the water pump room is 3 years out of service/test. | Please can it be confirmed that the caretaker is checking this water pump room at the same time as he is undertaking his checks of the residential building? | A & R Contract Management | Alex Bosman |  | ESA inspects this area - confirmed | 2015-05-29 | Fully Completed | Janice Wray | 2015-03-26 13:17 | 2015-05-25 13:18 | 2015-03-26 13:17 | 2015-12-01 16:44 | -60 | In target
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:53 | S217008560001 | DIXON HOUSE | 244917 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building plus the lift motor room and other plant room areas. Keystone checked | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-21
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:58 | S217008560001 | DIXON HOUSE | 244921 | Active | 23c | High | Fire Extinguisher | Some of the fire extinguishers located in this building are out of test date according to the servicing labels attached to them. The carbon dioxide fire extinguishers in the roof level plant room have a last test date of 2008, others a last test date of March 2013. | All out of date service date fire extinguishers in this building should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-03-21
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:40 | S217010050004 | DOMBEY HOUSE | 158105 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed in each staircase enclosure of this building appears to have been installed in the last couple of years and these units do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are the installed emergency lighting systems being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting systems in this building are being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately including a discharge test and any defects etc rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-08-19 15:40 | 2014-09-09 15:41 | 2014-08-19 15:40 | 2015-12-15 11:19 | -21 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:39 | S217010470003 | EASTRY HOUSE | 196882 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase landings, on the external balconies and in the entrance hall area. | Please see note in bold below Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Keystone has EL at this block on "Servicing & Inspection Reporting" - but last servicing 09/13 | A & R Contract Management | Alex Bosman |  | serviced by chubb 14.5.2015 confirmed ok | 2015-08-11 | Fully Completed | Gillian Kennedy | 2015-05-13 15:39 | 2015-06-03 15:41 | 2015-05-13 15:39 | 2015-08-12 12:23 | -21 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:31 | S217002186603 | ELM PARK HOUSE PARKING | 122259 | Completed | 18a | High | Fire Extinguisher | There are dry powder and foam fire extinguishers located side by side in this car park. These two types of fire extinguisher should not be located together as one counter acts the other one. | I would recommend that the dry powder fire extinguishers are removed from this car park. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-01-02 09:31 | 2014-01-23 09:32 | 2014-01-02 09:31 | 2015-09-30 09:42 | -21 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:40 | S217002186603 | ELM PARK HOUSE PARKING | 122264 | Completed | 18b | Low | Fire Extinguisher | There are fire extinguishers provided in this car park, this car park does not have anybody employed to work in it and it is full covered by an automatic water sprinkler system. | All the fire extinguishers in this car park should be removed from this car park.(This area is covered by an automatic water sprinkler system. ) | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-01-02 09:40 | 2014-07-01 09:41 | 2014-01-02 09:40 | 2015-09-30 09:43 | -180 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:42 | S217002186603 | ELM PARK HOUSE PARKING | 122266 | Completed | 19 | Low | Hose Reels | There is a water hose reel provided in this car park, this car park does not have anybody employed to work in it and it is full covered by an automatic water sprinkler system. | This water hose reel in this car park should be removed from this car park. (This area is covered by an automatic water sprinkler system. ) | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-01-02 09:42 | 2014-07-01 09:44 | 2014-01-02 09:42 | 2015-09-30 09:46 | -180 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:47 | S217002186603 | ELM PARK HOUSE PARKING | 122269 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed in this car park does not appear on the electrical asset list as supplied by the TMO electrical engineer and there are no documents on site indicating that contractor servicing etc has been undertaken. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 28.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-01-02 09:47 | 2014-01-23 09:47 | 2014-01-02 09:47 | 2015-11-20 12:05 | -21 | In target
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:08 | S217010050009 | ESTELLA HOUSE | 158181 | Completed | 1 | High | Electrical Wire Check | The door of the ground floor electrical meter room of the staircase of flats 13 to 16 appears to be damaged and will not open | Can it please be confirmed that the electrical supply/distribution boards and any electrical wiring within this cupboard were periodic tested at the same time as the electrical wiring in the other staircases of this building. If there is no contractors label on the electrical components in this cupboard then a periodic electrical wiring test should be undertaken. | A & R Contract Management | Alex Bosman |  | 30/04/2015 - Completed Certificate held in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-08-20 11:08 | 2014-09-10 11:29 | 2014-08-20 11:08 | 2015-08-25 16:32 | -21 | In target
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:35 | S217010050009 | ESTELLA HOUSE | 158197 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. | The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB if required. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | Hard wired detectors installed during 5 year PIR progeram | 2015-03-23 | Fully Completed |  |  |  | 2014-08-20 11:35 | 2015-03-24 17:04
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:37 | S217008270001 | CAMBORNE MEWS (1-12) | 181046 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system currently installed on the means of escape routes of this building, | Can it please be conformed when the installed emergency lighting system in these 2 buildings were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266 Part 1. If the last test/service was more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP - COMPLETE 5.8.2015under separate blocks: Block 1- 1-6 Block 2- 7-12 Block 3- 13-18 Block 4- 19-24 Block 5- 25-30 Block 6- 31-36 . Have added this address now to cover entire estate 1-36 as well as the ones for separate blocks. | 2015-12-14 | Fully Completed | Maria Ares | 2015-01-30 12:37 | 2015-02-20 12:38 | 2015-01-30 12:37 | 2015-12-15 11:21 | -21 | In target
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 13:00 | S217008270001 | CAMBORNE MEWS (1-12) | 181059 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system currently installed on the means of escape routes of this building, | Can it please be conformed when the installed emergency lighting system in these 2 buildings were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266 Part 1. If the last test/service was more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | Duplicate action (181046) | 2015-12-01 | Fully Completed | Maria Ares | 2015-01-30 13:00 | 2015-02-20 13:01 | 2015-01-30 13:00 | 2015-12-02 13:40 | -21 | In target
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 16:10 | S217010550001 | WEST ROW 15-49 ODD | 243886 | Active | 15 | High | Emergency Lighting | The locations of the installed emergency escape lighting units on the means of escape routes of this property appear to be random and haphazard. | I would recommend that a full survey of the as installed emergency escape lighting system of this building is undertaken. This should then be compared to the requirements of BS 5266 Part 1 and any deficiencies or lack of coverage on the means of escape routes of this building then rectified. The newly installed system should then comply with the requirements in full of BS5266 Part1. | A & R Contract Management | Alex Bosman | 2016-03-15
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 16:12 | S217010550001 | WEST ROW 15-49 ODD | 243887 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on some of the landings of the staircases of this building. Keystone checked | Can it please be confirmed when the installed emergency lighting units/system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-15
FLATS 31 - 53 ADAIR ROAD - 2015.06.16 | 2015-06-26 14:40 | S217007860005 | ADAIR ROAD (31-53) | 203628 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - REFERRED TO BUT NOT FLAGGED UP FOR SERVICING BY CONTRACTOR | A & R Contract Management | Alex Bosman |  | serviced by chubb 19.5.2015 confirmed ok | 2015-08-11 | Fully Completed | Gillian Kennedy | 2015-06-26 14:40 | 2015-07-17 14:41 | 2015-06-26 14:40 | 2015-08-12 12:24 | -21 | In target
FLORENCE HOUSE - 2014.08.14 | 2014-08-20 10:33 | S217010050012 | FLORENCE HOUSE | 158160 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. | The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB if required. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | hard wired detectors installed during 5 year PIR program | 2015-03-23 | Fully Completed |  |  |  | 2014-08-20 10:33 | 2015-03-24 17:05
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:18 | S217010470002 | FORELAND HOUSE | 196910 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of this building, on the staircase landings, on the external balconies and in the entrance hall area. | SEE NOTE BELOW Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Keystone has EL at this block on "Servicing & Inspection Reporting" - but last servicing 03/13 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-05-13 16:18 | 2015-06-03 16:19 | 2015-05-13 16:18 | 2015-12-15 11:22 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-23 16:42 | S217008740001 | FRINSTEAD HOUSE | 245326 | Active | 5 | High | Miscellaneous | There was no access to the water pump room of this building because it is within the fenced off construction site area. | Can it please be confirmed that the water pumps are being serviced and maintained? | A & R Contract Management | Alex Bosman | 2016-03-22
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 10:08 | S217008740001 | FRINSTEAD HOUSE | 245409 | Active | 19 | High | Miscellaneous | There was a water sprinkler system installed in this building, I have been told that this system has been removed. | Can it please be confirmed that the water sprinkler system that was installed in this building has now been removed? This includes and sprinkler heads in the residents club room or other ground floor areas. | A & R Contract Management | Alex Bosman | 2016-03-23
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:47 | S217008740001 | FRINSTEAD HOUSE | 245449 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building plus the lift motor room and other plant room areas. Keystone checked | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-23
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:51 | S217008740001 | FRINSTEAD HOUSE | 245458 | Active | 23c | High | Dry or Wet Riser | There was no access to the dry riser inlet box so it is not known when the dry riser installed in this building was last serviced/tested. The inlet is presently within the construct site. Keystone checked, last service date recorded was July 2013. | Can it please be confirmed that the dry rising main installed in this building is up to date for servicing and testing? If it is not it should be serviced/tested immediately, with any defects found rectified. | A & R Contract Management | Alex Bosman | 2016-03-23
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:53 | S217008740001 | FRINSTEAD HOUSE | 245461 | Active | 23d | High | Lightning Protection | Keystone states that the lightning protection system installed on this building was lasted serviced in August 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-23 |  |  |  | Cyril Morris | 2016-02-24 11:53 | 2016-03-16 11:54 |  |  | 21 | 21 days overdue
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:55 | S217008740001 | FRINSTEAD HOUSE | 245463 | Active | 23e | High | Fire Extinguisher | The roof level carbon dioxide fire extinguisher was out of service/test date according to the contractors label fixed to the extinguisher. | This fire extinguisher should be serviced immediately and it confirmed that it on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-03-23 |  |  |  | Cyril Morris | 2016-02-24 11:55 | 2016-03-16 11:57 |  |  | 21 | 21 days overdue
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:09 | S217008850003 | GADSDEN HOUSE | 185129 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape routes of this building, on the staircase landings, the entrance hall areas, on the balconies and at the basement level in the electrical rooms. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 14.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-02-24 12:09 | 2015-03-17 12:10 | 2015-02-24 12:09 | 2015-11-20 12:06 | -21 | In target
GALSWORTHY HOUSE - 2015.06.03 | 2015-06-11 14:40 | S217008660003 | GALSWORTHY HOUSE | 201130 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of each part of this building, on the staircase landings, in the entrance hall areas and in the electrical rooms/cupboards. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO REFERENCE TO THIS ON KEYSTONE SERVICING | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 19.11.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-11 14:40 | 2015-07-02 14:42 | 2015-06-11 14:40 | 2015-11-27 10:58 | -21 | In target
GILLRAY HOUSE, MILMAN STREET, LONDON SW10 0BT - 2016.01.28 | 2016-02-16 11:22 | S217012760004 | GILLRAY HOUSE | 243711 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building also on the secondary staircase and in the lift motor rooms etc. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-15
GILLRAY HOUSE, MILMAN STREET, LONDON SW10 0BT - 2016.01.28 | 2016-02-16 11:24 | S217012760004 | GILLRAY HOUSE | 243712 | Active | 23b | High | Lightning Protection | Keystone states that the lightning protection system installed on this building was lasted serviced on the 15th September 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-15
GREAVES TOWER-2013.04.01 | 2013-08-16 16:06 | S217012740008 | GREAVES TOWER 4-62 | 102319 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-06 | Block included in 13/14 block testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 16:06 | 2013-09-06 16:14 | 2013-08-16 16:06 | 2015-11-27 12:41 | -21 | In target | 2013-08-16 16:06 | 2015-12-03 10:57 | Janice Wray
GREAVES TOWER-2013.04.01 | 2013-08-16 16:55 | S217012740008 | GREAVES TOWER 4-62 | 102349 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed on the landings of the staircase and in the lift motor room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing | A & R Contract Management | Alex Bosman | 2013-09-06 | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 16:55 | 2013-09-06 16:57 | 2013-08-16 16:55 | 2013-10-02 16:48 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:57 | S217012740008 | GREAVES TOWER 4-62 | 102351 | Completed | 23b | High | Emergency Lighting | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-06 | ESA training now complete - ongoing refresher to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-08-16 16:57 | 2013-09-06 16:59 | 2013-08-16 16:57 | 2014-07-15 16:32 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:59 | S217012740008 | GREAVES TOWER 4-62 | 102353 | Completed | 23c | High | Fire Extinguisher | The fire extinguisher in the roof level lift motor room is out of test date according to the servicing label attached to it, the last test date being July 2011. | This fire extinguisher should be serviced immediately and placed on the contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2013-09-06 | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 16:59 | 2013-09-06 17:00 | 2013-08-16 16:59 | 2013-10-02 16:49 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172140 | Completed | 1a | High | Electrical Wire Check | According to the contractors label on the main electrical supply/distribution board of this building the next fixed electrical wiring test is due in December of this year. | Can it please be confirmed whether the contractors or the TMO will be responsible for undertaking this buildings fixed electrical wiring test in December 2014? | A & R Contract Management | Alex Bosman |  | INSTALLATION TESTED AND CERT SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2014-12-01 09:25 | 2014-12-22 09:27 | 2014-12-01 09:25 | 2015-11-18 13:48 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:23 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172213 | Completed | 19b | High | Hose Reels | There are fire fighting hose reels in the basement boiler room of this building, these hose reels have not been serviced according to the servicing labels attached to each item since August 2012. I am told that these hose reels are due to be removed as part of the boiler room refurbishment work. | Please can it be confirmed that the fire fighting hose reels in the basement boiler room of this building are being removed as part of the boiler room refurbishment work? If they are not then they should be serviced immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | Confirmed fire hose reels will be removed during boiler works | 2015-12-01 | Fully Completed | Maria Ares | 2014-12-01 11:23 | 2014-12-22 11:29 | 2014-12-01 11:23 | 2015-12-02 13:41 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:30 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172214 | Completed | 19c | High | Dry or Wet Riser | The dry rising main in this building is overdue its service according to the last service certificate seen. | The dry rising main in this building should be serviced immediately with any defects found rectified. Is the more recent servicing sheet now available? | A & R Contract Management | Alex Bosman |  | Chub satisfactory test cert held carried out 27.4.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-12-01 11:30 | 2014-12-22 11:31 | 2014-12-01 11:30 | 2015-12-02 13:43 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:18 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172239 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed to cover the common parts of this building appears to be overdue for its annual service, maintenance and discharge test. | I would recommend that the installed emergency lighting system in this building is serviced, tested and a discharge test of the batteries in the units undertaken immediately. Any defects should be rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed service complete 9.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-12-01 12:18 | 2014-12-22 12:19 | 2014-12-01 12:18 | 2016-01-22 13:02 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:28 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172246 | Completed | 23e | Information Only | Fire Alarm | The fire alarm system installed in this building is due for a test/service and maintenance next month, November 2014. | I would recommend that the fire alarm engineers liaise with the contractors when they undertake the fire alarm system service next month. | A & R Contract Management | Alex Bosman |  | complete - system no longer present | 2015-11-17 | Fully Completed |  |  |  | 2014-12-01 12:28 | 2015-11-18 13:49
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:05 | S217012770016 | GRENFELL WALK 201-211 | 146401 | Completed | 23a | High | Emergency Lighting | The emergency lighting units presently installed on the means of escape routes of Upper Grenfell Walk do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are these installed emergency lighting units being serviced, tested and maintained. | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting units in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 12.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-06-02 13:05 | 2014-06-23 13:06 | 2014-06-02 13:05 | 2015-11-20 12:07 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 15:54 | S210008550002 | HARRIET HOUSE (1-20) | 197858 | Completed | 1 | High | Electrical Wire Check | The last 5 year electrical fixed wiring check on this buildings common parts electrical wiring was undertaken on the 19th December 2013. The retest date on the RGE contractors test label on the electrical supply board in the electrical room/cupboard by flat 1 states the retest date is the 19th February 2014. | According to this contractors label the periodic test of the fixed electrical wiring controlled by this electrical supply board is over due for testing. I would recommend that the reason for 2 month time period is investigated and this supply board and the fixed wiring rested if required. The dates on the other electrical supply board in the room by flat 10 are tested on the 19th December 2013 and to be retested in December 2018. | A & R Contract Management | Alex Bosman |  | 19/01/2015 - Completed - Certificate held in keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-05-19 15:54 | 2015-06-09 15:56 | 2015-05-19 15:54 | 2015-08-25 16:33 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:05 | S210008550002 | HARRIET HOUSE (1-20) | 197866 | Completed | 15 | Medium | Emergency Lighting | For your infor-mation There is presently no emergency escape lighting installed on the 2nd floor level external walkway/balcony nor is there any external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover this walkway/balcony. | I would recommend that if any work is undertaken on the light units of the 2nd floor level balcony/walkway then some emergency escape lighting is installed. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed these additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-19 16:05 | 2015-07-18 16:07 | 2015-05-19 16:05 | 2015-11-23 14:52 | -60 | In target | 2015-05-19 16:05 | 2015-11-29 14:52 | Janice Wray
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:07 | S210008550002 | HARRIET HOUSE (1-20) | 197867 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON ASSET REGISTER - but servicing not since Feb 2013 | A & R Contract Management | Alex Bosman |  | emergency light test carried out 5th august 2015 | 2015-11-17 | Fully Completed | Maria Ares | 2015-05-19 16:07 | 2015-06-09 16:08 | 2015-05-19 16:07 | 2015-11-18 13:54 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:25 | S217008750001 | HAZLEWOOD TOWER | 133658 | Active | 15 | High | Emergency Lighting | There are no emergency lighting units covering the rest area in the bulk storage room, this is a windowless area. | I would recommend that emergency lighting units are also fitted in this rest area as this is a windowless area. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2014-03-07 14:25 | 2014-03-28 14:25 |  |  | 740 | 740 days overdue
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:26 | S217008750001 | HAZLEWOOD TOWER | 133660 | Completed | 17 | High | Smoke Alarms | In flats 65, 68 and 41 the electrically power smoke detectors were damaged or missing. The residents said that a contractor had carried out work on these devices, then left and had not returned to finish the work. | I would recommend that the contractor who has undertaken work on the hardwired smoke detectors in the flats of this building is asked to return and complete the work started. I would recommend that the contractor is asked to confirm that all flats have working automatic detectors. Also installation certificates to BS 5839 Part 6 2012 model standards are provided for each flat. These should then be filed and may be needed if the building is audited by the enforcing authority under the Fire Safety Order. This issue was reported to TMO Health and Safety team whilst I was at the premises. | A & R Contract Management | Alex Bosman |  | ALARMS CORRECTLY INSTALLED AND CERTS WHERE APPORPRIATE SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2014-03-07 14:26 | 2014-03-28 14:27 | 2014-03-07 14:26 | 2015-11-18 13:56 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2016-01-27 15:00 | S217008750001 | HAZLEWOOD TOWER | 239850 | Active | 22 | Information Only | Miscellaneous | The occupier of the ground floor level retail area spoke with Mr Bosman during this assessment regarding the electrical supply board within this retail unit. | Mr Bosman gave the occupier of the retail area some information and was going to contact him again later when he returned to this office. | A & R Contract Management | Alex Bosman | 2016-02-25
HAZLEWOOD TOWER - 2014.2.20 | 2016-01-27 15:02 | S217008750001 | HAZLEWOOD TOWER | 239851 | Active | 23 | High | Emergency Lighting | According to Keystone, the computerised maintenance system the last annual service of the installed emergency lighting system in this building was undertaken in February 2014. | Can it please be confirmed that an emergency lighting system test/service has been undertaken since February 2015? If one was undertaken, was a full discharge test completed and any defects found rectified? If a test/service is overdue then one should be undertaken immediately with any defects rectified. | A & R Contract Management | Alex Bosman | 2016-02-25
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 15:51 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153352 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. This includes the fixed heaters suspendered from the ceiling in the main hall area. | A & R Contract Management | Alex Bosman |  | Test complete, remedial action to be scheduled | 2015-12-14 | Fully Completed | Maria Ares | 2014-07-17 15:51 | 2014-08-07 15:53 | 2014-07-17 15:51 | 2015-12-15 11:24 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 15:54 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153353 | Completed | 1b | High | Inspection Regime | Most of the portable electrical appliances in the store rooms/cupboards and the boiler cupboard of this building do not have Portable Appliance Testing (PAT) labels attached to them. According to the contractors labels the extension cable was last tested in December 2009 and the fans etc did not have labels on them | All the electrical items in the kitchen had in date PAT labels on them. All of the portable electrical appliances without an in date test label on them should be testing by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. | A & R Contract Management | Alex Bosman |  | PAT testing completed 16.9.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-07-17 15:54 | 2014-08-07 15:56 | 2014-07-17 15:54 | 2015-12-02 14:44 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 15:56 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153355 | Completed | 4 | High | Inspection Regime | According to the contractors label, T Brown Heating, on the gas boiler the last service of this boiler was undertaken on the 30th May 2012. | Can it please be confirmed if the gas boiler has been serviced and checked since the May 2012 service. If it has not then it should be serviced immediately with any defects identified rectified and the boiler then placed on a planned preventative maintenance schedule for annual servicing and testing. | A & R Contract Management | Alex Bosman |  | 21/07/2015 - Completed by K&T heating | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-07-17 15:56 | 2014-08-07 15:57 | 2014-07-17 15:56 | 2015-08-25 16:34 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 15:58 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153358 | Completed | 6 | High | Inspection Regime | There are mechanical extractors located in the kitchen and the main hall areas, the controls for these extractors are located in the kitchen on the wall to the right hand side of the roller shutter which covers the serving hatch. | Can it please be confirmed if these extractors are being serviced and checked in line with any manufactures instructions. If they are then no further action is needed, if they are not then I would recommend that servicing etc in accordance with the manufactures instructions is undertaken with any defects identified rectified. The extractors should then placed on a planned preventative maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman |  | RENEWED 6 INCH KITCHEN PULLCORD FAN. OVERHAULED 2 X 9 INCH FANS IN MAIN ROOM AT HIGH LEVEL . | 2015-11-17 | Fully Completed | Maria Ares | 2014-07-17 15:58 | 2014-08-07 15:59 | 2014-07-17 15:58 | 2015-11-18 13:57 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:05 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153367 | Completed | 17a | High | Miscellaneous | There is a roller shutter which covers the kitchen serving hatch, it appears that this roller shutter may be interfaced with the buildings fire alarm system. The controls for this roller shutter are located in the kitchen on the wall to the left hand side of the roller shutter This roller shutter could also be on a fusible link as back up. | Can it please be confirmed if this roller shutter covering the serving hatch from the kitchen is interfaced with the buildings fire alarm system, if it is, is it being tested with the buildings fire alarm system? If it is not then no further action is needed on this issue but is the fusible link being checked?. | A & R Contract Management | Alex Bosman |  | complete 06.08.2015 not linked to FA | 2015-11-19 | Fully Completed | Maria Ares | 2014-07-17 16:05 | 2014-08-07 16:07 | 2014-07-17 16:05 | 2015-11-20 12:12 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:09 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153372 | Completed | 23a | High | Fire Alarm | The last service of the installed fire alarm system in this premises was on the 3rd February 2014 by RGE. Is the new fire alarm contractor now serviced and tested this system in accordance with BS5839 Part 1 2013? | Can it please be confirmed that the installed fire alarm system in this premises is being serviced and tested? | A & R Contract Management | Alex Bosman |  | completed 06.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-07-17 16:09 | 2014-08-07 16:10 | 2014-07-17 16:09 | 2015-11-20 12:13 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:14 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153378 | Completed | 23c | High | Emergency Lighting | Is the emergency lighting system currently installed in this premises being annually serviced, tested and maintained by the electrical contractors. | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this premises is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 06.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-07-17 16:14 | 2014-08-07 16:15 | 2014-07-17 16:14 | 2015-11-20 12:23 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:19 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153382 | Completed | 23f | Information Only | Fire Extinguisher | The annual service of the fire extinguishers in this building is duein June 2014. | Ask the caretaker to check the fire extinguishers in this building in July to see if they have been serviced | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 3.12.2015 | 2015-12-14 | Fully Completed |  |  |  | 2014-07-17 16:19 | 2015-12-15 11:26
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:46 | S217008850001 | HOLMEFIELD HOUSE | 130778 | Completed | 18 | High | Fire Extinguisher | There are 3 Carbon Dioxide fire extinguishers in electrical room of this building with no discharge horn fitted to them, If a person were to use these extinguishers then they could suffer serious cold burns. | A check on all the fire fighting equipment in this building should be carried immediately and any defective equipment made safe. Please see item 23a below as well, most the fire extinguishers located in this building are out of test date for servicing, the last servicing date on the RGE labels being July 2012. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-02-19 16:46 | 2014-03-12 16:48 | 2014-02-19 16:46 | 2015-09-30 09:46 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:52 | S217008850001 | HOLMEFIELD HOUSE | 130787 | Completed | 1c | High | Communal Lighting | The covers of some of the lighting units located on the external walkways/balconies of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-02-19 16:52 | 2014-03-12 16:54 | 2014-02-19 16:52 | 2015-04-14 10:13 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:24 | S217008850001 | HOLMEFIELD HOUSE | 130832 | Completed | 15 | Information Only | Communal Lighting | I have been informed that there will be upgrading of the lighting in this building later this year, with new lighting units being installed. | If this is correct then can it please be confirmed that this new lighting incorporates emergency lighting units located as appropriate to BS5266 Part 1 2011. | A & R Contract Management | Alex Bosman |  | complete - all programmed works now monitored to ensure complience with current BS | 2015-11-17 | Fully Completed |  |  |  | 2014-02-20 09:24 | 2015-11-18 14:57
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:26 | S217008850001 | HOLMEFIELD HOUSE | 130837 | Completed | 18a | High | Fire Extinguisher | In the room numbered 116A there is an assortment of different types of fire extinguishers, these are all out of test date for servicing. This room is not being used at present. | I would recommend that all of the fire extinguishers located inside room 116A are removed. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-02-20 09:26 | 2014-03-13 09:30 | 2014-02-20 09:26 | 2015-09-30 09:48 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 10:50 | S217008850001 | HOLMEFIELD HOUSE | 130866 | Completed | 23a | High | Fire Extinguisher | Most of the carbon dioxide portable fire extinguisher located in the electrical rooms are out of test date according to the RGE servicing label attached to them. The last test /service date being the 11th July 2012. | These carbon dioxide fire extinguishers located in the ground floor level electrical rooms/ cupboards should be serviced immediately and it confirmed that they are on the external contractors maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed service complete 8.12.2015 | 2016-02-16 | Fully Completed | Maria Ares | 2014-02-20 10:50 | 2014-03-13 10:55 | 2014-02-20 10:50 | 2016-02-17 10:34 | -21 | In target
HORTENSIA HOUSE, FLATS 9 - 48 - 2015.06.15 | 2015-06-26 15:03 | S217002700004 | HORTENSIA HOUSE (9-48) | 203636 | Completed | 15 | Low | Emergency Lighting | 15 Low There is presently no emergency escape lighting installed in this building, on the staircase, the landings or in the entrance lobby area. There is also no external lighting outside the building which could provide borrowed lighting during the hours of darkness to cover the staircase etc. This is the way the building was converted/ constructed ie without emergency lighting. | I would recommend that emergency lighting units are installed on the landings, on the staircase and in the entrance lobby area as soon as financially possible. This is to provide illumination of the means of escape route if the normal lighting fail, the installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. Alex | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed | Maria Ares | 2015-06-26 15:03 | 2015-12-23 15:04 | 2015-06-26 15:03 | 2015-11-23 16:08 | -180 | In target | 2015-06-26 15:03 | 2015-11-29 16:07 | Janice Wray
HUNTER HOUSE - 2015.05.13 | 2015-05-27 09:33 | S217003720001 | HUNTER HOUSE | 198830 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the means of escape route of each part of this building, on the staircase landings, in the entrance hall areas and in the electrical rooms/cupboards. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? On Keystone Asset Register but last servicing date Aug 2013 | A & R Contract Management | Alex Bosman |  | el testing completed on 12/08/15 | 2015-11-17 | Fully Completed | Maria Ares | 2015-05-27 09:33 | 2015-06-17 09:35 | 2015-05-27 09:33 | 2015-11-18 14:58 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:23 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171846 | Completed | 1a | High | Electrical Wire Check | There is no contractor's label on the electrical supply/distribution board located in the lower ground floor level OCS office/staff area, stating when the fixed electrical wiring was last tested and the next retest date. | Can it be confirmed with the TMO electrical engineer if the fixed wiring in this room/area of the building has been periodic tested? If it has not be tested in the last 5 years then a fixed wiring test should be undertaken with any defects identified rectified and then this area of the building put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | 16/02/2015 - Completed - Certificate held in Keystone. | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-11-28 10:23 | 2014-12-19 10:44 | 2014-11-28 10:23 | 2015-08-25 16:36 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:45 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171848 | Completed | 1b | Medium | Communal Lighting | The covers of some of the lighting units in the buildings are dirty, thus affecting the level of illuminating from the bulb. | I would recommend that the covers of the lighting units in the buildings are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircases and on the balconies. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-11-28 10:45 | 2015-01-27 10:50 | 2014-11-28 10:45 | 2015-04-14 10:14 | -60 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:51 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171851 | Completed | 1c | Information Only | Electrical Wire Check | There are no contractor's labels on the electrical supply/distribution boards in electrical intake rooms 2 to 4 this building stating the last 5 year periodic test date and the retest date. The electrical asset list states that the fixed electrical wiring was last tested in November 2010 and is due for retesting in November 2015. | I would recommend that when the next electrical fixed wiring test is undertaken on the common parts electrical wiring in this building that the electrical contractors are asked to display contractors labels on each of the electrical supply/distribution boards in electrical intake rooms with the test and retest dates. | A & R Contract Management | Alex Bosman |  | TESTED AND CERTS SUPPLIED. ALL LABELLING PRESENT | 2015-11-17 | Fully Completed |  |  |  | 2014-11-28 10:51 | 2015-11-18 15:00
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:59 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171858 | Completed | 15a | High | Emergency Lighting | There is presently an emergency escape lighting system installed in this building but the locations of these units and their positioning appears to be random and haphazard. | I would recommend that a full survey of the as installed emergency escape lighting system in this building is undertaken. This should then be compared to the requirements of BS 5266 and any deficiencies or lack of coverage then rectified. | A & R Contract Management | Alex Bosman |  | RMA inspection complete current system confirmed as designed; upgrade works to current standards submitted for future consideration | 2015-12-14 | Fully Completed | Maria Ares | 2014-11-28 10:59 | 2014-12-19 11:00 | 2014-11-28 10:59 | 2015-12-15 11:26 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:00 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171859 | Completed | 15b | High | Emergency Lighting | 15The covers of some of the emergency lighting units currently installed in this building are dirty. This means that the charger indicator light is not clearly visible as required by the British Standard. | I would recommend that the covers of the emergency lighting units currently installed in the building are cleaned, replaced or the charger indicator lights are replaced with brighter ones so that the neon indicators are easily seen. This will help the caretakers to undertake the monthly checking of the emergency lighting system. | A & R Contract Management | Alex Bosman |  | Complete. | 2015-08-07 | Fully Completed | Gillian Kennedy | 2014-11-28 11:00 | 2014-12-19 11:01 | 2014-11-28 11:00 | 2015-08-10 16:03 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:06 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171861 | Active | 17a | High | Fire Alarm | There is a fire alarm system installed in this building, which is limited to two different areas of the building, the electrical intake rooms and the roof areas. The automatic detectors operate the smoke vents in the roofs and there are separate detectors which cover the electrical intake rooms only. There is no warning system and the locations of these installed devices and their positioning indicates that they are for a bespoke reason only. The control panel for this installed fire alarm system is located in the now disused reception area of Grenfell Tower. | 1.The reception area of Grenfell Tower is being refurbished, how is access to the fire alarm control panel being maintained? 2.It is assumed that the present fire alarm system is fully operational, if it is not repairs to the installed fire alarm system must be undertaken immediately. 3.Will the fire alarm control panel be relocated in the future? 4.To comply with the requirements of the Building Regulations the smoke vents located in the glazed roof areas of this | A & R Contract Management | Alex Bosman
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:19 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171867 | Active | 17a ( continued) | High | Fire Alarm | It is a serious offence under the Fire Safety Order not to maintain an installed fire alarm system. building must be linked to local automatic smoke detection, how will this requirement be achieved? | 4.To comply with the requirements of the Building Regulations the smoke vents located in the glazed roof areas of this 5.How will the fire alarm system devices installed in the electrical intake rooms be controlled and monitored? | A & R Contract Management | Alex Bosman
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:22 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171868 | Active | 17b | High | Fire Alarm | How is the fire alarm system in this building being monitored now that the Grenfell Tower reception is not in existence? | I would recommend that the fire alarm control panel for the detectors of the smoke vents and the ones located in the electrical intake rooms is connected to a monitoring stationed so in the event of an activation of the system the fire service or on duty caretaker can be informed. | A & R Contract Management | Alex Bosman
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:26 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171880 | Completed | 19b | High | Dry or Wet Riser | The padlocks securing/locking the water ring main boxes above all of the dry risers at the lower ground floor level are either missing or not Fire Brigade (FB) padlocks. | The boxes housing the water main and the dry riser inlets and outlets should be checked and any found not secured with FB padlocks should have FB padlocks fitted asap. | A & R Contract Management | Alex Bosman |  |  | 2015-12-11 | Fully Completed | Janice Wray | 2014-11-28 11:26 | 2014-12-19 11:27 | 2014-11-28 11:26 | 2015-12-14 11:44 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:28 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171881 | Completed | 19c | High | Miscellaneous | There are automatic opening vents in the glazed ceiling of this building operated by smoke detectors. It is a serious offence under the Fire Safety Order not to maintain an installed fixed fire system. | Can it please be confirmed that these automatic opening vents are fully functional and in good working order? If they are not then a contractor should repair these automatic opening vents immediately. | A & R Contract Management | Alex Bosman |  | Colt confirmed all works complete and AOVs operational 3.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-11-28 11:28 | 2014-12-19 11:29 | 2014-11-28 11:28 | 2015-12-15 11:27 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:35 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171884 | Completed | 19d | High | Miscellaneous | The reception area of Grenfell Tower is being refurbished and the control panel for the automatic opening vents in the glazed ceiling of this building and the other 2 nearby ones repositioned. | In the interim I would recommend that the fire service manual control switches located by the entrance door to each section of this building area checked and these are used to open the roof vents if needed. When the control panel for all of the automatic opening vents is repositioned then it should be fully tested before a commissioning certificate issue for it by the contractor. The control panel must be located/positioned so that it can easily be used and accessed but must not be in a location where it will be vandalised | A & R Contract Management | Alex Bosman |  | Colt confirmed firemans swith fully working 3.12.201 | 2015-12-14 | Fully Completed | Maria Ares | 2014-11-28 11:35 | 2014-12-19 11:37 | 2014-11-28 11:35 | 2015-12-15 11:28 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:39 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171890 | Completed | 19f | Information Only | Miscellaneous | The last service and test on the water ring main was undertaken by M and P Fire Protection Limited on the 29th November 2013 and is therefore due to be undertaken again this month. | I would recommend that it is confirmed that the contractor will be servicing and testing the water ring main in the lower ground floor level of this building this month. | A & R Contract Management | Alex Bosman |  | completed 09.07.15 | 2015-11-19 | Fully Completed |  |  |  | 2014-11-28 11:39 | 2015-11-20 12:26
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:41 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171893 | Active | 21 | High | Miscellaneous | There are automatic ventilation systems installed in this building. | Have the caretakers and any duty or on call managers/housing officers etc been given specific instructions on how to use the installed smoke ventilation system of this building? This instruction should also be included how to use the fire service manual control boxes located by the entrance doors to each section of this building. | A & R Contract Management | Alex Bosman
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:43 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171894 | Active | 23a | High | Fire Alarm | There is a fire alarm system installed in this building. | Can the TMO electrical engineer and the electrical contractor please confirm that the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc found rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman
HURSTWAY WALK - 2014.11.13 | 2014-11-28 12:02 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171909 | Completed | 23c | High | Miscellaneous | There are automatic smoke ventilation systems installed in this building. | Are the automatic ventilation systems installed in this building being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Colt confirmed service complete 3.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-11-28 12:02 | 2014-12-19 12:03 | 2014-11-28 12:02 | 2015-12-15 11:29 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 12:05 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171912 | Completed | 23e | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in electrical intake rooms 8 and 10 are out of service date according to the contractor's servicing labels attached to them, the last test date being July 2013. | These two carbon dioxide fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP 13.8.2015 confirmed no extingishers on site | 2015-11-26 | Fully Completed | Maria Ares | 2014-11-28 12:05 | 2014-12-19 12:06 | 2014-11-28 12:05 | 2015-11-27 11:20 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 11:20 | S217002640001 | INGELOW HOUSE | 204022 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed on the means of escape routes of this building, on the staircase landings, in the entrance hall area or in the lower ground floor level of this building. This is a five storey building. | As soon as financially possible I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-06-30 11:20 | 2015-11-23 16:18 |  |  | 2015-06-30 11:20 | 2015-11-29 16:18 | Janice Wray
INGELOW HOUSE - 2015.06.15 | 2015-06-30 16:18 | S217002640001 | INGELOW HOUSE | 204135 | Completed | 17c | High | Fire Alarm | There is no fire alarm layout diagram or zone chart displayed next to the fire alarm control panel. | I would recommend that a layout and zone diagram of the as installed fire alarm system is displayed next to the fire alarm panel. | A & R Contract Management | Alex Bosman |  | AP producing zone chart | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-30 16:18 | 2015-07-21 16:19 | 2015-06-30 16:18 | 2015-12-15 11:29 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 16:19 | S217002640001 | INGELOW HOUSE | 204136 | Completed | 23a | High | Fire Alarm | There is a fire alarm system installed to cover the lower ground floor level area of this building, according to the logbook next to the fire alarm control panel the last service/test of this system was undertaken on the 24th April 2010 | Please can it be confirmed that this fire alarm system has been serviced/tested and inspected by a fire alarm engineer since this last recorded test date. If it is has not then a test/service should be undertaken immediately and any defects found rectified and then the system with locations of devices etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-30 16:19 | 2015-07-21 16:20 | 2015-06-30 16:19 | 2015-12-02 13:46 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 16:23 | S217002640001 | INGELOW HOUSE | 204140 | Completed | 23c | High | Fire Extinguisher | The foam and carbon dioxide fire extinguishers located at the lower ground floor level of this building are out of test date according to the servicing labels attached to them. The last test date on these labels being in December 2010. | The fire extinguishers located at this lower ground floor level should be serviced immediately and it confirmed that they are on the external contractors maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-30 16:23 | 2015-07-21 16:27 | 2015-06-30 16:23 | 2015-12-15 11:30 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 16:28 | S217002640001 | INGELOW HOUSE | 204144 | Completed | 23d | High | Emergency Lighting | It is possible that some of the lower ground floor level lights are combined normal and emergency lights, it is not known when or if these lights have been tested or serviced. | Please can it be confirmed if any of the lighting units at the lower ground floor level are combined normal and emergency lights? If any are combined lighting units have these been tested or serviced in the last year including a discharge test? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-30 16:28 | 2015-07-21 16:31 | 2015-06-30 16:28 | 2015-12-15 11:31 | -21 | In target
JEAN DARLING HOUSE - 2013.05.01 | 2013-08-19 14:59 | S217012760006 | JEAN DARLING HOUSE | 102610 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-09 | Block included in 14/15 communal electrical testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-19 14:59 | 2013-09-09 15:01 | 2013-08-19 14:59 | 2014-03-21 16:40 | -21 | In target
JEAN DARLING HOUSE - 2013.05.01 | 2013-08-19 15:01 | S217012760006 | JEAN DARLING HOUSE | 102611 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-09 | Added to the Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-19 15:01 | 2013-09-09 15:06 | 2013-08-19 15:01 | 2013-10-02 17:10 | -21 | In target
JEAN DARLING HOUSE - 2013.05.01 | 2013-08-19 15:07 | S217012760006 | JEAN DARLING HOUSE | 102616 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the emergency lighting system and the buildings structure. | Can it be confirmed that the monthly occupiers tests of the emergency lighting system and the buildings structure are being undertaken, with the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-09 | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-19 15:07 | 2013-09-09 15:09 | 2013-08-19 15:07 | 2015-02-27 14:48 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:14 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181506 | Completed | 1a | High | Electrical Wire Check | According to the contractor's label on the buildings electrical supply/distribution board the last 5 year electrical fixed wiring test for the electrical wiring of this building was meant to be undertaken in March 2011 | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | RMA test complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-02-03 10:14 | 2015-02-24 10:15 | 2015-02-03 10:14 | 2015-12-15 11:32 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:26 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181523 | Active | 23a | High | Fire Extinguisher | The fire extinguishers located in this premises are out of test date according to the contractor's servicing labels attached to them. The last test date being June 2011. | The 2 fire extinguishers and the fire blanket located in this premises should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:28 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181525 | Active | 23b | High | Fire Alarm | Is the installed fire alarm system in this premises being serviced and tested by a fire alarm contractor in accordance with BS5839 Part 6 2013? | If it is not I would recommend that the instated fire alarm system in this premises is serviced and tested immediately with any defects rectified and the system placed on a planned preventive maintenance programme. If the installed fire alarm system is being serviced etc then no action is needed but a fire logbook should be available on the premises. | A & R Contract Management | Alex Bosman
KELFIELD COURT - 2015.06.03 | 2015-06-11 15:22 | S217009010001 | KELFIELD COURT | 201155 | Completed | 23a | High | Emergency Lighting | There has been in the last couple of years a new emergency lighting units/system installed on the means of escape route of each part of this building, on the staircase landings, in the entrance hall areas and in the electrical rooms/cupboards. | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? NO SERVICING CERTIFICATE ON KEYSTONE - BUT REFERENCE TO SYSTEM | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-11 15:22 | 2015-07-02 15:23 | 2015-06-11 15:22 | 2015-12-02 13:49 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:23 | B217009120001 | KENSAL HOUSE | 102868 | Completed | 17e | High | Fire Alarm | Inside the entrance door to the estate off Ladbroke Grove there is recessed into the wall a control/indicator panel for the fire detection devices located within the buildings. The information on the display is hard to see because it is worn. | I would recommend that the present display is cleaned up if possible so that the information is easier to see or a new display provided if the present one cannot be cleaned up. | A & R Contract Management | Alex Bosman | 2013-09-10 | completed 15.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-08-20 14:23 | 2013-09-10 14:46 | 2013-08-20 14:23 | 2015-11-20 12:28 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:10 | B217009120001 | KENSAL HOUSE | 102857 | Completed | 15b | High | Emergency Lighting | Some of the neon/charger indicator lights cannot be seen on what I think should be the emergency lighting units installed within these buildings. This includes the units in the ground floor level electrical cupboards. | I would recommend that the emergency lighting systems/units currently installed in the staircases of these buildings and in the electrical cupboards are checked to see that units are installed to the requirements of BS 5266 Part 1. If it is found that there are not any emergency lighting units installed/sited in some areas as required by the BS then some should be installed in these locations as soon as possible. | A & R Contract Management | Alex Bosman | 2013-09-10 | completed 15.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-08-20 14:10 | 2013-09-10 14:14 | 2013-08-20 14:10 | 2015-11-20 12:29 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 09:22 | B217009120001 | KENSAL HOUSE | 102715 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on these buildings electrical supply boards and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of these buildings. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of these buildings were last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the buildings then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-10 | Block included on 13/14 testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 09:22 | 2013-09-10 09:29 | 2013-08-20 09:22 | 2013-12-10 17:28 | -21 | In target | 2013-08-20 09:22 | 2013-10-09 15:14 | Alex Bosman
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:51 | B217009120001 | KENSAL HOUSE | 102882 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide portable fire extinguishers located in the ground floor electrical cupboards of each of the staircases and the 4 externally accessed rooms are out of test date according to the servicing labels attached to them. The last test date being February 2011 on each extinguisher. | All the carbon dioxide portable fire extinguishers located in these ground floor level electrical cupboards and the 4 externally accessed rooms should be serviced immediately and it confirmed that they are on the external contractors maintenance schedule. The extinguishers in the internally accessed electrical cupboards could be removed and not serviced etc or replaced, as well as the one in the externally accessed room which is completely empty. The external contractor's maintenance schedule should be amended to show these changes. | A & R Contract Management | Alex Bosman | 2013-09-10 | completed 15.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-08-20 14:51 | 2013-09-10 14:55 | 2013-08-20 14:51 | 2015-11-20 12:30 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:56 | B217009120001 | KENSAL HOUSE | 102885 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of these buildings does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-10 | Added to Keystone asset register | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 14:56 | 2013-09-10 14:59 | 2013-08-20 14:56 | 2013-10-02 17:17 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 15:00 | B217009120001 | KENSAL HOUSE | 102888 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman | 2013-09-10 | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-20 15:00 | 2013-09-10 15:02 | 2013-08-20 15:00 | 2015-02-27 14:49 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 15:13 | B217009120001 | KENSAL HOUSE | 102899 | Completed | 23f | Medium | Dry or Wet Riser | There is a dry rising main located with the staircase of flats 8 to 16 only, it states on the asset register given to me that this dry riser is on a maintenance contract. But the dry riser boxes look as though they have not been opened for some time. Also there is no signage for this dry riser indicating its location etc by the staircase entrance door as in other TMO buildings with dry risers installed within them. | I would recommend that the TMO engineer is asked to check when the last service/test on this dry riser was undertaken? If it is outside its 6 monthly test date then testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of inlets and outlets etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-18 | To be included in 13/14 testing program and added asset register | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-20 15:13 | 2013-10-19 15:14 | 2013-08-20 15:13 | 2014-03-21 16:51 | -60 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:23 | S217007970011 | KENSAL COMMUNITY OFFICE | 181612 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply/distribution boards located in the OCS offices and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this area. The fixed wiring in the community area has been undertaken recently. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the OCS offices was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA test complete and remidail actions submitted | 2016-01-13 | Fully Completed | Maria Ares | 2015-02-03 12:23 | 2015-02-24 12:30 | 2015-02-03 12:23 | 2016-01-14 15:50 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:31 | S217007970011 | KENSAL COMMUNITY OFFICE | 181613 | Completed | 1b | High | Electrical Wire Check | Most of the portable electrical appliances in the community area do not have portable appliance testing labels attached to them, all of the electrical items in the kitchen apart from the fridge freezer for instance. In the OCS offices all of the electrical items have PAT labels on them. | All of the portable electrical appliances without an in date test label on them should be testing by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. | A & R Contract Management | Alex Bosman |  | PAT testing completed 2/9/15 & 1/10/15 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-03 12:31 | 2015-02-24 12:32 | 2015-02-03 12:31 | 2015-12-02 14:45 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:32 | S217007970011 | KENSAL COMMUNITY OFFICE | 181614 | Completed | 1c | High | Miscellaneous | There is an electrical water heater located in both the kitchen of the community area and OCS office, it is not known if these electrical emersion heaters need to be inspected /serviced. | Can it please be confirmed that if these electrical water heaters needs to be tested/serviced/inspected as per any manufacturers guidance? If these items have not been serviced/ tested/inspected as required then I would recommend that these checks etc are undertaken and any defects found rectified. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA service completed | 2016-01-13 | Fully Completed | Maria Ares | 2015-02-03 12:32 | 2015-02-24 12:34 | 2015-02-03 12:32 | 2016-01-14 16:03 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:41 | S217007970011 | KENSAL COMMUNITY OFFICE | 181621 | Completed | 18 | Information Only | Fire Extinguisher | Presently I believe that there is overprovision of fire fighting equipment in these areas. There is a fire blanket located in each of the kitchens, this item of fire equipment should remain in place. | If a water and carbon dioxide fire extinguisher was provided just inside the entrance door of each area then these would provide an adequate number of fire extinguishers in each area. As these are small areas the carbon dioxide fire extinguisher can be used to cover the whole area including the kitchens, the electrical boards and any other electrical equipment in each area. | A & R Contract Management | Alex Bosman |  | COMPLETED - NOTED FOR FUTURE ASSESSMENT | 2015-11-17 | Fully Completed |  |  |  | 2015-02-03 12:41 | 2015-11-18 15:01
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:46 | S217007970011 | KENSAL COMMUNITY OFFICE | 181626 | Completed | 23b | High | Fire Alarm | Is the installed fire alarm system in both parts of these premises being serviced and tested by a fire alarm contractor in accordance with BS5839 Part 1 2013? Part servicing and testing of the OCS area was undertaken on the 16th June 2014 | If it is not I would recommend that the installed fire alarm system in both parts is serviced and tested immediately with any defects rectified and the whole system placed on a planned preventive maintenance programme. The fire logbook next to the fire panel should be filled in, to show testing and servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-03 12:46 | 2015-02-24 12:47 | 2015-02-03 12:46 | 2015-12-02 14:02 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:48 | S217007970011 | KENSAL COMMUNITY OFFICE | 181627 | Completed | 23c | High | Emergency Lighting | Is the emergency lighting system currently installed in these premises being annually serviced, tested and maintained by the electrical contractors. | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in both areas is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 23.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-03 12:48 | 2015-02-24 12:48 | 2015-02-03 12:48 | 2015-12-02 14:04 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:50 | S217007970011 | KENSAL COMMUNITY OFFICE | 181629 | Completed | 23e | High | Fire Extinguisher | According to the contractors labels on the fire extinguishers in both areas the last servicing date was July 2012 or July 2013 the extinguishers have "Out of test date need replacing" on the contractor's labels. Please see item 8 above as well. | The fire extinguishers in both areas should be serviced or replaced so that there is a water and a carbon dioxide fire extinguisher is by the entrance door and a fire blanket in the kitchen. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 24.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-03 12:50 | 2015-02-24 12:51 | 2015-02-03 12:50 | 2015-12-02 14:04 | -21 | In target
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 11:48 | S217002180001 | KEPPEL HOUSE | 200435 | Completed | 15 | High | Emergency Lighting | As soon as financially possible There is presently no emergency escape lighting installed in this building on the external walkways/balconies. | I would recommend that as soon as financially possible consideration is given to fitting emergency escape lighting on the means of escape routes of this building. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the additional emergency lighting units should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed | Maria Ares | 2015-06-08 11:48 | 2015-06-29 12:34 | 2015-06-08 11:48 | 2015-11-23 14:57 | -21 | In target | 2015-06-08 11:48 | 2015-11-29 14:56 | Janice Wray
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 12:39 | S217002180001 | KEPPEL HOUSE | 200473 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the roof level lift motor room and the ground floor level cleaners room are out of test date according to the contractors servicing label attached to them. The last test date according to the RGE service labels on the lift motor room one was the 1st March 2013 and the cleaners room one January 2014. | These fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 28.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-08 12:39 | 2015-06-29 12:40 | 2015-06-08 12:39 | 2015-12-15 11:32 | -21 | In target
KINGSLEY HOUSE, BEAUFORT STREET, LONDON SW3 5BD - 2016.02.11 | 2016-04-04 14:41 | S217000310001 | KINGSLEY HOUSE | 252353 | Active | 5a | High | Miscellaneous | In the roof space area of this building there is extraction/ventilation equipment installed. | Can it be confirmed that any maintenance or servicing is being undertaken as per the manufactures requirements for the roof space extraction systems. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman | 2016-05-09
KINGSLEY HOUSE, BEAUFORT STREET, LONDON SW3 5BD - 2016.02.11 | 2016-04-04 14:58 | S217000310001 | KINGSLEY HOUSE | 252370 | Active | 14a | High | Miscellaneous | Are there any fire dampers or filters installed in the extraction units located in the roof space areas? | If any dampeners or filters are installed within the roof space area extraction systems are these on a maintenance and servicing contract, if applicable? | A & R Contract Management | Alex Bosman | 2016-05-09
KINGSLEY HOUSE, BEAUFORT STREET, LONDON SW3 5BD - 2016.02.11 | 2016-04-04 15:08 | S217000310001 | KINGSLEY HOUSE | 252375 | Active | 15 | High | Emergency Lighting | There was a new emergency lighting system/units installed to cover the means of escape route of each staircase of this building. On the staircase landings and also in the lower ground floor electrical rooms/cupboards and in the roof space areas. | I would recommend that the buildings file is check to see if all the correct documentation is contained within it reference these new emergency lighting systems/units. There should be design, installation and completion certificates etc to the model standards in BS 5266 Part 1 2011. If these are not available then the contractor who installed the systems should be asked to provide all the relevant documentation including as installed drawings. This is evidence of correct installation etc if the enforcing authorities undertake an audit of this building and question the installation. | A & R Contract Management | Alex Bosman | 2016-05-09
KINGSLEY HOUSE, BEAUFORT STREET, LONDON SW3 5BD - 2016.02.11 | 2016-04-04 15:15 | S217000310001 | KINGSLEY HOUSE | 252377 | Active | 23c | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of each staircase of this building, on the landings of the staircases and in the entrance hall areas. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-05-09
LACLAND HOUSE, MILMAN STREET, LONDON SW10 0BP - 2016.01.28 | 2016-02-19 16:18 | S217012760002 | LACLAND HOUSE | 244688 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building also on the secondary staircase and in the lift motor rooms etc. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-21
LACLAND HOUSE, MILMAN STREET, LONDON SW10 0BP - 2016.01.28 | 2016-02-19 16:19 | S217012760002 | LACLAND HOUSE | 244689 | Active | 23b | High | Lightning Protection | Keystone states that the lightning protection system installed on this building was lasted serviced on the 7th September 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-21
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:06 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164641 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply/distribution board for this area and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this area of the building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this area of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. A | A & R Contract Management | Alex Bosman |  | There is a compliant certification for this property.Test complete cert supplied April2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-10-09 11:06 | 2014-10-30 11:08 | 2014-10-09 11:06 | 2015-12-02 14:05 | -21 | In target
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:13 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164645 | Completed | 12b | Medium | Miscellaneous | There is a metal roller shutter which covers the door to the end meeting room, the old caretaker's office. | Can it please be confirmed that this roller shutter including the electrical motor is being serviced and maintained in accordance with the manufacturers instructions. If it is not then a contractor should service/test this roller shutter and any electrical components associated with it. | A & R Contract Management | Alex Bosman | 2016-01-21 | Shutter now removed | 2016-01-21 | Fully Completed | Maria Ares | 2014-10-09 11:13 | 2014-12-08 11:20 | 2014-10-09 11:13 | 2016-01-22 13:05 | -60 | In target
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:24 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164653 | Completed | 15 | Information Only | Emergency Lighting | 1Recommendation There is presently no emergency lighting installed within this premises as previously this office area was used during day time hours only. | If this premises is to be used during the hours of darkness then an emergency lighting system in accordance with BS 5266 Part 1 2011 must be installed within it. Lanc West Manager confirms area used during hours of darkness so EL required. | A & R Contract Management | Alex Bosman |  | complete - include within programmed works | 2015-11-17 | Fully Completed |  |  |  | 2014-10-09 11:24 | 2015-11-18 15:02
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-06 15:54 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164181 | Completed | 1b | Information Only | Electrical Wire Check | There is no contractor's label on the electrical supply/distribution board for this premises indicating the date of the last 5 year electrical fixed wiring test and the next test date. The wiring was last tested on the 21st July 2014 and is due a retest in July 2019. | I would recommend that a label is placed on the electrical supply/distribution board with these dates on them. | A & R Contract Management | Alex Bosman |  | complete - include within programmed works | 2015-11-17 | Fully Completed |  |  |  | 2014-10-06 15:54 | 2015-11-23 14:28 |  |  | 2014-10-06 15:54 | 2015-11-29 14:28 | Janice Wray
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 09:08 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164219 | Completed | 12c | Medium | Miscellaneous | There are metal roller shutters which cover the entrance doors and the windows of this premises. | Can it please be confirmed that these roller shutters including the electrical motors are being serviced and maintained in accordance with the manufacturers instructions. If they are not then a contractor should service/test these roller shutters and any electrical components associated with them. | A & R Contract Management | Alex Bosman | 2016-01-21 | main entrance added to R & B Doors maintenance which is due in January. Window shutters are manual and do not require servicing | 2016-01-21 | Fully Completed | Maria Ares | 2014-10-07 09:08 | 2014-12-06 09:11 | 2014-10-07 09:08 | 2016-01-22 13:06 | -60 | In target
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 11:18 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164249 | Active | 17a | High | Fire Alarm | There is no zoning diagram or text indicating the zones of the installed fire alarm system next to the fire alarm control panel. As this is a simple system a text sheet will suffice. | I would recommend that a zoning diagram or text indication the zones of the installed fire alarm system is displayed next to the fire alarm control panel. | A & R Contract Management | Alex Bosman
LEDBURY HOUSE | 2014-05-19 09:57 | S217012270005 | LEDBURY HOUSE | 144326 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the electrical supply rooms and the lift motor room , Block 1-10 were last tested in November 2011 The extinguishers were removed from Block 1-18 | These carbon dioxide fire extinguishers should be serviced immediately and placed on the contractor's maintenance schedule. Alternatively they could be removed from the building and not replaced. | A & R Contract Management | Michael Lyons | 2016-02-16 | AP confirmed service complete 8.12.2015 | 2016-02-16 | Fully Completed | Maria Ares | 2014-05-19 09:57 | 2014-06-09 10:04 | 2014-05-19 09:57 | 2016-02-17 11:56 | -21 | In target
LEDBURY HOUSE | 2015-03-26 16:08 | S217012270005 | LEDBURY HOUSE | 190063 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed in this building, on the landings of the staircases or in the entrance hall areas ie the means of escape routes/common parts of this building. One part of this building is five storey's in height. | I would recommend that emergency lighting units are installed on the means of escape routes/in the common parts of this building, ie the staircase enclosures. This is to provide illumination of the means of escape routes if the normal lighting fails. The installation should be to British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | complete - include within programmed works | 2015-11-17 | Fully Completed |  |  |  | 2015-03-26 16:08 | 2015-11-23 14:44 |  |  | 2015-03-26 16:08 | 2015-11-29 14:43 | Janice Wray
LEDBURY HOUSE | 2015-03-26 16:16 | S217012270005 | LEDBURY HOUSE | 190068 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the lift motor room located at the roof level is out of service/test date according to the contractors servicing label attached to it. The last test date on the service label is November 2011. | The carbon dioxide portable fire extinguisher located in the lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed service complete 8.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2015-03-26 16:16 | 2015-04-16 16:17 | 2015-03-26 16:16 | 2016-01-22 13:07 | -21 | In target
LEDBURY HOUSE | 2015-03-26 16:17 | S217012270005 | LEDBURY HOUSE | 190070 | Completed | 23b | High | Emergency Lighting | There are emergency lighting units installed in the roof level lift motor room, in the lower ground floor level electrical room and in the under stairs cupboard of the staircase of flats 11 to 18. These emergency lighting units do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are these installed emergency lighting units being serviced, tested and maintained, including a discharge test undertaken? | Can it please be confirmed that the installed emergency lighting units in this building is being serviced, tested and a discharge test of the units batteries is being undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-03-26 16:17 | 2015-04-16 16:19 | 2015-03-26 16:17 | 2015-12-15 11:33 | -21 | In target
LEDBURY HOUSE | 2015-03-26 16:21 | S217012270005 | LEDBURY HOUSE | 190078 | Completed | 23d | Medium | Fire Extinguisher | The fire extinguisher in the lift motor room is 3 years out of service/test. | Please can it be confirmed that the caretaker is checking this area? | A & R Contract Management | Alex Bosman |  |  | 2015-05-29 | Fully Completed | Janice Wray | 2015-03-26 16:21 | 2015-05-25 16:22 | 2015-03-26 16:21 | 2015-12-01 16:45 | -60 | In target
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:18 | S217012770017 | CLARENDON WALK 1-24 | 219183 | Active | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on each of the staircase landings of this building, the means of escape routes from the building. | Can it please be conformed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - reference to inspection in 2010 - nothing more recent Alex | A & R Contract Management | Alex Bosman
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:22 | S217012770017 | CLARENDON WALK 1-24 | 219187 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the ground floor level electrical room/cupboard is out of service/test date according to the contractors servicing label attached to it. The last test date on this RGE service label was November 2011. | This carbon dioxide fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. Alternatively it could be removed from this area of the building and not serviced etc or replaced, the external contractor's maintenance schedule should be amended to show this change. | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed servbice complete 1.2.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2015-09-30 12:22 | 2015-10-21 12:23 | 2015-09-30 12:22 | 2016-02-17 10:35 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:27 | S217012770017 | CLARENDON WALK 1-24 | 212619 | Completed | 1 | High | Miscellaneous | There is no contractors label on the electrical supply boards located in the electrical room under the end staircase, off the public road. The other supply boards have in date contractors labels on them. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this part of the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | TESTED AND CERTS SUPLPIED. ALL LABELLING PRESENT | 2015-11-17 | Fully Completed | Maria Ares | 2015-08-19 10:27 | 2015-09-09 10:33 | 2015-08-19 10:27 | 2015-11-18 15:05 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:40 | S217012770017 | CLARENDON WALK 1-24 | 212627 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on each of the staircase landings of this building, the means of escape routes from the building. | Can it please be conformed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - reference to inspection in 2010 - nothing more recent | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed service complete 1.2.2016 | 2016-02-16 | Fully Completed | Maria Ares | 2015-08-19 10:40 | 2015-09-09 10:43 | 2015-08-19 10:40 | 2016-02-17 10:53 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:46 | S217012770017 | CLARENDON WALK 1-24 | 212632 | Active | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the ground floor level electrical room/cupboard is out of service/test date according to the contractors servicing label attached to it. The last test date on this RGE service label was November 2011. | This carbon dioxide fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. Alternatively it could be removed from this area of the building and not serviced etc or replaced, the external contractor's maintenance schedule should be amended to show this change. | A & R Contract Management | Alex Bosman
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:34 | S217010570003 | LOWERWOOD COURT | 133667 | Completed | 1b | Medium | Communal Lighting | The covers of some of the lighting units located on the external walkways/balconies of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-03-07 14:34 | 2014-05-06 14:47 | 2014-03-07 14:34 | 2015-04-14 10:14 | -60 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:58 | S217010570003 | LOWERWOOD COURT | 133680 | Completed | 15a | High | Emergency Lighting | The covers of the emergency lighting units currently installed in the building are dirty, thus affecting the level of illuminating from the bulb and you cannot see the charger indicator light clearly. | I would recommend that the covers of the emergency lighting units currently installed in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels and help the caretakers to undertake the monthly checking of the emergency lighting system. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-03-07 14:58 | 2014-03-28 14:58 | 2014-03-07 14:58 | 2015-04-14 10:17 | -21 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:59 | S217010570003 | LOWERWOOD COURT | 133682 | Completed | 15b | High | Emergency Lighting | There are no emergency lighting units in the basement level boiler room. | I would recommend that when the new boilers are fitted that emergency lighting units are also fitted in this basement boiler room area. | A & R Contract Management | Alex Bosman |  | It has been confirmed that appropriate lighting will be installed when the new boilers are fitted. | 2015-10-28 | Fully Completed | Gillian Kennedy | 2014-03-07 14:59 | 2014-03-28 15:00 | 2014-03-07 14:59 | 2015-10-29 15:19 | -21 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 15:00 | S217010570003 | LOWERWOOD COURT | 133683 | Completed | 18a | High | Fire Extinguisher | Very Dangerous The horn on the carbon dioxide fire extinguisher in residents meeting room ground floor level was not screwed up tightly. If a person were to use this fire extinguisher then they could suffer serious cold burns. | I would recommend that RGE are asked to explain why this extinguisher has not been serviced correctly. RGE should service this fire extinguisher again correctly. Removed from Clubroom to ESA's office to ensure not used by residents. | A & R Contract Management | Alex Bosman |  | Made safe by ESA | 2014-05-26 | Fully Completed | Janice Wray | 2014-03-07 15:00 | 2014-03-28 15:03 | 2014-03-07 15:00 | 2015-11-26 17:10 | -21 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 15:03 | S217010570003 | LOWERWOOD COURT | 133686 | Completed | 18b | Information Only | Fire Extinguisher | There was a spare out of date water fire extinguisher in residents meeting room at the 1st floor level. | This was removed from the meeting room as it is not required and placed in the cleaners area for collection by RGE. | A & R Contract Management | Alex Bosman |  | This was removed from the meeting room as it is not required and placed in the cleaners area for collection by RGE. | 2014-05-26 | Fully Completed |  |  |  | 2014-03-07 15:03 | 2015-11-26 17:14
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:12 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205669 | Completed | 15 | Low | Emergency Lighting | There appears to be no emergency lighting units installed in the internal ground floor level corridors. | I would recommend that consideration is given to the fitting of some emergency lighting units in the internal ground floor level corridors as these area do not have any windows in them. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed | Maria Ares | 2015-07-09 09:12 | 2016-01-05 09:13 | 2015-07-09 09:12 | 2015-11-23 16:20 | -180 | In target | 2015-07-09 09:12 | 2015-11-29 16:20 | Janice Wray
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:16 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205673 | Completed | 23a | High | Fire Extinguisher | The fire extinguisher located in this building are out of test date according to the contractors servicing label attached to each one, the last test date according to these servicing labels was August 2013. | The portable fire extinguishers in this buildings should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing compelet 23.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-07-09 09:16 | 2015-07-30 09:48 | 2015-07-09 09:16 | 2015-11-27 11:22 | -21 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:48 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205688 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the landings of the staircases of this building and in the entrance hall/lobby areas. | Can it please be confirmed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Keystone does refer to some EL but last date in 1994 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-07-09 09:48 | 2015-07-30 09:58 | 2015-07-09 09:48 | 2015-12-15 11:34 | -21 | In target
MANNING HOUSE - 2015.06.03 | 2015-06-12 08:29 | S217008490001 | MANNING HOUSE | 201210 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building, by the double doors of the external balconies and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE REFERS TO EL ON "1st FLOOR BALCONY" BUT NO CERTIFICATE | A & R Contract Management | Adrian Bowman | 2016-01-21 | AP confirmed service complete 19.11.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2015-06-12 08:29 | 2015-07-03 08:31 | 2015-06-12 08:29 | 2016-01-22 13:41 | -21 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 15:04 | S217008560002 | MARKLAND HOUSE | 244924 | Active | 1a | High | Electrical Wire Check | 1According to the contractors label on an electrical, supply board in the lift motor room the last electrical test was in July 2009 and this electrical board should have be retested in July 2014. | Can it please be confirmed that this electrical supply board in the lift motor room has been retested since 2014, the contractors label on the main electrical intake board states that this buildings fixed electrical wiring was retested in April 2015. If this supply board in the lift motor room is out of test date if should be tested immediately with any defects found rectified. | A & R Contract Management | Alex Bosman | 2016-03-21
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 15:06 | S217008560002 | MARKLAND HOUSE | 244926 | Active | 1b | High | Miscellaneous | In the ground floor office area which is used by the caretaker and also a contractor, Cofley, it appears that Portable electrical Appliance Testing (PAT) is not being undertaken on all the portable electrical items. Some had in date PAT labels on them others did not, these are items in the same rooms. | All TMO owned portable electrical items should be PAT, if items of portable electrical equipment owned by Cofley are not PAT then they should be asked to undertake PAT as well. | A & R Contract Management | Alex Bosman | 2016-03-21
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 15:10 | S217008560002 | MARKLAND HOUSE | 244928 | Active | 5 | High | Miscellaneous | It is not known when the water pumps were last serviced by the contractor Cofley because the service book has not been filled in, the pages are blank. | Can it please be confirmed when the last service was undertaken on the water pump? I would recommend that the contractor is asked to make certain that the service book is filled in after every service. Alex | A & R Contract Management | Alex Bosman | 2016-03-21
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 08:49 | S217008560002 | MARKLAND HOUSE | 245020 | Active | 18 | High | Fire Alarm | The fire alarm and warning system in these offices appears not to be working, because this fire alarm system is not powered up, the power light in the panel was not lit. So this fire alarm system is not in use, but there are persons working in these offices. | This fire alarm system should be brought back into full working order immediately, if this can be achieved in a couple of days then the persons who are working in these offices can remain here. If repairing this system will take longer then the offices should be vacated until the installed fire alarm system is fully functioning again. | A & R Contract Management | Alex Bosman | 2016-03-22
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 08:56 | S217008560002 | MARKLAND HOUSE | 245022 | Active | 23a | High | Fire Alarm | There is a fire alarm system installed in the office area on the ground floor level of this building, this fire alarm system is not being serviced or maintenance and no weekly occupiers tests are being undertaken. This is because this fire alarm system is not powered up or turned on. Keystone checked, last serviced 12th March 2013 | Please also see item 18, the fire alarm system installed in the office area on the ground floor level of this building should be serviced immediately with and defects found rectified. Occupiers weekly tests of this system should be undertaken and recorded as proof of testing. | A & R Contract Management | Alex Bosman | 2016-03-22
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 08:58 | S217008560002 | MARKLAND HOUSE | 245024 | Active | 23b | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of this building plus the lift motor room and other plant room areas. Keystone checked | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-22
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 09:02 | S217008560002 | MARKLAND HOUSE | 245028 | Active | 23d | High | Emergency Lighting | Keystone states that the lightning protection system installed on this building was lasted serviced in October 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-22
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 09:22 | S217008560002 | MARKLAND HOUSE | 245036 | Active | 23e | High | Fire Extinguisher | Some fire extinguishers located within this building have not been serviced since 2013, according to the contractors labels, these are mostly in the office area. | All of the fire extinguishers in this building should be serviced immediately if they are out of service date. | A & R Contract Management | Alex Bosman | 2016-03-22
MARLEY HOUSE - 2014.4.22 | 2014-05-14 09:54 | S217010050008 | MARLEY HOUSE | 143625 | Completed | 1a | High | Electrical Wire Check | It is not known if the fixed electrical wiring in the cleaners/caretakers area of this building is being tested. The next periodic fixed wiring test for the common parts of this building is due in August of this year, 2014. | I would recommend that when the next fixed electrical wiring test of the common parts areas of this building is undertaken in August of this year that it confirmed that the cleaners/ caretakers area of this building is also being tested. If it is not then the fixed electrical wiring in this area of the building should be included in this test. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2014-05-14 09:54 | 2014-06-04 09:56 | 2014-05-14 09:54 | 2014-07-15 15:55 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:39 | S217010050008 | MARLEY HOUSE | 143654 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed to cover the common parts of this building at the time of the last refurbishment does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained. | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | serviced by chubb 14.5.2015 confirmed ok | 2015-08-11 | Fully Completed | Gillian Kennedy | 2014-05-14 10:39 | 2014-06-04 10:40 | 2014-05-14 10:39 | 2015-08-12 12:25 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:40 | S217010050008 | MARLEY HOUSE | 143655 | Completed | 23b | High | Fire Alarm | The is a fire alarm system currently installed in the cleaners/caretakers area of this building this fire alarm system does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed fire alarm system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed fire alarm system in the cleaners area of this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-05-14 10:40 | 2014-06-04 10:41 | 2014-05-14 10:40 | 2015-12-15 11:35 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:44 | S217010050008 | MARLEY HOUSE | 143658 | Completed | 23e | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of test date according to the RGE servicing label attached to it. The last test date being the 8th October 2012. . | I would recommend that the carbon dioxide fire extinguisher located in the roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Michael Lyons | 2016-01-21 | AP confirmed service complete 3.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-05-14 10:44 | 2014-06-04 10:46 | 2014-05-14 10:44 | 2016-01-22 13:43 | -21 | In target
MILMAN HOUSE, MILMAN STREET, LONDON SW10 0BU - 2016.01.28 | 2016-02-19 10:38 | S217012760005 | MILMANS HOUSE | 244474 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building also on the secondary staircase and in the lift motor rooms etc. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-21
MILMAN HOUSE, MILMAN STREET, LONDON SW10 0BU - 2016.01.28 | 2016-02-19 10:41 | S217012760005 | MILMANS HOUSE | 244475 | Active | 23b | High | Fire Extinguisher | The fire extinguishers located within this building were last serviced in February 2014, according to the contractors labels attached to each extinguisher. | All of the fire extinguishers in this building should be serviced immediately as there are all out of service date. | A & R Contract Management | Alex Bosman | 2016-03-21
MILMAN HOUSE, MILMAN STREET, LONDON SW10 0BU - 2016.01.28 | 2016-02-19 10:43 | S217012760005 | MILMANS HOUSE | 244476 | Active | 23 | High | Lightning Protection | Keystone states that the lightning protection system installed on this building was lasted serviced on the 7th September 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-21
MORLAND HOUSE- 2015.06.22 | 2015-06-29 12:02 | S217009210003 | MORLAND HOUSE | 203800 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in the two electrical cupboards/areas of these building are out of test date according to the servicing labels attached to them. The last test date on these service labels being the 25th July 2012. | These fire extinguishers should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule for annual servicing. Alternatively they could be removed from the building and not serviced, they could be taken to the Lancaster West office as spares as these extinguishers have 4 plus years of service life left. | A & R Contract Management | Alex Bosman | 2016-01-13 | AP confirmed service complete 4.12.2015 | 2016-01-13 | Fully Completed | Maria Ares | 2015-06-29 12:02 | 2015-07-20 12:04 | 2015-06-29 12:02 | 2016-01-14 16:04 | -21 | In target
MORLAND HOUSE- 2015.06.22 | 2015-06-29 12:04 | S217009210003 | MORLAND HOUSE | 203803 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE - NO CERTIFICATES & LAST INSPECTION DATE JULY 2013 | A & R Contract Management | Alex Bosman |  | AP confirmed service complet 1.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-06-29 12:04 | 2015-07-20 12:05 | 2015-06-29 12:04 | 2015-12-15 11:36 | -21 | In target
NICKLEBY HOUSE - 2014.7.22 | 2014-08-04 13:05 | S217010050001 | NICKLEBY HOUSE | 155839 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building, these do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are the installed emergency lighting units/system being serviced, tested and maintained. | Can it please be confirmed that the emergency lighting units/system installed within this building are being serviced, tested and maintained by an electrical contractor. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-08-04 13:05 | 2014-08-25 13:06 | 2014-08-04 13:05 | 2015-12-15 11:45 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 15:44 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151232 | Completed | 1b | Information Only | Electrical Wire Check | The last electrical test on the fixed wiring in this building was undertaken on the 10th April of this year with the next test being due next April, 2015 according to the contractor's label. Normally the fixed electrical wiring test lasts for 5 years not 1, so I believe that the next electrical wiring test should be in April 2019 | I would recommend that the electrical test sheets are looked at reference the electrical wiring test for this building to see if the wrong date has been inserted on the contractor's label. | A & R Contract Management | Alex Bosman |  | RMA tests complete 28.11.2015 | 2015-12-14 | Fully Completed |  |  |  | 2014-07-01 15:44 | 2015-12-15 11:46
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 15:53 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151238 | Completed | 23a | High | Fire Alarm | Is the installed fire alarm system in this premises being serviced and tested by a fire alarm contractor in accordance with BS5839 Part 1 2013? | If it is not I would recommend that the instated fire alarm system in this premises is serviced and tested immediately with any defects rectified and the system placed on a planned preventive maintenance programme. If the installed fire alarm system is being serviced etc then no action is needed but a fire logbook should be available on the premises. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-07-01 15:53 | 2014-07-22 15:54 | 2014-07-01 15:53 | 2015-12-15 11:47 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:16 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151247 | Completed | 23c | High | Emergency Lighting | Is the emergency lighting system currently installed in this premises being annually serviced, tested and maintained by the electrical contractors. | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this premises is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-07-01 16:16 | 2014-07-22 16:17 | 2014-07-01 16:16 | 2015-12-15 11:48 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:20 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151250 | Completed | 23e | High | Fire Extinguisher | According to the contractors label on the carbon dioxide fire extinguisher in the entrance corridor the last servicing date was March 2009. All of the other fire extinguishers were in service date. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 24.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-07-01 16:20 | 2014-07-22 16:21 | 2014-07-01 16:20 | 2015-12-02 14:12 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:23 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151252 | Completed | 23g | High | Inspection Regime | There did not appear to be a logbook in this building were the fire tests and inspections could be recorded in. | I would recommend that a fire logbook is provided in this building so that any tests and inspections can be recorded. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-07-01 16:23 | 2014-07-22 16:24 | 2014-07-01 16:23 | 2015-12-15 11:48 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:35 | S217010030001 | OCTAVIA HOUSE | 205855 | Completed | 7 & 23c | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. Is the installed lightning protection system being serviced, tested and maintained. Parts of the lightning protection system installed on this building were damaged and not secured to the buildings structure the area concerned is mostly above flats 66 and 67 on the open external roof. | Confirmation required that this system is being inspected, serviced & maintained. Additionally, that the damaged lightning protection systems installed on this building should be repaired or replaced and a full service/test of the full lightning protection system undertaken by a competent contractor. Any other defects found during this test/service should also be rectified and a new test certificate obtained for the whole system. THIS ADDRESS IS NOT ON CURRENT SCHEDULE - Alex advised by e-mail. | A & R Contract Management | Alex Bosman | 2016-01-13 | RMA tests completed Dec 15 | 2016-01-13 | Fully Completed | Maria Ares | 2015-07-09 14:35 | 2015-07-30 14:36 | 2015-07-09 14:35 | 2016-01-14 16:04 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:59 | S217010030001 | OCTAVIA HOUSE | 205877 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system currently installed on the means of escape routes of this building, | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - 07/13 - NO CERTIFICATES | A & R Contract Management | Alex Bosman |  | AP servicing complete 8.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-07-09 14:59 | 2015-07-30 15:00 | 2015-07-09 14:59 | 2015-11-27 11:23 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:31 | S217010030001 | OCTAVIA HOUSE | 102910 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Battery powered devices were fitted in the four flats visited. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. I would recommend that the caretaker is instructed to put a copy of the LFB leaflet through each flats letter box. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | A & R Contract Management | Alex Bosman |  | Hard wired detectors fitted to all properties during PIR testing | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-20 15:31 | 2014-02-16 15:32 | 2013-08-20 15:31 | 2013-12-10 17:36 | -180 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:33 | S217010030001 | OCTAVIA HOUSE | 102912 | Completed | 23a | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. Is the installed lightning protection system being serviced, tested and maintained. | I would recommend that the TMO engineer is asked if the installed lightning protection system is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Block added to 13/14 testing program | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-20 15:33 | 2013-09-10 15:34 | 2013-08-20 15:33 | 2013-12-10 17:37 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:36 | S217010030001 | OCTAVIA HOUSE | 102913 | Completed | 23b | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Added to asset register for inclusion in servicing contract | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-20 15:36 | 2013-09-10 15:37 | 2013-08-20 15:36 | 2014-03-21 16:49 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:38 | S217010030001 | OCTAVIA HOUSE | 102915 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system and other items in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken along with all the other items on the caretakers checklist. | A & R Contract Management | Alex Bosman |  | ESA training complete - ongoing refresher to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-08-20 15:38 | 2013-09-10 15:39 | 2013-08-20 15:38 | 2014-07-15 16:40 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 15:40 | S217010030001 | OCTAVIA HOUSE | 102917 | Completed | 23d | Medium | Fire Extinguisher | According to the asset list supplied by the TMO engineers there is portable fire fighting equipment provided in this building. None could be found during this risk assessment. | I would recommend that the TMO engineer is asked to check the asset list as no portable fire fighting equipment was located during this risk assessment. There is I believe no requirement for portable fire fighting equipment to be provided in this building so the asset list could be amended to show no items provided and any contractor's maintenance lists also amended. If the use of the basement areas changes then some portable fire fighting equipment may be required. | A & R Contract Management | Alex Bosman |  | Asset register updated | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-20 15:40 | 2013-10-19 15:41 | 2013-08-20 15:40 | 2014-03-21 16:54 | -60 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:36 | S217010030001 | OCTAVIA HOUSE | 102871 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply boards and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of this building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | Included in 13/14 block electrical testing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-20 14:36 | 2013-09-10 14:38 | 2013-08-20 14:36 | 2014-01-03 10:18 | -21 | In target | 2013-08-20 14:36 | 2014-01-09 10:17 | Janice Wray
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:45 | S217010030001 | OCTAVIA HOUSE | 102878 | Completed | 7 | High | Lightning Protection | Parts of the lightning protection system installed on this building were damaged and not secured to the buildings structure the area concerned is mostly above flat 68 on the open external roof. There are contractors working in this area repairing the brickwork of the roof parapet wall. | I would recommend that the TMO engineer checks who damaged the lightning protection system installed on this building. Can it be confirmed who will repair the lightning protection system and re-secure it back to the buildings structure? | A & R Contract Management | Alex Bosman |  | Block included in 13/14 lighting protection testing program | 2014-03-20 | Fully Completed | Alex Bosman | 2013-08-20 14:45 | 2013-09-10 14:47 | 2013-08-20 14:45 | 2014-03-21 16:48 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:50 | S217010050005 | PICKWICK HOUSE | 158111 | Completed | 1 | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of this building were last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | 30/08/2013 - Completed - Certificate held in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-08-19 15:50 | 2014-09-09 15:51 | 2014-08-19 15:50 | 2015-08-25 16:37 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:59 | S217010050005 | PICKWICK HOUSE | 158122 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. Copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders have been left in this building. | The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/ sounders fitted by the LFB if required. These domestic detectors/sounders would be located in accordance with the requirements of BS 5839 Part 6 2013. | A & R Contract Management | Alex Bosman |  | Hard Wired detectors to be installed during 5 year PIR program | 2015-03-23 | Fully Completed |  |  |  | 2014-08-19 15:59 | 2015-03-24 17:07
POND HOUSE, FLATS 1 TO 32 - 2015.07.16 | 2015-09-01 14:26 | S217004267702 | POND HOUSE (1-32) | 214354 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed in each of the staircase enclosures of this building, on the staircase landings and in the entrance hall areas. | Can it please be confirmed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If these last tests/services were more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE -SERVICING JAN 13 - no docs | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-01 14:26 | 2015-09-22 14:27 | 2015-09-01 14:26 | 2015-12-02 14:13 | -21 | In target
POND HOUSE, FLATS 1 TO 32 - 2015.07.16 | 2015-09-01 14:33 | S217004267702 | POND HOUSE (1-32) | 214362 | Completed | 23c | High | Fire Extinguisher | According to the Chubb contractors label fixed to the carbon dioxide fire extinguisher in the electrical room/cupboard by flat 4 of this building the last service/test date was July 2014. The carbon dioxide fire extinguisher in the electrical room/cupboard by flat 17 of this building has a RGE contractors service label on it with a last service/test date of January 2014, this extinguisher is out of service date. | I would recommend that both of these fire extinguishers are serviced. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-01 14:33 | 2015-09-22 14:38 | 2015-09-01 14:33 | 2015-12-15 11:49 | -21 | In target
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 08:57 | S217004267703 | POND HOUSE (33-47) | 214212 | Active | 14 | Medium | Miscellaneous | There is a smoke ventilation system fitted in this building. | Can it be confirmed that the ductwork for the smoke ventilation system installed in this building is cleaned and any filters or dampeners fitted within the duct work are checked or changed during the service undertaken on this system? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 09:01 | S217004267703 | POND HOUSE (33-47) | 214213 | Active | 21a | High | Miscellaneous | There is a mechanical ventilation system installed to cover the protected staircase and the refuse chute rooms of this building. | Have the caretakers and housing officers being given specific instructions on how to use this installed smoke vent system and how it works? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 09:02 | S217004267703 | POND HOUSE (33-47) | 214214 | Active | 21b | High | Miscellaneous | There is a mechanical ventilation system installed to cover the protected staircase and the refuse chute rooms of this building. | Is there a policy and procedure for using the smoke ventilation system installed to cover the protected staircase and the refuse chute rooms of this building. Do the caretakers and housing officers know this policy and the procedures? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 09:05 | S217004267703 | POND HOUSE (33-47) | 214215 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall area of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-01 09:05 | 2015-09-22 09:06 | 2015-09-01 09:05 | 2015-12-02 14:14 | -21 | In target
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 09:08 | S217004267703 | POND HOUSE (33-47) | 214217 | Active | 23c | High | Miscellaneous | There is a smoke ventilation system installed to cover the protected staircase and the refuse chute rooms of this building. The last service according to the service book for the smoke ventilation system installed in this building was on the 4th February 2014, it was serviced at 6 monthly intervals before this date. | Please can it be confirmed that the smoke ventilation system installed to cover the protected staircase and the refuse chute rooms of this building is being serviced, tested and maintained according to the manufactures instructions. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 33 TO 47 -2015.07.16 | 2015-09-01 09:13 | S217004267703 | POND HOUSE (33-47) | 214220 | Completed | 23f | Information Only | Fire Extinguisher | The fire extinguisher in the ground floor electrical cupboard/room was last serviced in July 2014. | This fire extinguisher is still in service date but is due to be serviced again by the end of July 2015 | A & R Contract Management | Alex Bosman |  | AP confirmed complete 27.11.2015 | 2015-12-14 | Fully Completed |  |  |  | 2015-09-01 09:13 | 2015-12-15 11:55
POND HOUSE, FLATS 48 TO 93 - 2015.07.16 | 2015-09-01 11:32 | S217004267704 | POND HOUSE (48-63) | 214277 | Active | 14 | Medium | Miscellaneous | There is a smoke ventilation system fitted to cover the two protected staircases and the refuse chute rooms of this building. | Can it be confirmed that the ductwork for these smoke ventilation systems installed to cover the protected staircases of this building are cleaned and any filters or dampeners fitted within the duct work are checked or changed during the service undertaken on these systems? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 48 TO 93 - 2015.07.16 | 2015-09-01 11:34 | S217004267704 | POND HOUSE (48-63) | 214278 | Active | 21a & 21b | High | Miscellaneous | There is a smoke ventilation system installed to cover the two protected staircases and the refuse chute rooms of this building. | Have the caretakers and housing officers being given specific instructions on how to use these installed smoke ventilation systems and how they work? Is there a policy and procedure for using the smoke ventilation systems installed to cover the protected staircases and the refuse chute rooms off of them? Do the caretakers and housing officers know this policy and the procedures? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 48 TO 93 - 2015.07.16 | 2015-09-01 11:41 | S217004267704 | POND HOUSE (48-63) | 214280 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed in each part of this building, on the staircase landings, in the entrance hall areas and on the external balconies. | Can it please be conformed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complerte 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-01 11:41 | 2015-09-22 11:43 | 2015-09-01 11:41 | 2015-12-02 14:15 | -21 | In target
POND HOUSE, FLATS 48 TO 93 - 2015.07.16 | 2015-09-01 11:45 | S217004267704 | POND HOUSE (48-63) | 214283 | Active | 23c | High | Miscellaneous | There is a smoke ventilation system installed to cover the two protected staircases and the refuse chute rooms off of them. The last service according to the service book for these smoke ventilation systems installed in this building was on the 4th February 2014, it was serviced at 6 monthly intervals before this date. | Please can it be confirmed that the smoke ventilation systems installed to cover the protected staircases and the refuse chute rooms off of them are being serviced, tested and maintained according to the manufactures instructions. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  |  |  |  | Cyril Morris | 2015-09-01 11:45 | 2015-09-22 11:47 |  |  | 197 | 197 days overdue
POND HOUSE, FLATS 48 TO 93 - 2015.07.16 | 2015-09-01 11:52 | S217004267704 | POND HOUSE (48-63) | 214293 | Completed | 23e | High | Fire Extinguisher | The carbon dioxide fire extinguishers located in each of the ground floor level electrical cupboards/rooms are out of service date. The last service according to the RGE contractors labels fixed to them has a last service date of February 2013. | These fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-01 11:52 | 2015-09-22 11:53 | 2015-09-01 11:52 | 2015-12-15 11:57 | -21 | In target
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 10:42 | S217004267707 | POND HOUSE (94-109) | 214460 | Active | 13 | Medium | Miscellaneous | There is a smoke ventilation system fitted to cover the protected staircase and the refuse chute rooms off of it. | Can it be confirmed that the ductwork for this smoke ventilation system installed to cover the protected staircase of this building is being cleaned and any filters or dampeners fitted within the duct work are checked or changed during the service undertaken on this system? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 10:51 | S217004267707 | POND HOUSE (94-109) | 214463 | Active | 21a & 21b | High | Miscellaneous | There is a smoke ventilation system installed to cover the protected staircase and the refuse chute rooms off of it. | Have the caretakers and housing officers being given specific instructions on how to use this installed smoke ventilation system and how it works? Is there a policy and procedure for using the smoke ventilation system installed to cover the protected staircase and the refuse chute rooms? Do the caretakers and housing officers know this policy and the procedures? | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 10:53 | S217004267707 | POND HOUSE (94-109) | 214464 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed in each part of this building, on the staircase landings, in the entrance hall areas and on the external balconies. | Can it please be conformed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-02 10:53 | 2015-09-23 10:54 | 2015-09-02 10:53 | 2015-12-15 11:59 | -21 | In target
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 10:56 | S217004267707 | POND HOUSE (94-109) | 214466 | Active | 23c | High | Miscellaneous | 23c High There is a smoke ventilation system installed to cover the protected staircase and the refuse chute rooms off of it. The last service according to the service book for these smoke ventilation systems installed in this building was on the 4th February 2014, it was serviced at 6 monthly intervals before this date. | Please can it be confirmed that the smoke ventilation systems installed to cover the protected staircase and the refuse chute rooms off of it is being serviced, tested and maintained according to the manufactures instructions. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 11:00 | S217004267707 | POND HOUSE (94-109) | 214470 | Completed | 23e | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the ground floor level electrical cupboard/room by flat 94 is out of service date according to the RGE contractors label on it. The last service was in January 2014. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-02 11:00 | 2015-09-23 11:05 | 2015-09-02 11:00 | 2015-12-15 12:01 | -21 | In target
POND HOUSE, FLATS 94 TO 124 - 2015.07.16 | 2015-09-02 11:07 | S217004267707 | POND HOUSE (94-109) | 214476 | Completed | 23g | Information Only | Fire Extinguisher | The carbon dioxide fire extinguisher located in the ground floor level electrical cupboard/room by flat 110 was last serviced in July 2014 by Chubb Fire. | This fire extinguisher is still in service date but is due to be serviced again but the end of this month. | A & R Contract Management | Alex Bosman |  | COMPLETE DUPLICATE ACTION | 2015-11-17 | Fully Completed |  |  |  | 2015-09-02 11:07 | 2015-11-18 15:06
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 11:24 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181296 | Completed | 1 | High | Electrical Wire Check | 1There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2016-01-21 | RMA confirmed all works complete | 2016-01-21 | Fully Completed | Maria Ares | 2015-02-02 11:24 | 2015-02-23 11:32 | 2015-02-02 11:24 | 2016-01-22 13:09 | -21 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 11:32 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181298 | Completed | 4 | High | Boiler | There does not appear to be a gas contractors label or print out attached to the gas boiler in this building indication when the last boiler service was undertaken? | Can it please be confirmed when the last service of this gas boiler was undertaken, if this was more than a year ago then a service/ maintenance check should be undertaken immediately by a "Gas Safe " registered contractor. With any defects found rectified and this boiler and the fixed heating system then placed on a planned preventative maintenance schedule. | A & R Contract Management | Alex Bosman |  | 21/07/2015 - Completed by K&T | 2015-08-24 | Fully Completed | Gillian Kennedy | 2015-02-02 11:32 | 2015-02-23 11:33 | 2015-02-02 11:32 | 2015-08-25 16:38 | -21 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 11:34 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181299 | Completed | 6 | High | Miscellaneous | There are mechanical extractors located in the kitchen and in the main hall areas of this building with the controls on the walls next to the extractors. | Can it please be confirmed if these extractors are being serviced and checked in line with any manufacturers instructions. If they are then no further action is needed, if they are not then I would recommend that servicing etc in accordance with the manufactures instructions is undertaken with any defects identified rectified. The extractors should then placed on a planned preventative maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-21 | RMA confirmed all works complete | 2016-01-21 | Fully Completed | Maria Ares | 2015-02-02 11:34 | 2015-02-23 11:42 | 2015-02-02 11:34 | 2016-01-22 13:10 | -21 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 11:48 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181304 | Completed | 23a | High | Emergency Lighting | Is the emergency lighting system currently installed in this premises being annually serviced, tested and maintained by the electrical contractors. | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this premises is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-02 11:48 | 2015-02-23 12:14 | 2015-02-02 11:48 | 2015-12-02 14:16 | -21 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 12:16 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181314 | Completed | 23c | High | Fire Extinguisher | The fire extinguishers located in this building are all out of service date according to the information on the contractor's labels on each extinguisher. The last service date was February 2011. | All the fire extinguishers in this building should be serviced immediately and it confirmed that they are on a contractor's maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed service complete 8.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2015-02-02 12:16 | 2015-02-23 12:17 | 2015-02-02 12:16 | 2016-01-22 13:11 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:47 | S217010420002 | RAYMEDE TOWER | 148299 | Completed | 1 | Medium | Communal Lighting | The covers of some of the lighting units located in the staircase enclosure of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. . | I would recommend that the covers of the lighting units located at the roof level of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-06-11 17:47 | 2014-08-10 17:48 | 2014-06-11 17:47 | 2015-04-14 10:18 | -60 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:52 | S217010420002 | RAYMEDE TOWER | 148302 | Completed | 7 | High | Lightning Protection | Parts of the lightning protection system installed on this building were missing and other parts are damaged and not secured to the buildings structure. This includes area at the roof level as well. | I would recommend that a contractor is asked to repair this damaged lightning protection system as soon as possible. | A & R Contract Management | Alex Bosman |  | TESTED AND CERTS SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2014-06-11 17:52 | 2014-07-02 17:52 | 2014-06-11 17:52 | 2015-11-18 15:07 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:58 | S217010420002 | RAYMEDE TOWER | 148307 | Active | 15a | High | Emergency Lighting | There are lighting units located on the landings of the staircase but there are no neon charging/indicator lights visible on these light units. On the external balconies there are light units with the neon charging/indicator lights clearly visible so it can be seen that these are also emergency lighting units. | Can it be confirmed that the lighting units in the staircase enclosure are also emergency lighting units as no neon indicator/charging lights could be seen on these units. This building is over two storeys in height and new lighting was installed during the refurbishment in 2011 so I would expect to find emergency lighting in the staircase enclosure of a tower block. If it is found that no emergency lighting units are fitted within this staircase enclosure then some must be fitted to the requirements of BS 5266 Part 1 2011 including the risk assessment section. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2014-06-11 17:58 | 2014-07-02 17:59 |  |  | 644 | 644 days overdue
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:00 | S217010420002 | RAYMEDE TOWER | 148308 | Active | 15b | High | Emergency Lighting | There are lighting units located on the landings of the staircase but there are no neon charging/indicator lights visible on these light units. On the external balconies there are light units with the neon charging/indicator lights clearly visible so it can be seen that these are also emergency lighting units. | If it is found that the lighting units in the staircase enclosure are also emergency lighting units why are the neon indicator/charging lights not visible on these units. The occupiers monthly tests and inspections cannot be undertaken if the charge light cannot be seen. Also the emergency lighting requirement should then be compared to the requirements of BS 5266 Part 1 2011 and the risk assessment section and then any deficiencies or lack of coverage then rectified If it is found that the present lights on the staircase landings are not also emergency lights, see item 15 a above the new light units will be fitted. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2014-06-11 18:00 | 2014-07-02 18:01 |  |  | 644 | 644 days overdue
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:04 | S217010420002 | RAYMEDE TOWER | 148311 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed to cover the common parts of this building at the time of the last refurbishment does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 29.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-06-11 18:04 | 2014-07-02 18:05 | 2014-06-11 18:04 | 2015-11-27 11:25 | -21 | In target
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 14:48 |  |  | 244651 | Active
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 15:46 | S217012760003 | RILEY HOUSE | 244672 | Active | 23a | High | Emergency Lighting | There are emergency lighting units installed on the means of escape routes of this building also on the secondary staircase and in the lift motor rooms etc. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-03-21
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 15:47 | S217012760003 | RILEY HOUSE | 244673 | Active | 23b | High | Lightning Protection | Keystone states that the lightning protection system installed on this building was lasted serviced on the 12th August 2015. It is not known if this system passed the service, previously remedial work was needed on this lighting protection system. | Please can it be confirmed that the lighting protection system passed the service? If it did not any remedial work should be undertaken. | A & R Contract Management | Alex Bosman | 2016-03-21
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 15:49 | S217012760003 | RILEY HOUSE | 244675 | Active | 23c | High | Fire Extinguisher | The fire extinguishers located within this building were last serviced in November 2013, according to the RGE contractors labels attached to each extinguisher. | All of the fire extinguishers in this building should be serviced immediately as there are all out of service date. | A & R Contract Management | Alex Bosman | 2016-03-21
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:36 | S217007860006 | SOUTHAM HOUSE | 201214 | Completed | 1 | High | Wiring Inspection | There is no information available to say when the last 5 year electrical fixed wiring test of the landlords/common parts electrical wiring was undertaken for both parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of both parts of this building were last tested. If these tests were more than 5 years ago then they should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | complete as per 2015 communal testing program | 2015-08-11 | Fully Completed | Gillian Kennedy | 2015-06-12 08:36 | 2015-07-03 08:38 | 2015-06-12 08:36 | 2015-08-12 12:26 | -21 | In target
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:41 | S217007860006 | SOUTHAM HOUSE | 201218 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building, on the balconies, on the staircase landings and in the entrance hall/lobby areas. | Can it please be confirmed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting systems should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON ASSET REGISTER- BUT NO CERTIFICATE | A & R Contract Management | Alex Bosman |  | AP confirmed serviced 17.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-06-12 08:41 | 2015-07-03 08:42 | 2015-06-12 08:41 | 2015-11-27 11:26 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:14 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215806 | Completed | 13 | High | Miscellaneous | There appears to be a disabled alarm call system installed in 4 parts of this building. There is an alarm indicator panel by the front entrance door of the building and an indicator light/beacon outside each flat entrance door. This is I believe an emergency pull cord system with the pull cords located within the bathroom areas of each flat. | Can it be confirmed if this alarm call system is functioning and in use. If it is not then I would recommend that the indicator panels are covered over and the system removed from each flat. If the system is being used then is it being serviced and maintained in accordance with the manufactures instructions? | A & R Contract Management | Alex Bosman | 2016-02-16 | AP confirmed inspected 3.12.15. system is a diabled cal system which is disabled. Order raised to RMA to remove remaining equipment | 2016-02-16 | Fully Completed | Maria Ares | 2015-09-09 17:14 | 2015-09-30 17:15 | 2015-09-09 17:14 | 2016-02-17 10:54 | -21 | In target
ST MARKS GROVE FLATS 1-12 - 2015.06.15 | 2015-06-29 10:47 | S217010180013 | ST MARKS GROVE 1-12 | 203756 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE - NO CERTIFICATE & Last test date JULY 2013 Alex | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-29 10:47 | 2015-07-20 10:49 | 2015-06-29 10:47 | 2015-12-02 14:17 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:11 | S217010180014 | ST MARKS GROVE 13-48 | 203734 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby areas. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE BUT NO CERTIFICATE _ REFERENCE TO LAST TEST Jan 2013 | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 25.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-06-29 10:11 | 2015-07-20 10:13 | 2015-06-29 10:11 | 2015-12-02 14:18 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:06 | S217008220100 | STABLE WAY SITE | 105894 | Completed | 1 | High | Electrical Wire Check | There are different test dates on the labels of the portable electrical appliances in this building, some were last tested in May 2010 and others last tested in April 2012. | I would recommend that all the portable electrical appliances in this building are tested and an asset register maintained of all items tested and when. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-12 14:06 | 2013-10-03 14:08 | 2013-09-12 14:06 | 2015-02-27 14:51 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:11 | S217008220100 | STABLE WAY SITE | 105898 | Completed | 6 | High | Electrical Wire Check | It is not known if the washing machine in the kitchen area is being serviced or electrically tested. | Can it please be confirmed that the electrical items in the kitchen are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-09-12 14:11 | 2013-10-03 14:14 | 2013-09-12 14:11 | 2015-02-27 14:51 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:20 | S217008220100 | STABLE WAY SITE | 105903 | Completed | 18 | High | Fire Extinguisher | There is no fire blanket located in the kitchen of this building. | I would recommend that a fire blanket is provided in the kitchen of this building. | A & R Contract Management | Alex Bosman |  | completed 31.07.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-09-12 14:20 | 2013-10-03 14:22 | 2013-09-12 14:20 | 2015-11-20 12:33 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:21 | S217008220100 | STABLE WAY SITE | 105906 | Completed | 23a | High | Fire Alarm | There are no records of the fire alarm system currently installed in this building having been serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 28.10.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-09-12 14:21 | 2013-10-03 14:23 | 2013-09-12 14:21 | 2015-11-20 12:35 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:25 | S217008220100 | STABLE WAY SITE | 105909 | Completed | 23c | High | Emergency Lighting | There are no records of the emergency lighting units currently installed in this building having been serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting unitsin this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the units placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | completed 28.10.15 | 2015-11-19 | Fully Completed | Maria Ares | 2013-09-12 14:25 | 2013-10-03 14:27 | 2013-09-12 14:25 | 2015-11-20 12:34 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:34 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151157 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply/distribution board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | 27/08/2013 - Completed - Certificate in Keystone | 2015-08-24 | Fully Completed | Gillian Kennedy | 2014-07-01 12:34 | 2014-07-22 12:36 | 2014-07-01 12:34 | 2015-08-25 16:39 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:36 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151159 | Completed | 1b | Medium | Miscellaneous | The covers of some of the lighting units located in the staircase enclosure of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units located in the staircases of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Complete | 2015-08-17 | Fully Completed | Gillian Kennedy | 2014-07-01 12:36 | 2014-08-30 12:38 | 2014-07-01 12:36 | 2015-08-18 11:28 | -60 | In target | 2014-07-01 12:36 | 2015-08-24 11:27 | Janice Wray
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 13:07 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151176 | Completed | 17 | Information Only | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building. But in the flats I looked at automatic domestic detection was fitted. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. The residents can contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. Is this on the electrical inspection schedule? | A & R Contract Management | Alex Bosman |  | Hard wired detectors to be installed during 5 year PIR program | 2015-03-23 | Fully Completed |  |  |  | 2014-07-01 13:07 | 2015-03-24 17:08
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:19 | S217012770006 | TALBOT GROVE HOUSE | 177703 | Completed | 1a | Medium | Emergency Lighting | The covers of some of the lighting units located in the common parts of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. Please also see item 15a below as some of the lights maybe combined emergency light units as well. | I would recommend that the covers of the lighting units located in the common parts of this building, on the staircases and the balconies are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux, and over 1 lux when tested on keyswitch | 2015-04-13 | Fully Completed | Gillian Kennedy | 2015-01-12 11:19 | 2015-03-13 11:20 | 2015-01-12 11:19 | 2015-04-14 10:19 | -60 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:58 | S217012770006 | TALBOT GROVE HOUSE | 177743 | Completed | 15a | High | Emergency Lighting | Most of the neon/charger indicator lights cannot be seen on what I think should be the emergency lighting units installed on the means of escape routes of this building. | I would recommend that the emergency lighting systems/units currently installed in this building is checked to see what units are emergency lights and what are not? The installed system should then be compared to the requirements of BS 5266 Part 1, any deficiencies found against the BS5266 layout requirements should be rectified by the installation of new emergency lighting units. | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade progra | 2015-12-14 | Fully Completed | Maria Ares | 2015-01-12 11:58 | 2015-02-02 11:59 | 2015-01-12 11:58 | 2015-12-15 12:01 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 12:07 | S217012770006 | TALBOT GROVE HOUSE | 177748 | Completed | 15b | High | Emergency Lighting | The covers of the emergency lighting units currently installed in the building are dirty, thus affecting the level of illuminating from the bulb and you cannot see the charger indicator light clearly. | I would recommend that the covers of the emergency lighting units currently installed in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels and help the caretakers to undertake the monthly checking of the emergency lighting system. | A & R Contract Management | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2015-01-12 12:07 | 2015-02-02 12:08 | 2015-01-12 12:07 | 2015-11-18 15:09 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 12:08 | S217012770006 | TALBOT GROVE HOUSE | 177750 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguishers in the 3 under staircase, ground floor electrical rooms of the building are out of test date according to the servicing labels, the last test date on the RGE contractor's labels being the 25th July 2012. | The carbon dioxide fire extinguishers in the three ground floor electrical rooms should be serviced immediately and it confirmed that they are on the external contractor's maintenance schedule. Alternatively they could be removed from the building and not serviced, they could be taken to the Lancaster West office as spares as these extinguishers have 4 to 5 years of service life left. . | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 3.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-01-12 12:08 | 2015-02-02 12:10 | 2015-01-12 12:08 | 2015-12-15 12:02 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 12:10 | S217012770006 | TALBOT GROVE HOUSE | 177752 | Completed | 23b | High | Emergency Lighting | There is an emergency lighting units/system currently installed on the means of escape routes of this building, | Can it please be conformed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 2.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-01-12 12:10 | 2015-02-02 12:11 | 2015-01-12 12:10 | 2015-12-15 12:03 | -21 | In target
TALBOT HOUSE -2015.05.11 | 2015-05-20 10:00 | S217009100001 | TALBOT HOUSE | 197939 | Completed | 15 | Medium | Emergency Lighting | When financially possible There is presently no emergency lighting installed on the means of escape routes of this building, on the walkways/balconies, on the staircase landings, in the entrance hall area or any of the common parts of this building. This is a five storey building. | As soon as financially possible I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed | Maria Ares | 2015-05-20 10:00 | 2015-07-19 10:26 | 2015-05-20 10:00 | 2015-11-23 14:53 | -60 | In target | 2015-05-20 10:00 | 2015-11-29 14:53 | Janice Wray
TALBOT HOUSE -2015.05.11 | 2015-05-20 10:26 | S217009100001 | TALBOT HOUSE | 197946 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the roof level lift motor room is out of service/test date according to the contractors servicing label attached to it. The last test date on this service label is the 8th October 2012. | The carbon dioxide portable fire extinguisher located in the roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 6.8.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-05-20 10:26 | 2015-06-10 10:27 | 2015-05-20 10:26 | 2015-11-27 11:27 | -21 | In target
TALBOT HOUSE -2015.05.11 | 2015-05-20 10:27 | S217009100001 | TALBOT HOUSE | 197947 | Completed | 23b | High | Fire Extinguisher | The carbon dioxide portable fire extinguisher located in the ground floor electrical cupboard/room under the concrete staircase is out of test date according to the contractor's servicing labels attached to it. The last test date on this service label being July 2013. | The carbon dioxide portable fire extinguisher located in the ground floor electrical room/ cupboard should be serviced immediately and it confirmed that it is on the external contractors maintenance schedule. Alternatively this extinguisher could be removed from this area and not serviced etc or replaced. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 6.8.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2015-05-20 10:27 | 2015-06-10 10:28 | 2015-05-20 10:27 | 2015-11-27 11:27 | -21 | In target
TALBOT WALK AND UPPER TALBOT WALK - 2015.06.22 | 2015-07-09 11:20 | S217012770008 | TALBOT WALK | 205726 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on each of the staircase landings of this building, the means of escape routes from the building. | Can it please be confirmed when the installed emergency lighting systems in this building were last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? ON KEYSTONE - dated 01/04 & no certificates | A & R Contract Management | Alex Bosman |  | AP confirmed service complete | 2015-12-14 | Fully Completed | Maria Ares | 2015-07-09 11:20 | 2015-07-30 11:22 | 2015-07-09 11:20 | 2015-12-15 12:04 | -21 | In target
TALBOT WALK AND UPPER TALBOT WALK - 2015.06.22 | 2015-07-09 11:24 | S217012770008 | TALBOT WALK | 205730 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the ground floor level electrical room with the water pump room at the rear of it is out of service/test date according to the contractors servicing label attached to it. The last test date on this RGE service label was July 2013. | This carbon dioxide fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-07-09 11:24 | 2015-07-30 11:25 | 2015-07-09 11:24 | 2015-12-15 12:04 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:17 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215314 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the landings of the staircases, on the balconies and in the entrance hall/lobby areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-07 16:17 | 2015-09-28 16:18 | 2015-09-07 16:17 | 2015-12-02 14:20 | -21 | In target
TAVISTOCK CRESCENT FLATS 43 TO 85 - 2015.08.27 | 2015-09-04 12:30 | S217010330001 | TAVISTOCK CRESCENT 43-63 ODD | 214931 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed on the landings of the staircases, on the balconies and in the entrance hall/lobby areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-04 12:30 | 2015-09-25 12:43 | 2015-09-04 12:30 | 2015-12-02 14:20 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:11 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173300 | Completed | 1b | Medium | Communal Lighting | The covers of some of the lighting units in the buildings are dirty, thus affecting the level of illuminating from the bulb. | I would recommend that the covers of the lighting units in the buildings are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels in the staircases and on the balconies. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-12-08 16:11 | 2015-02-06 16:12 | 2014-12-08 16:11 | 2015-04-14 10:20 | -60 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:58 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173322 | Completed | 15a | High | Emergency Lighting | There is presently an emergency escape lighting system installed in this building but the locations of these units and their positioning appears to be random and haphazard. | I would recommend that a full survey of the as installed emergency escape lighting system in this building is undertaken. This should then be compared to the requirements of BS 5266 and any deficiencies or lack of coverage then rectified. | A & R Contract Management | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade program | 2015-12-14 | Fully Completed | Maria Ares | 2014-12-08 16:58 | 2014-12-29 16:59 | 2014-12-08 16:58 | 2015-12-15 12:05 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:59 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173323 | Completed | 15b | High | Emergency Lighting | The covers of some of the emergency lighting units currently installed in this building are dirty. This means that the charger indicator light is not clearly visible as required by the British Standard. | I would recommend that the covers of the emergency lighting units currently installed in the building are cleaned, replaced or the charger indicator lights are replaced with brighter ones so that the neon indicators are easily seen. This will help the caretakers to undertake the monthly checking of the emergency lighting system. | A & R Contract Management | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2014-12-08 16:59 | 2014-12-29 17:00 | 2014-12-08 16:59 | 2015-11-18 15:11 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 17:02 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173325 | Active | 17a | High | Fire Alarm | There is a fire alarm system installed in this building, which is limited to two different areas of the building, the electrical intake rooms and the roof areas. The automatic detectors operate the smoke vents in the roofs and there are separate detectors which cover the electrical intake rooms only. There is no warning system and the locations of these installed devices and their positioning indicates that they are for a bespoke reason only. The control panel for this installed fire alarm system is located in the now disused reception area of Grenfell Tower. It is a serious offence under the Fire Safety Order not to maintain an installed fire alarm system. | 1.The reception area of Grenfell Tower is being refurbished, how is access to the fire alarm control panel being maintained? 2.It is assumed that the present fire alarm system is fully operational, if it is not repairs to the installed fire alarm system must be undertaken immediately. 3.Will the fire alarm control panel be relocated in the future? 4.To comply with the requirements of the Building Regulations the smoke vents located in the glazed roof areas of this building must be linked to local automatic smoke detection, how will this requirement be achieved? 5.How will the fire alarm system device installed in the electrical intake rooms be controlled and monitored? | A & R Contract Management | Alex Bosman
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:18 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173533 | Active | 17b | High | Fire Alarm | How is the fire alarm system in this building being monitored now that the Grenfell Tower reception is not in existence? | I would recommend that the fire alarm control panel for the detectors of the smoke vents and the ones located in the electrical intake rooms is connected to a monitoring stationed so in the event of an activation of the system the fire service or on duty caretaker can be informed. | A & R Contract Management | Alex Bosman
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:24 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173540 | Completed | 19c | High | Miscellaneous | There are automatic opening vents in the glazed ceiling of this building operated by smoke detectors. It is a serious offence under the Fire Safety Order not to maintain an installed fixed fire system. | Can it please be confirmed that these automatic opening vents are fully functional and in good working order? If they are not then a contractor should repair these automatic opening vents immediately. | A & R Contract Management | Alex Bosman | 2016-02-16 | Certification received confirming all in nworking condition COLT | 2016-02-16 | Fully Completed | Maria Ares | 2014-12-09 15:24 | 2014-12-30 15:25 | 2014-12-09 15:24 | 2016-02-17 10:56 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:25 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173543 | Completed | 19d | High | Miscellaneous | The reception area of Grenfell Tower is being refurbished and the control panel for the automatic opening vents in the glazed ceiling of this building and the other 2 nearby ones repositioned. | In the interim I would recommend that the fire service manual control switches located by the entrance door to each section of this building area checked and these are used to open the roof vents if needed. When the control panel for all of the automatic opening vents is repositioned then it should be fully tested before a commissioning certificate issue for it by the contractor. The control panel must be located/positioned so that it can easily be used and accessed but must not be in a location where it will be vandalised. | A & R Contract Management | Alex Bosman | 2016-01-13 | COLT confirmed drop keys operational | 2016-01-13 | Fully Completed | Maria Ares | 2014-12-09 15:25 | 2014-12-30 15:26 | 2014-12-09 15:25 | 2016-01-14 16:05 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:29 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173547 | Completed | 19f | Information Only | Miscellaneous | It appears that the last service and test on the water ring main was undertaken by M and P Fire Protection Limited on the 29th November 2013 and is therefore due to be undertaken again this month. The dry risers have been tested by Chubb on the 22nd October of this year. | I would recommend that it is confirmed that the contractor will be servicing and testing the water ring main in the lower ground floor level of this building this month. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 9.7.2015 | 2015-11-26 | Fully Completed |  |  |  | 2014-12-09 15:29 | 2015-11-27 12:55
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:31 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173551 | Active | 21 | High | Miscellaneous | There are automatic ventilation systems installed in this building. | Have the caretakers and any duty or on call managers/housing officers etc been given specific instructions on how to use the installed smoke ventilation system of this building? This instruction should also be included how to use the fire service manual control boxes located by the entrance doors to each section of this building. | A & R Contract Management | Alex Bosman
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:33 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173552 | Active | 23a | High | Fire Alarm | There is a fire alarm system installed in this building. | Can the TMO electrical engineer and the electrical contractor please confirm that the installed fire alarm system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc found rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:48 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173573 | Completed | 23c | High | Miscellaneous | There are automatic smoke ventilation systems installed in this building. | Are the automatic ventilation systems installed in this building being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2016-02-16 | Colt commisioned to carry out servicing of ventillation system. | 2016-02-16 | Fully Completed | Maria Ares | 2014-12-09 15:48 | 2014-12-30 15:49 | 2014-12-09 15:48 | 2016-02-17 10:56 | -21 | In target
TOR COURT - 2015.06.15 | 2015-06-29 11:43 | S217005550001 | TOR COURT | 203786 | Active | 15 | High | Emergency Lighting | A new emergency lighting system has been installed in this building recently. | Please can it be confirmed that the installation and/or commissioning certificates for this new emergency lighting system have be obtained from the contractors who installed the new emergency lighting units/system as required by BS 5266 Part 1 2011. If not the certificates should be obtained. NOT ON KEYSTONE | A & R Contract Management | Alex Bosman
TOR COURT - 2015.06.15 | 2015-06-29 11:44 | S217005550001 | TOR COURT | 203787 | Completed | 23a | High | Emergency Lighting | There is a new emergency lighting units/system installed on the balconies and on the staircase landings of this building. | Please can it confirmed that this newly installed emergency lighting system/units have been added to the contractors maintenance schedule for future annual servicing/testing including a full discharge test? Are records being kept of all the testing and servicing of this buildings emergency lighting system? NOT ON KEYSTONE | A & R Contract Management | Alex Bosman | 2016-01-13 | AP confirmed service complete 4.12.2015 | 2016-01-13 | Fully Completed | Maria Ares | 2015-06-29 11:44 | 2015-07-20 11:45 | 2015-06-29 11:44 | 2016-01-14 16:06 | -21 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:20 | S217008170001 | TREADGOLD HOUSE | 205785 | Completed | 23a | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings of this building and in the entrance hall/lobby area. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? KEYSTONE - last Cert 03/11 | A & R Contract Management | Alex Bosman |  | completed 17.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-07-09 12:20 | 2015-07-30 12:21 | 2015-07-09 12:20 | 2015-11-20 12:37 | -21 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:22 | S217008170001 | TREADGOLD HOUSE | 205789 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift room is out of test date according to the contractors servicing label attached to it, the last test date according to this servicing label was July 2013. | The portable fire extinguisher in this building's roof level lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | completed 17.09.15 | 2015-11-19 | Fully Completed | Maria Ares | 2015-07-09 12:22 | 2015-07-30 12:24 | 2015-07-09 12:22 | 2015-11-20 12:38 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:23 | S217008770001 | TRELLICK TOWER | 136750 | Completed | 1 | High | Electrical Wire Check | In the end staircase of the taller tower there are electrical cupboards on the staircase landings. There is a large black electrical cable in this staircase fixed to the walls coming from 3rd floor cupboard which says "To Afro Carribean(sic) Centre". | Can it be confirmed that the TMO know about this cable and that this cable has been installed correctly. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-03-26 16:23 | 2014-04-16 16:25 | 2014-03-26 16:23 | 2015-02-27 14:53 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:04 | S217008770001 | TRELLICK TOWER | 136788 | Completed | 18 | High | Fire Extinguisher | Very Dange-rous The horns on the carbon dioxide fire extinguishers in the upper most water tank room and the basement level area of the central core tower were not screwed up tightly. If a person were to use these fire extinguishers then they could suffer serious cold burns. | I would recommend that RGE are asked to explain why the carbon dioxide fire extinguishers in these two areas of the building have not be service correctly. RGE should service these fire extinguishers again correctly. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-26 17:04 | 2014-04-16 17:17 | 2014-03-26 17:04 | 2015-09-30 09:49 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:25 | S217008770001 | TRELLICK TOWER | 136801 | Completed | 23a | High | Emergency Lighting | There is a full emergency lighting system installed in this building to cover the common parts and the plant rooms etc. Is the installed emergency lighting system being serviced, tested and maintained. | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 24.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-03-26 17:25 | 2014-04-16 17:27 | 2014-03-26 17:25 | 2015-12-02 14:21 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:27 | S217008770001 | TRELLICK TOWER | 136802 | Completed | 23b | High | Fire Extinguisher | The portable fire extinguisher located in Plant room 21A is out of test date according to the contractors servicing label attached to it, the last service date being the 27th July 2011 | This fire extinguisher should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed complete | 2016-01-21 | Fully Completed | Maria Ares | 2014-03-26 17:27 | 2014-04-16 17:28 | 2014-03-26 17:27 | 2016-01-22 13:14 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:23 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181318 | Completed | 4 | High | Miscellaneous | There are electrical heaters built into wall cavities in this room, with the controls being located on the wall to the right hand side of the entrance doors to this room, as you enter it, next to the extract controls. | Can it please be confirmed if the heaters in this room are being serviced and checked in line with any manufactures instructions. If they are then no further action is needed, if they are not then I would recommend that servicing etc in accordance with the manufactures instructions is undertaken with any defects identified rectified. These then should be placed on a planned preventative maintenance schedule for annual servicing if required. | A & R Contract Management | Alex Bosman |  | All works completed 19.10.15 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-02 12:23 | 2015-02-23 12:25 | 2015-02-02 12:23 | 2015-12-02 14:22 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:26 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181319 | Completed | 6 | High | Miscellaneous | There are mechanical extractors located in this room, the controls for these extractors are located on the wall to the right hand side of the entrance doors to this room, as you enter it. | Can it please be confirmed if the extraction units in this room are being serviced and checked in line with any manufactures instructions. If they are then no further action is needed, if they are not then I would recommend that servicing etc in accordance with the manufactures instructions is undertaken with any defects identified rectified. The extractors should then placed on a planned preventative maintenance schedule for annual servicing. | A & R Contract Management | Alex Bosman |  | COMPLETE - EQUIPMENT PROTECTED BY RCD ON CIRCUIT | 2015-11-17 | Fully Completed | Maria Ares | 2015-02-02 12:26 | 2015-02-23 12:27 | 2015-02-02 12:26 | 2015-11-18 15:22 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 12:34 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181324 | Completed | 23a | High | Emergency Lighting | Is the emergency lighting system currently installed in this area being annually serviced, tested and maintained by the electrical contractor. | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this area is being serviced, tested and maintained as part the whole buildings system. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 24.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-02-02 12:34 | 2015-02-23 12:36 | 2015-02-02 12:34 | 2015-12-02 14:23 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:11 | S217015000050 | TREVERTON TOWER CLUBROOM | 239888 | Active | 1b | High | Miscellaneous | The retest date for the portable electrical appliances seen in the kitchen area, the kettle, water boiler, microwave is overdue according to the contractors test labels fixed to the items. Retesting was due in July 2013 according to one label. There is also a fridge/freezer in the electrical intake room. | I would recommend that all of the portable electrical appliance in this building that are out of test date are tested by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. | A & R Contract Management | Alex Bosman | 2016-02-25
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 16:10 | S217015000050 | TREVERTON TOWER CLUBROOM | 240137 | Active | 18 | High | Fire Extinguisher | There is presently no portable fire fighting equipment provided within this clubroom. | I would recommend that a carbon dioxide and a foam fire extinguisher is located by the kitchen area along with a fire blanket. | A & R Contract Management | Alex Bosman | 2016-02-26
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:12 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111266 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the buildings electrical supply board and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this premises or for the common parts of the tower block if they done at the same time. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring for this premises etc was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2013-10-18 11:12 | 2013-11-08 11:14 | 2013-10-18 11:12 | 2014-07-15 15:56 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:17 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111268 | Completed | 1c | High | Electrical Wire Check | The retest date for the portable electrical appliances is overdue according to the contractors test labels fixed to the items. Retesting was due last month, July 2013. | I would recommend that all the portable electrical appliance in this building are testing by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. For your information 2 year testing is now the normal time period not annually. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-10-18 11:17 | 2013-11-08 11:18 | 2013-10-18 11:17 | 2015-02-27 14:55 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:19 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111269 | Completed | 1d | High | Electrical Wire Check | On the ceiling of this premises there are two bars of coloured lights which have cables running from them, fixed to the ceiling by cable clips or tape back to plugs. | Can it be confirmed that these two bars of coloured lights are on the electrical testing schedule as they are not part of the fixed lighting circuit. | A & R Contract Management | Alex Bosman |  | Works complete | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-10-18 11:19 | 2013-11-08 11:20 | 2013-10-18 11:19 | 2015-02-27 14:56 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 11:20 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111270 | Completed | 1e | High | Electrical Wire Check | It is not known if the fridge/freezer located under the work surface in the kitchen area is being electrically tested. | Can it be confirmed that the fridge is on the electrical testing schedule | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-10-18 11:20 | 2013-11-08 11:21 | 2013-10-18 11:20 | 2015-02-27 14:57 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 12:15 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111306 | Completed | 4 | High | Electrical Wire Check | It is not known if the wall mounted electrical water heater located over the sink in the kitchen area is included in the electrical testing of this premises. | Can it please be confirmed that this electrical water heater is being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | COMPLETE - EQUIPMENT PROTECTED BY RCD ON CIRCUIT | 2015-11-17 | Fully Completed | Maria Ares | 2013-10-18 12:15 | 2013-11-08 12:21 | 2013-10-18 12:15 | 2015-11-18 15:24 | -21 | In target
TREVERTON CLUBROOM-2013.08.06 | 2013-10-18 12:32 | U217015000050 | CLCM COMMUNITY TREVERTON TOWER CLUBROOM | 111315 | Completed | 23 | High | Emergency Lighting | There are no records of the monthly occupiers tests and inspections of the emergency lighting system, fire extinguishers etc, are these tests are being undertaken? | Can it be confirmed that all the monthly occupier's tests and inspections are being undertaken as per the caretaker's checklist? | A & R Contract Management | Alex Bosman |  | ESA training completed - ongoing refresher to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-10-18 12:32 | 2013-11-08 12:33 | 2013-10-18 12:32 | 2014-07-15 16:42 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 15:50 | S217010420001 | TREVERTON TOWER | 148231 | Completed | 1a | High | Electrical Wire Check | According to the contractors label on the electrical supply board in the basement cleaners/caretakers area of this building the last fixed electrical wiring test was on the 25th July 2001 and it was due to be retested in July 2006. | Can it be confirmed with the TMO electrical engineer if the fixed wiring of the basement cleaners/caretakers area of this building has been retested. If it has not, a fixed wiring test should be undertaken with any defects identified rectified and this area then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | included on 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2014-06-11 15:50 | 2014-07-02 17:34 | 2014-06-11 15:50 | 2014-07-15 15:58 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 16:46 | S217010420001 | TREVERTON TOWER | 148276 | Completed | 1b | High | Electrical Wire Check | There is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for the common parts of this building. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in the common parts of the building was last tested. If this was more than 5 years ago then it should be retested with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2014-06-11 16:46 | 2014-07-02 17:34 | 2014-06-11 16:46 | 2014-07-15 15:59 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 16:51 | S217010420001 | TREVERTON TOWER | 148280 | Completed | 1c | Medium | Communal Lighting | The covers of some of the lighting units located in the staircase enclosure of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of the lighting units located at the roof level of this building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-06-11 16:51 | 2014-08-10 16:55 | 2014-06-11 16:51 | 2015-04-14 10:21 | -60 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:04 | S217010420001 | TREVERTON TOWER | 148281 | Completed | 5 | High | Lifts | There is a wheel chair lift located outside flat number 4, if this is a tenanted flat and this lift was installed by the TMO, is this lift serviced and maintained? | If this is a tenanted flat and this chair lift was installed by the TMO I would recommend that the TMO mechanical engineers asked if this lift in serviced and maintained as per the manufactures instructions. If this is a leaseholder and the TMO did not install this chair lift then no action is needed on this subject. | A & R Contract Management | Alex Bosman |  | Lift included in Stannah service contract. valid cert held by TMO | 2014-10-08 | Fully Completed | Alex Bosman | 2014-06-11 17:04 | 2014-07-02 17:05 | 2014-06-11 17:04 | 2014-10-09 14:41 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:16 | S217010420001 | TREVERTON TOWER | 148291 | Active | 15 a & b | High |  | There are lighting units located on the landings of the staircase but there are no neon charging/indicator lights visible on these light units. On the external balconies there are light units with the neon charging/indicator lights clearly visible so it can be seen that these are also emergency lighting units. | Can it be confirmed that the lighting units in the staircase enclosure are also emergency lighting units as no neon indicator/charging lights could be seen on these units. If it is found that the lighting units in the staircase enclosure are also emergency lighting units why are the neon indicator/charging lights not visible on these units. The occupiers monthly tests and inspections cannot be undertaken if the charge light cannot be seen. Also the emergency lighting requirement should then be compared to the requirements of BS 5266 Part 1 2011 and the risk assessment section and then any deficiencies or lack of coverage then rectified This building is over two storeys in height and new lighting was installed during the refurbishment in 2011 so I would expect to find emergency lighting in the staircase enclosure of a tower block. If it is found that no emergency lighting units are fitted within this staircase enclosure then some must be fitted to the requirements of BS 5266 Part 1 2011 including the risk assessment section | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2014-06-11 17:16 | 2014-07-02 17:20 |  |  | 644 | 644 days overdue
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:28 | S217010420001 | TREVERTON TOWER | 148295 | Active | 23a | High | Emergency Lighting | The emergency lighting system installed to cover the common parts of this building at the time of the last refurbishment does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2014-06-11 17:28 | 2014-07-02 17:29 |  |  | 644 | 644 days overdue
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:04 | S217005570001 | WALNUT TREE HOUSE | 103497 | Active | 15 | Medium | Emergency Lighting | There appeared to be no emergency lighting units in the corridor directly outside flats 2 and 3's entrance doors and directly outside flats 33 and 35's entrance doors. These locations are above each other but on the 1st and 3rd floor levels, there are emergency lighting units covering all the other corridors. | Could it please be confirmed that there are emergency lighting units in the corridors directly outside these flats. If there are units installed why are the neon indicator lights not glowing, if there are no units installed then some should be to conform to the requirements of BS 5266 Part 1. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. | 2015-05-12 | Partially Completed | Maria Ares | 2013-08-23 12:04 | 2013-10-22 12:24 |  |  | 897 | 897 days overdue
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:25 | S217005570001 | WALNUT TREE HOUSE | 103503 | Completed | 23a | High | Emergency Lighting | The emergency lighting units/system currently installed to cover the common parts of this building does not appear on the electrical asset list as supplied by the TMO electrical engineer. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | System added to asset register for inclusion in future servicing | 2013-12-09 | Fully Completed | Alex Bosman | 2013-08-23 12:25 | 2013-09-13 12:26 | 2013-08-23 12:25 | 2013-12-10 18:00 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:26 | S217005570001 | WALNUT TREE HOUSE | 103504 | Completed | 23b | High | Lightning Protection | There is a lightning protection system installed on this building, this system does not appear on the asset list as supplied by the TMO engineer. Is the installed lightning protection system being serviced, tested and maintained. | I would recommend that the TMO engineer is asked if the installed lightning protection system is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | RMA confirmed system tested and remidial works in progress | 2015-12-14 | Fully Completed | Maria Ares | 2013-08-23 12:26 | 2013-09-13 12:28 | 2013-08-23 12:26 | 2015-12-15 12:07 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:29 | S217005570001 | WALNUT TREE HOUSE | 103506 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2013-08-23 12:29 | 2013-09-13 12:30 | 2013-08-23 12:29 | 2015-02-27 14:59 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:57 | S217005570001 | WALNUT TREE HOUSE | 103511 | Completed | 18 | High | Fire Extinguisher | There is a carbon dioxide fire extinguisher located in each of the two ground floor level electrical cupboards. | The fire extinguishers could be removed from the cupboards and no signs displayed. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2013-08-23 12:57 | 2013-09-13 12:59 | 2013-08-23 12:57 | 2015-09-30 09:49 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:58 | S217012740010 | WHISTLER TOWER 1-61 | 102317 | Completed | 23a | High | Emergency Lighting | The emergency escape lighting system/units currently installed on the landings of the staircase and in the lift motor room does not appear on the electrical asset list as supplied by the TMO electrical engineers. Is the installed emergency lighting system being serviced, tested and maintained? | I would recommend that the electrical contractor is asked if the installed emergency lighting system in this building is being serviced, tested and maintained. If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman | 2013-09-06 | System added to Keystone asset register for inclusion in future servicing program | 2013-10-01 | Fully Completed | Alex Bosman | 2013-08-16 15:58 | 2013-09-06 16:00 | 2013-08-16 15:58 | 2013-10-02 16:43 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 16:01 | S217012740010 | WHISTLER TOWER 1-61 | 102318 | Completed | 23b | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, fire fighting lifts, dry riser and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | A & R Contract Management | Alex Bosman | 2013-09-06 | ESA training completed - ongoing refresher to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2013-08-16 16:01 | 2013-09-06 16:03 | 2013-08-16 16:01 | 2014-07-15 16:52 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 14:53 | S217012740010 | WHISTLER TOWER 1-61 | 102273 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards of this building and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman | 2013-09-06 | block included in 13/14 block testing program | 2013-10-01 | Partially Completed | Alex Bosman | 2013-08-16 14:53 | 2013-09-06 14:58 | 2013-08-16 14:53 | 2013-10-02 16:40 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:12 | S217009090002 | WHITCHURCH HOUSE | 142358 | Completed | 1a | High | Miscellaneous | It is not known if the washing machines and tumble dryers in the laundry are being serviced or electrically tested. | Can it please be confirmed that the electrical items in the laundry area are being serviced and electrically tested according to the manufactures instructions. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-05-06 14:12 | 2014-05-27 14:14 | 2014-05-06 14:12 | 2015-02-27 15:00 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:15 | S217009090002 | WHITCHURCH HOUSE | 142362 | Completed | 1c | Medium | Communal Lighting | Some of the covers of the lighting units in the common parts of this building are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the dirty covers of the lighting units in the building are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels especially in the staircases. | A & R Contract Management | Alex Bosman |  | Covers are either dirty or opaque in design.the illumination was measured and found to be acceptable at between 10-40 lux | 2015-04-13 | Fully Completed | Gillian Kennedy | 2014-05-06 14:15 | 2014-07-05 14:17 | 2014-05-06 14:15 | 2015-04-14 10:21 | -60 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:17 | S217009090002 | WHITCHURCH HOUSE | 142367 | Completed | 5 | High | Standby Generator | his building has a stand by diesel generator in it. I have been told that this stand by diesel generator is now not longer being used, if this is correct please see the next column. According to the information held on site this generator has not been serviced for at least a year now. | Please can it be confirmed that the stand by diesel generator in this building is now not being used ? If this is the case can the following also please be confirmed. 1. That the generator has been disconnected from all the electrical circuits that it use to backed up? 2. Have all the electrical circuits been correctly isolated? 3. Have the backed up circuits been checked to see that they are now compliant? Ie the emergency lighting units, lift etc, if not this check should be undertaken immediately. 4. Has all the diesel fuel been drained from the generator and any stand by tanks? 5. I would recommend that a large sign is placed on the generator stating that it is not now in use. If the generator has not been taken out of use it should be serviced and run immediately and all the electrical circuits that it backs up checked to see that they work correctly. Monthly running under load, servicing and maintenance should be undertaken in accordance with the manufactures recommendations. | A & R Contract Management | Alex Bosman |  | Confirmed that standby genorators are no longer required as all systems have battery back up. Genorators to be removed 2015/16 | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-05-06 14:17 | 2014-05-27 14:19 | 2014-05-06 14:17 | 2015-02-27 20:38 | -21 | In target | 2014-05-06 14:17 | 2015-03-05 20:37 | Janice Wray
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:34 | S217009090002 | WHITCHURCH HOUSE | 142387 | Completed | 15 | High | Standby Generator | It appears that the stand by generator is now not in use, all of the emergency lighting units in this building should now be self contained units. | Please can it be confirmed that all of the emergency lighting units in this building are self contained ones and not backed up by the stand by generator as it appears that the generator is now not in use. If it is found that any emergency lighting units are not self contained ones then they must be changed immediately for self contained ones if the stand by generator is now not in use. | A & R Contract Management | Alex Bosman |  | Confirmed that standby genorators are no longer required as all systems have battery back up. Genorators to be removed 2015/16 | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-05-06 14:34 | 2014-05-27 14:35 | 2014-05-06 14:34 | 2015-02-27 15:02 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:41 | S217009090002 | WHITCHURCH HOUSE | 142391 | Completed | 18a | High | Fire Extinguisher | There is a dry powder fire extinguisher located by the stand by generator room, this fire extinguisher was last serviced in October 2009 according to the information on the RGE contractors label. | This dry powder fire extinguisher should be serviced immediately and it confirmed that it is on the external contractors maintenance schedule. If the generator is no longer in use then this extinguisher could be removed and not serviced, the external contractor's maintenance schedule should be amended to show this change. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-05-06 14:41 | 2014-05-27 14:43 | 2014-05-06 14:41 | 2015-09-30 09:50 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:45 | S217009090002 | WHITCHURCH HOUSE | 142394 | Completed | 19 | Information Only | Hose Reels | There are fire fighting hose reels located on each floor level of the building. These could be removed if TMO wanted too as there is sufficient portable fire fighting equipment in the building. | No actions are needed, this item is for information only, but please see item 21a | A & R Contract Management | Alex Bosman |  | COMPLETE - INFORMATION NOTED | 2015-11-17 | Fully Completed |  |  |  | 2014-05-06 14:45 | 2015-11-18 15:27
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:47 | S217009090002 | WHITCHURCH HOUSE | 142397 | Completed | 21a | High | Hose Reels | There are fire fighting hose reels installed in this building. | Have any staff, wardens/caretakers etc who may be employed in this building been given training on the use of fire fighting hose reels? If they have not, then training should be given immediately, this is while hose reels are installed in this building. | A & R Contract Management | Alex Bosman |  | ESA training completed. Ongoing training to be completed by ESA management & H&S | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-05-06 14:47 | 2014-05-27 14:48 | 2014-05-06 14:47 | 2015-02-27 15:03 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:50 | S217009090002 | WHITCHURCH HOUSE | 142401 | Completed | 23a | High | Miscellaneous | There are automatic ventilation units, smoke control, installed on the windows in the corridors of this building. | Is the ventilation system installed in the building being serviced, tested and maintained by a contractor as per the manufactures instructions? If it is not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems placed on the contractors maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 15.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-05-06 14:50 | 2014-05-27 14:51 | 2014-05-06 14:50 | 2015-11-27 13:00 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:51 | S217009090002 | WHITCHURCH HOUSE | 142404 | Completed | 23b | High | Fire Alarm | The fire alarm system in this building extends into the private flats. | Can it please be confirmed by the TMO electrical engineer and the fire alarm maintenance company that the devices of the fire alarm system installed in the private flats/dwellings are all being serviced and maintained at the same time as the devices in the common parts of the building? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 16.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-05-06 14:51 | 2014-05-27 14:53 | 2014-05-06 14:51 | 2015-11-27 13:34 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:53 | S217009090002 | WHITCHURCH HOUSE | 142405 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of test date according to the contractor's service label attached to it. The last test date on the service label being the 27th February 2013 | This fire extinguisher in the lift motor room should be serviced immediately and it confirmed that it is on the external contractor's maintenance schedule. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 25.9.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-05-06 14:53 | 2014-05-27 14:54 | 2014-05-06 14:53 | 2015-11-27 13:37 | -21 | In target
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:42 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214794 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed on the means of escape routes of this building, that is on the walkways/balconies or on the landings of the staircases, ie in the common parts of this building. This is a five and six storey building. There are emergency lighting units in the lift lobby areas. | As soon as financially possible or if any work is being undertaken on the common parts lighting. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included within this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-09-03 16:42 | 2015-11-23 16:28 |  |  | 2015-09-03 16:42 | 2015-11-29 16:28 | Janice Wray
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:44 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214795 | Completed | 23a | High | Emergency Lighting | There are some emergency lighting units installed in one part of this building, on the lift lobby areas, in the roof space areas and some external units. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 27.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2015-09-03 16:44 | 2015-09-24 16:53 | 2015-09-03 16:44 | 2015-12-15 12:09 | -21 | In target
WILTSHIRE CLOSE FLATS 1 TO 34 - 2015.07.27 | 2015-09-03 16:55 | S217011667702 | WILTSHIRE CLOSE (1-34) | 214802 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of service date according to the RGE contractors label on it. The last service was on the 18th October 2012. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-03 16:55 | 2015-09-24 16:56 | 2015-09-03 16:55 | 2015-12-02 14:24 | -21 | In target
WILTSHIRE CLOSE FLATS 147 TO 180 - 2015.07.27 | 2015-09-09 14:58 | S217011667704 | WILTSHIRE CLOSE (147-180) | 215716 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed on the means of escape routes of this building, that is on the walkways/ balconies or on the landings of the staircases, ie in the common parts of this building. This is a five and six storey building. There are emergency lighting units in the lift lobby areas. | As soon as financially possible or if any work is being undertaken on the common parts lighting. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | 147 has emergency lighting and is due 2024, 155 does not and needs installation. Will be included within this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-09-09 14:58 | 2015-11-23 16:30 |  |  | 2015-09-09 14:58 | 2015-11-29 16:30 | Janice Wray
WILTSHIRE CLOSE FLATS 147 TO 180 - 2015.07.27 | 2015-09-09 15:00 | S217011667704 | WILTSHIRE CLOSE (147-180) | 215718 | Completed | 23a | High | Emergency Lighting | There are some emergency lighting units installed in one part of this building, on the lift lobby areas, in the roof space areas and some external units. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:00 | 2015-09-30 15:01 | 2015-09-09 15:00 | 2015-12-02 14:25 | -21 | In target
WILTSHIRE CLOSE FLATS 147 TO 180 - 2015.07.27 | 2015-09-09 15:03 | S217011667704 | WILTSHIRE CLOSE (147-180) | 215721 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of service date according to the RGE contractors label on it. The last service was on the 13th October 2012. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:03 | 2015-09-30 15:04 | 2015-09-09 15:03 | 2015-12-02 14:26 | -21 | In target
WILTSHIRE CLOSE FLATS 181 TO 214 - 2015.07.27 | 2015-09-04 09:05 | S217011667706 | WILTSHIRE CLOSE (181-188) | 214821 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed on the means of escape routes of this building, that is on the walkways/ balconies or on the landings of the staircases, ie in the common parts of this building. This is a five and six storey building. There are emergency lighting units in the lift lobby areas. | As soon as financially possible or if any work is being undertaken on the common parts lighting. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. | A & R Contract Management | Alex Bosman |  | COMPLETE - INCLUDED WITHIN PROGRAMME OF WORKS | 2015-11-17 | Fully Completed |  |  |  | 2015-09-04 09:05 | 2015-11-18 15:28
WILTSHIRE CLOSE FLATS 181 TO 214 - 2015.07.27 | 2015-09-04 09:07 | S217011667706 | WILTSHIRE CLOSE (181-188) | 214822 | Completed | 23a | High | Emergency Lighting | There are some emergency lighting units installed in one part of this building, on the lift lobby areas, in the roof space areas and some external units. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-04 09:07 | 2015-09-25 09:08 | 2015-09-04 09:07 | 2015-12-02 14:26 | -21 | In target
WILTSHIRE CLOSE FLATS 181 TO 214 - 2015.07.27 | 2015-09-04 09:10 | S217011667706 | WILTSHIRE CLOSE (181-188) | 214827 | Completed | 23c | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of service date according to the RGE contractors label on it. The last service was October 2012. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-04 09:10 | 2015-09-25 09:11 | 2015-09-04 09:10 | 2015-12-02 14:27 | -21 | In target
WILTSHIRE CLOSE FLATS 35 TO 68 - 2015.07.27 | 2015-09-09 15:15 | S217011667711 | WILTSHIRE CLOSE (35-68) | 215729 | Completed | 15 | Information Only | Emergency Lighting | There is presently no emergency lighting installed on the means of escape routes of this building, that is on the walkways/ balconies or on the landings of the staircases, ie in the common parts of this building. This is a five and six storey building. There are emergency lighting units in the lift lobby areas. | As soon as financially possible or if any work is being undertaken on the common parts lighting. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-09-09 15:15 | 2015-11-23 16:31 |  |  | 2015-09-09 15:15 | 2015-11-29 16:31 | Janice Wray
WILTSHIRE CLOSE FLATS 35 TO 68 - 2015.07.27 | 2015-09-09 15:17 | S217011667711 | WILTSHIRE CLOSE (35-68) | 215730 | Completed | 23a | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in the roof level lift motor room is out of service date according to the RGE contractors label on it. The last service was on the 18th October 2012. | This fire extinguisher should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 26.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:17 | 2015-09-30 15:18 | 2015-09-09 15:17 | 2015-12-02 14:28 | -21 | In target
WILTSHIRE CLOSE FLATS 35 TO 68 - 2015.07.27 | 2015-09-09 15:18 | S217011667711 | WILTSHIRE CLOSE (35-68) | 215732 | Completed | 23b | High | Emergency Lighting | There are some emergency lighting units installed in one part of this building, on the lift lobby areas, in the roof space areas and some external units. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago these emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed servicing complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:18 | 2015-09-30 15:20 | 2015-09-09 15:18 | 2015-12-02 14:28 | -21 | In target
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:41 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215751 | Completed | 15 | Information Only |  | There is presently no emergency lighting installed on the means of escape routes of this building, that is on the open external walkways/balconies or on the landings of the staircases, ie in the common parts of this building. This is a six storey building. There are emergency lighting units in the lift motor rooms. | As soon as financially possible or if any work is being undertaken on the common parts lighting. I would recommend that emergency lighting units are installed on the means of escape routes, the common parts of this building. This is to provide illumination of the means of escape routes if the normal lighting fails. Any installed emergency lighting should be to British Standard 5266 Part 1 at the time of installation, including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Will be included into this years programme if there is capacity. If not budget year 16/17 | 2015-11-19 | Fully Completed |  |  |  | 2015-09-09 15:41 | 2015-11-23 16:32 |  |  | 2015-09-09 15:41 | 2015-11-29 16:32 | Janice Wray
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:43 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215754 | Completed | 23a | High | Emergency Lighting | There are emergency lighting units installed in each of the two roof level lift rooms. | Can it please be confirmed when these installed emergency lighting units in the lift motor rooms were last serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266. If this last test/service was more that 1 year ago these emergency lighting units should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 20.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:43 | 2015-09-30 15:45 | 2015-09-09 15:43 | 2015-12-02 14:29 | -21 | In target
WILTSHIRE CLOSE FLATS 69 TO 146 - 2015.07.27 | 2015-09-09 15:45 | S217011667713 | WILTSHIRE CLOSE (69-146) | 215756 | Completed | 23b | High | Fire Extinguisher | The carbon dioxide fire extinguisher located in each of the roof level lift motor rooms is out of service date according to the RGE contractors label on them. The last service of these extinguishers was in January 2012. | These fire extinguishers should be serviced immediately. | A & R Contract Management | Alex Bosman |  | AP confirmed servie complete 26.11.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2015-09-09 15:45 | 2015-09-30 15:46 | 2015-09-09 15:45 | 2015-12-02 14:29 | -21 | In target
WINCHESTER HOUSE, BEAUFORT STREET, LONDON SW3 5BJ - 2016.02.11 | 2016-04-04 10:39 | S217000310004 | WINCHESTER HOUSE | 252231 | Active | 5a | High | Miscellaneous | On the top floor level of the staircase landing by flats 25 to 28 and behind the ground floor staircase entrance door in the other staircase there is a wall mounted box which has marked on it "Fan Switch/Ventilation". | Can it be confirmed what these switches are for?, is it for or connected with the extraction equipment in the roof space areas? Can it be confirmed that any maintenance or servicing is being undertaken as per the manufacturers requirements for the roof space extraction systems. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman | 2016-05-09
WINCHESTER HOUSE, BEAUFORT STREET, LONDON SW3 5BJ - 2016.02.11 | 2016-04-04 10:48 | S217000310004 | WINCHESTER HOUSE | 252234 | Active | 14a | High | Miscellaneous | Are there any fire dampers or filters installed in the extraction units located in the roof space areas? | If any dampeners or filters are installed within the roof space area extraction systems are these on a maintenance and servicing contract, if applicable? | A & R Contract Management | Alex Bosman | 2016-05-09
WINCHESTER HOUSE, BEAUFORT STREET, LONDON SW3 5BJ - 2016.02.11 | 2016-04-04 10:58 | S217000310004 | WINCHESTER HOUSE | 252241 | Active | 15 | High | Emergency Lighting | There was a new emergency lighting system/units installed to cover the means of escape route of each staircase of this building. On the staircase landings and also in the lower ground floor electrical rooms/cupboards and in the roof space areas. | I would recommend that the buildings file is check to see if all the correct documentation is contained within it reference these new emergency lighting systems/units. There should be design, installation and completion certificates etc to the model standards in BS 5266 Part 1 2011. If these are not available then the contractor who installed the systems should be asked to provide all the relevant documentation including as installed drawings. This is evidence of correct installation etc if the enforcing authorities undertake an audit of this building and question the installation. | A & R Contract Management | Alex Bosman | 2016-05-09
WINCHESTER HOUSE, BEAUFORT STREET, LONDON SW3 5BJ - 2016.02.11 | 2016-04-04 11:00 | S217000310004 | WINCHESTER HOUSE | 252242 | Active | 23c | High | Emergency Lighting | There are emergency lighting units installed on the means of escape route of each staircase of this building, on the landings of the staircases and in the entrance hall areas. Keystone checked | Can it please be confirmed that all of the installed emergency lighting system/units in this building have been serviced, tested and a discharge test of these units batteries undertaken, to the requirements of BS5266 in the last 12 months. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? | A & R Contract Management | Alex Bosman | 2016-05-09
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:27 | S217012746601 | WORLDS END ESTATE CAR PARK | 134335 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on any electrical supply boards in this car park and there is no information on the TMO electrical engineers asset list when the last 5 year electrical fixed wiring test was carried out for this car park. | Could the TMO electrical engineer confirm the last date when the electrical fixed wiring in this car park? If the last test was more than 5 years ago then it should be retested with any defects identified rectified and then put on a planned preventative maintenance schedule. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2014-03-12 16:27 | 2014-04-02 16:28 | 2014-03-12 16:27 | 2014-07-15 16:00 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:42 | S217012746601 | WORLDS END ESTATE CAR PARK | 134347 | Completed | 3a | High | Miscellaneous | At the time of this assessment the internally located emergency manual override buttons by the vehicle openings did not work. | I would recommend that these emergency manual override buttons at the vehicle openings are checked to make certain that they work correctly. If they do not they should be repaired of replaced so that in an emergency the barriers etc can be opened. Alex - under maintenance contract?? | A & R Contract Management | Alex Bosman |  | Completed during current works. | 2015-08-07 | Fully Completed | Gillian Kennedy | 2014-03-12 16:42 | 2014-04-02 16:51 | 2014-03-12 16:42 | 2015-08-10 16:05 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:57 | S217012746601 | WORLDS END ESTATE CAR PARK | 134350 | Active | 5 | High | Miscellaneous | There does not appear to be a mechanical air/exhaust extraction system installed in this car park and there is limited natural ventilation of this area. | I would recommend that a suitably qualified person/contractor is asked to assess the ventilation aspects of this car park and produce a report on ventilation for this car park. Any outcomes from this report should then be implemented. | A & R Contract Management | Alex Bosman
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:11 | S217012746601 | WORLDS END ESTATE CAR PARK | 134360 | Completed | 15 | Information Only | Emergency Lighting | As soon as financially possible There appears to be some emergency lighting units installed in this car park area, but this installation is not to a recognised standard. Emergency lighting units appear to just be randomly fitted. There are also some emergency lighting units in the plant rooms areas. | As soon as financially possible I would recommend that new or additional emergency lighting units are installed in this car park and in the plant room areas. This should be to the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | A & R Contract Management | Alex Bosman |  | Inspection complete. Report and costs to follow. COMPLETE - INCLUDED WITH PROGRAMMED WORKS | 2015-11-17 | Fully Completed |  |  |  | 2014-03-12 17:11 | 2015-11-18 15:30
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:15 | S217012746601 | WORLDS END ESTATE CAR PARK | 134363 | Completed | 18a | High | Fire Extinguisher | There are dry powder and foam fire extinguishers located side by side in this car park. These two types of fire extinguisher should not be located together as one counter acts the other one. | I would recommend that the dry powder fire extinguishers are removed from this car park, if dry powder fire extinguishers are located in the plant rooms this is ok as long as a Health and Safety assessment has been undertaken. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-12 17:15 | 2014-04-02 17:16 | 2014-03-12 17:15 | 2015-09-30 09:52 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:16 | S217012746601 | WORLDS END ESTATE CAR PARK | 134364 | Completed | 18b | High | Fire Extinguisher | The fire extinguishers missing from the wall mounted red plastic boxes in this car park should be replaced and the boxes secured again. | Please see the other items reference fire extinguishers but any missing ones from the wall mounted boxes in the car park area should be replaced with serviced and in date fire extinguishers immediately. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-12 17:16 | 2014-04-02 17:17 | 2014-03-12 17:16 | 2015-09-30 09:53 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:18 | S217012746601 | WORLDS END ESTATE CAR PARK | 134366 | Completed | 19 | High | Hose Reels | There are water hose reels provided in this car park, this car park does not have anybody employed to work in it. These two hose reels were last serviced and tested in September 2011 according to the RGE contractors servicing labels on them. | The fire fighting hose reels in this car park are not required. The fire signage on the water hose reels in this car park could be removed so that they are just normal hose reels which could be used for washing down etc or the hose reels could be removed completely. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-12 17:18 | 2014-04-02 17:19 | 2014-03-12 17:18 | 2015-09-30 09:53 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:22 | S217012746601 | WORLDS END ESTATE CAR PARK | 134369 | Completed | 23a | High | Fire Extinguisher | The fire extinguishers and the hose reels located in this car park and the plant rooms off of it are all out of test date according to the servicing labels attached to them. The last test date on most being in September 2011. | The fire extinguishers in this car park and in the plant rooms located off of it must be serviced and tested immediately with any defective ones removed and replaced. Please see item 19 reference the hose reels before these are serviced. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 28.11.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-03-12 17:22 | 2014-04-02 17:24 | 2014-03-12 17:22 | 2015-12-15 12:10 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:24 | S217012746601 | WORLDS END ESTATE CAR PARK | 134372 | Completed | 23b | High | Fire Extinguisher | The fire extinguishers in the water booster room have "condemned" written on them in large black writing and were last serviced on the 24th September 2011 according to the RGE contractors service labels. | If these fire extinguishers are condemned then they should be replaced immediately. I would recommend that the fire extinguisher contractor is asked why condemned items have been left on site and available to be used and these items are over 2 years past a service. | A & R Contract Management | Alex Bosman |  | Completed | 2015-09-28 | Fully Completed | Gillian Kennedy | 2014-03-12 17:24 | 2014-04-02 17:25 | 2014-03-12 17:24 | 2015-09-30 09:54 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:25 | S217012746601 | WORLDS END ESTATE CAR PARK | 134373 | Completed | 23c | High | Fire Extinguisher | Some of the fire extinguishers in the plant rooms off of this car park have "condemned" written on them in large black writing. This seems to indicate that monthly occupier inspections of the fire extinguishers are not being carried out as the inspections would have spotted the writing and the last service date was in 2011. | It should be confirmed with the caretakers if they have carrying out monthly occupier's inspections of the fire fighting extinguishers as per the caretakers check list. If the monthly checks are not being undertaken they should be started immediately. | A & R Contract Management | Alex Bosman |  | ESA training completed - ongoing refresher training to be arranged by H&S and team leaders | 2014-07-14 | Fully Completed | Alex Bosman | 2014-03-12 17:25 | 2014-04-02 17:27 | 2014-03-12 17:25 | 2014-07-15 16:55 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:29 | S217012746601 | WORLDS END ESTATE CAR PARK | 134376 | Completed | 23e | High |  | The emergency lighting units/system currently installed in the plant rooms off this car park and the ones in the car park do not appear on the electrical asset list as supplied by the TMO electrical engineer and there are no documents on site indicating that contractor servicing etc has been undertaken. Are the installed emergency lighting system/units being serviced, tested and maintained? | I would recommend that the TMO electrical engineer and the electrical contractor are asked if the installed emergency lighting system/units in the plant rooms and the car park are being serviced, tested and maintained. If they are not, testing and servicing should be undertaken immediately and any defects etc rectified and then the systems with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed service complete 4.12.2015 | 2015-12-14 | Fully Completed | Maria Ares | 2014-03-12 17:29 | 2014-04-02 17:30 | 2014-03-12 17:29 | 2015-12-15 12:10 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:27 |  |  | 122455 | Completed | 1a | High | Electrical Wire Check | There are no contractor's labels on the electrical supply boards in this club room and according to the TMO electrical engineers asset list the last recorded 5 year electrical fixed wiring test of this building would have expired in 2012. | Could it be confirmed with the TMO electrical engineer if the fixed wiring in the building is in test date. If it is not, a fixed wiring test should be undertaken with any defects identified rectified and the building then put on a planned preventative maintenance schedule for retesting. | A & R Contract Management | Alex Bosman |  | included in 14/15 communal testing program | 2014-07-14 | Fully Completed | Alex Bosman | 2014-01-03 11:27 | 2014-01-24 11:31 | 2014-01-03 11:27 | 2014-07-15 16:02 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:31 |  |  | 122457 | Completed | 1b | High | Inspection Regime | There is an electrical cooker in the kitchen of this clubroom and a fridge, it is not known if these electrical items were inspected/ tested when the portable electrical appliances were last tested in this premises. | Can it please be confirmed that the electrical cooker and the fridge in the kitchen are tested/serviced/inspected as per any manufactures guidance and PAT if required. If these items were not PAT or tested/inspected as required then I would recommend that it is undertaken and any defects found rectified. | A & R Contract Management | Alex Bosman |  | Included in 2014/15 testing program (now complete) | 2015-02-26 | Fully Completed | Gillian Kennedy | 2014-01-03 11:31 | 2014-01-24 11:34 | 2014-01-03 11:31 | 2015-02-27 15:06 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:35 |  |  | 122458 | Completed | 5a | High | Inspection Regime | There are extraction fans/units in this clubroom with the control switches for these extractors located on the wall in the corridor on the secondary exit route. | Can it be confirmed that any maintenance or servicing is being undertaken as per the manufactures requirements on a planned preventive maintenance contract for these extractors including any filters being changed. If it is not then maintenance and/or servicing should be undertaken immediately with any defects etc rectified if any are found. | A & R Contract Management | Alex Bosman |  | COMPLETE - EQUIPMENT PROTECTED BY RCD ON CIRCUIT | 2015-11-17 | Fully Completed | Maria Ares | 2014-01-03 11:35 | 2014-01-24 11:37 | 2014-01-03 11:35 | 2015-11-18 15:31 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:49 |  |  | 122470 | Completed | 23b | High | Emergency Lighting | According to the fire logbook hanging on the wall by the fire alarm panel it appears that the emergency lighting units/system currently installed in this clubroom is not being annually serviced, tested and maintained by the electrical contractors. | Testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | AP confirmed servicing compelte 10.7.2015 | 2015-11-26 | Fully Completed | Maria Ares | 2014-01-03 11:49 | 2014-01-24 11:50 | 2014-01-03 11:49 | 2015-11-27 13:40 | -21 | In target