## Fire Risk Assessment by Team Us
Fire Risk Assessment by Team / User
Total: 481
Risk Assessment | Process Start Date | Prop ref | Block | Process No | Proc Status | Iitem no | Priority | Category | Risk | Action | Team | Who | Action Due Date | Action taken | Comp date | Full or partial | Reporting User | Feedback Start Date | Feedback Due Date | Closure Start Date | Closure Due Date | Date Difference | In Target | Return Stage Startdate | Return Stage Duedate | Return User
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:29 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172141 | Completed | 1b | High | Responsive Item | At the time of this assessment the lighting was not working in the roof level room where the water tanks are located. | I would recommend that the lighting units in this roof level area are repaired or replaced so that they work correctly. | Responsive Repairs | John Tatham | 2016-02-16 | all necessary works completed on 201552556 | 2016-02-16 | Fully Completed | Maria Ares | 2014-12-01 09:29 | 2014-12-22 09:30 | 2014-12-01 09:29 | 2016-02-17 11:02 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:22 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172163 | Completed | 12b | High | Responsive Item | The access door to the external roof from the internal corridor has had both of the "Gerda" locks removed from it, this door is now only secured by a normal latch type lock opened by a door handle. This door is now damaged and does not shut securely. | I would recommend that this door is repaired or replaced and that locks or a device is fitted to this roof door so that it can be secured fully and that the door does not flap in the wind and get damaged. | Responsive Repairs | John Tatham | 2014-12-22 | 201554098 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-01 10:22 | 2014-12-22 10:23 | 2014-12-01 10:22 | 2016-03-07 17:23 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172168 | Completed | 12d | High | Responsive Item | The fire door to the refuse chute room on the 14th floor level grounds and will not shut fully. | I would recommend that this door to the refuse chute room on the 14th floor level is repaired so that is does not ground and that the self closing device shuts the door fully onto its stops. | Responsive Repairs | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-01 10:25 | 2014-12-22 10:27 | 2014-12-01 10:25 | 2016-02-23 20:29 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:28 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172169 | Completed | 12e | High | Responsive Item | The fire door to the staircase from the lift lobby areas on the 2nd and 19th floor levels are damaged and do not shut fully. | I would recommend that these doors are repaired or replaced so that they shut fully. | Responsive Repairs | John Tatham | 2015-01-06 | RD confirm completion | 2016-02-22 | Fully Completed | Janice Wray | 2014-12-01 10:28 | 2014-12-22 10:28 | 2014-12-01 10:28 | 2016-02-23 20:33 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:29 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172170 | Completed | 12f | High | Responsive Item | On the 10th floor level the refuse chute hopper head is damaged - it's handle is missing and it does not shut fully | This hopper head to the rubbish chute on the 10th floor level should be repaired or replaced so that it shuts fully. | Responsive Repairs | John Tatham | 2014-12-22 | 201554019 RD confirm completion | 2016-03-05 | Fully Completed | Janice Wray | 2014-12-01 10:29 | 2014-12-22 10:31 | 2014-12-01 10:29 | 2016-03-07 17:25 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:33 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172174 | Completed | 12h | High | Responsive Item | The door handle of the staircase door (separating lift lobby and staircase) is missing on the staircase side on the 13th floor level. | A new door handle should be fitted to this staircase door. | Responsive Repairs | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-12-01 10:33 | 2014-12-22 10:35 | 2014-12-01 10:33 | 2016-02-02 19:58 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:46 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172180 | Completed | 14b | High | Responsive Item | On the 2nd and the 15th floor levels the panels covering the cable ducts have been removed and not refitted correctly. One is held on with tape. | These covers should be fitted back correctly. . | Responsive Repairs | John Tatham | 2015-12-22 | RD confirm completion | 2016-02-01 | Fully Completed | Janice Wray | 2014-12-01 10:46 | 2014-12-22 10:47 | 2014-12-01 10:46 | 2016-02-02 20:01 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:25 | S217012770010 | GRENFELL WALK | 146388 | Completed | 1 | Medium | Communal Lighting | The covers of some of the lighting units located on the external balconies and staircases of Grenfell Walk are dirty, thus affecting the level of illumination from the bulb of the light unit. | I would recommend that the covers of these lighting units are removed and cleaned or replaced if they cannot be cleaned thoroughly. This will improve the illumination levels of these lights. | Responsive Repairs | Alex Bosman |  | Action Complete - considered information only. FM contract would address future concerns. | 2015-11-17 | Fully Completed | Maria Ares | 2014-06-02 12:25 | 2014-08-01 12:38 | 2014-06-02 12:25 | 2015-11-18 13:50 | -60 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:51 | S217012770010 | GRENFELL WALK | 146397 | Completed | 15a | High | Emergency Lighting | There are emergency lighting system/units installed on the balconies and the staircases of Upper Grenfell Walk. Where these emergency lighting units are installed though the positioning is haphazard. | I would recommend that emergency lighting units installed on the means of escape routes of Upper Grenfell Walk are checked against the requirements of British Standard 5266 Part 1 2011 and then additional units are installed where required. This will including the undertaking of the risk assessment section of the BS first. Once installed the emergency lighting system should be added to the TMO asset register so that servicing and maintenance is undertaken by the electrical contractors on a planned maintenance programme. | Responsive Repairs | Alex Bosman |  | RMA inspection complete confirming current condition. Keystone updated to include block in 16/16 upgrade progra | 2015-12-14 | Fully Completed | Maria Ares | 2014-06-02 12:51 | 2014-06-23 12:54 | 2014-06-02 12:51 | 2015-12-15 11:23 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:54 | S217012770010 | GRENFELL WALK | 146398 | Completed | 15b | High | Emergency Lighting | There appear to be no emergency lighting system/units installed on the balconies and the staircases of Grenfell Walk, but it is hard to tell because the covers of the lights are dirty but the neon charging lights cannot be seen. | I would recommend that light units installed on the means of escape routes of Grenfell Walk are checked to see if they are also emergency lighting units. If they are not then no action is needed to install emergency lighting units but the light cover should be cleaned or replaced. If they are emergency lighting units then they should be tested and checked against the requirements of British Standard 5266 Part 1 2011 including the undertaking of the risk assessment section first. | Responsive Repairs | Alex Bosman |  | COMPLETE - INFORMATION ONLY AS EMERGENCY LIGHT TESTING IS NOT REQUIRED. | 2015-11-17 | Fully Completed | Maria Ares | 2014-06-02 12:54 | 2014-06-23 12:56 | 2014-06-02 12:54 | 2015-11-18 13:51 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:16 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172159 | Completed | 8 | High | Communal Area Storage | On the 19th and 20th floor levels push bikes have been chained to the dry rising main outlets. | The dry rising main outlets must not be obstructed at anytime, these push bikes should not be chained to these outlets and the owners of the push bikes must be told not to do this. | Neighbourhood Management | Siobhan Rumble |  | these have been removed | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 10:16 | 2014-12-22 10:18 | 2014-12-01 10:16 | 2015-03-10 14:54 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:51 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172187 | Completed | 16b | Medium | Signage | The floor number on staircase landing on the 16th floor level has been altered to look like an 18. Floor numbers aid the fire service if there is an incident in this building. | I would recommend that the 16th floor number is altered back to 16 from 18. Opposite the lifts and on each staircase landings of this building where there is a balcony. Seamus or OCS to sort | Neighbourhood Management | Siobhan Rumble |  | all done | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 10:51 | 2015-01-30 10:53 | 2014-12-01 10:51 | 2015-03-10 14:54 | -60 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:19 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172240 | Completed | 23b | High | Miscellaneous | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | these were done by RGE 6 monthly under contract. inspectors check the block lighting to check if all bulbs and emergency lighting are working and records are kept | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:19 | 2014-12-22 12:22 | 2014-12-01 12:19 | 2015-03-10 14:56 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:23 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172242 | Completed | 23c | High | Fire Alarm | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? Including testing the automatic smoke vents | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, including testing the smoke vents with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | being done by rydons | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:23 | 2014-12-22 12:24 | 2014-12-01 12:23 | 2015-03-10 14:57 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172245 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes and these are available for inspection at any time | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:25 | 2014-12-22 12:27 | 2014-12-01 12:25 | 2015-03-10 14:59 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:39 | S217012770015 | GRENFELL WALK 101-111 | 146393 | Completed | 8a | High | Communal Area Storage | There are numerous tubs and pots of shrubs and plants on the 1st floor level balcony of Grenfell Walk, this includes the staircase landing areas at each end of the building. Some of these tubs have small conifer trees in them. | I would recommend some of the tubs and pots of shrubs and plants on the 1st floor level of Grenfell Walk, this includes the staircase landing areas and the balcony outside the flat entrance doors are removed. Some of these tubs and pots can remain but they must not obstruct the dry rising water main outlet or the balcony. Please see item 19 below because the fire service must have a working area around the dry riser outlet valve. If the person responsible for placing the plants etc here on the 1st floor level balconies and staircases landings of Grenfell Walk does not agree with the removal of some of the shrubs and plants etc then I would recommend that all of the plants should be removed and the areas maintained completely clear at all items. | Neighbourhood Management | Janice Jones |  | Letter has been written to tenant stating he needs to remove the plants otherwise he will be re charged for all their removal. Home visit being undertaken by Siobhan Rumble on 04/09. Confrmation plants removed in Nov 2014 | 2013-11-29 | Fully Completed | Janice Jones | 2014-06-02 12:39 | 2014-06-23 12:41 | 2014-06-02 12:39 | 2015-03-12 16:15 | -21 | In target | 2014-06-02 12:39 | 2015-03-18 16:14 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:41 | S217012770015 | GRENFELL WALK 101-111 | 146394 | Completed | 8b | High | Communal Area Storage | There are some pots of plants on the 1st to 2nd floor level staircase of Grenfell Walk by flat 106. | All pots of plants should be removed from this staircase immediately, the staircase should be maintain free of all obstructions so that they can be used without the risk of tripping over pots of plants. | Neighbourhood Management | Janice Jones |  | This work has been completed - plants cleared | 2015-07-03 | Fully Completed | Janice Wray | 2014-06-02 12:41 | 2014-06-23 12:43 | 2014-06-02 12:41 | 2015-07-06 14:28 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:43 | S217012770010 | GRENFELL WALK | 146395 | Completed | 8c | High | Communal Area Storage | There are numerous tubs, pots and other gardening items stored under Grenfell Walk at the garden level. There is also some furniture. Some of these items are placed up against the vents of the underground garages. | I would recommend that this area at the garden level is tidied up and some of the tubs, pots and furniture etc is removed. This will reduce the fire loading of this area. | Neighbourhood Management | Janice Jones |  |  | 2014-10-27 | Fully Completed | Janice Wray | 2014-06-02 12:43 | 2014-06-23 12:44 | 2014-06-02 12:43 | 2015-05-11 09:51 | -21 | In target | 2014-06-02 12:43 | 2014-11-03 14:11 | Janice Jones
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:45 | S217012770010 | GRENFELL WALK | 146396 | Completed | 8d | Information Only | Communal Area Storage | For your infor-mation In contrast to the number of tubs and pots of shrubs and plants on the 1st floor level of Grenfell Walk the 2nd floor is not obstructed and the pots of plants located here do not need to be removed. | No action required | Neighbourhood Management | Janice Jones |  |  | 2014-10-27 | Fully Completed |  |  |  | 2014-06-02 12:45 | 2014-10-28 14:09 |  |  | 2014-06-02 12:45 | 2014-11-03 14:09 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:56 | S217012770015 | GRENFELL WALK 101-111 | 146399 | Completed | 19 | High | Hose Reels | The dry rising main outlet valve located on the 1st floor level of Grenfell Walk is partly obstructed by tubs of plants and shrubs. I believe that the fire service would find it hard the access this dry riser outlet. | Please also see item 8a as the balcony of this building at this floor level is also obstructed by plants and the fire service would find it hard to manoeuvre along this balcony with hose charged from the dry riser outlet. The shrubs and plants obscuring the dry rising main outlet should be removed so that the fire service have a clear working area around this dry riser outlet. Regular checks should be made so that this outlet remains usable at all times and that there is a clear area around the outlet. | Neighbourhood Management | Janice Jones |  |  | 2015-05-08 | Fully Completed | Janice Jones | 2014-06-02 12:56 | 2014-06-23 13:05 | 2014-06-02 12:56 | 2015-05-11 13:38 | -21 | In target | 2014-06-02 12:56 | 2015-05-15 13:37 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:06 | S217012770010 | GRENFELL WALK | 146403 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system of Upper Grenfell Walk and possibly Grenfell Walk being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in these buildings should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | Confirmation from Robert Regan that he is undertaking monthly testing of emergency lighting on Stage 3 at Lanc West. EL on this block not standard so Inspectors to be invited to follow-up training to ensure that they are clear about how to test at this block. | 2014-06-20 | Fully Completed | Siobhan Rumble | 2014-06-02 13:06 | 2014-06-23 13:08 | 2014-06-02 13:06 | 2014-06-23 12:01 | -21 | In target | 2014-06-02 13:06 | 2014-06-27 11:50 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:08 | S217012770010 | GRENFELL WALK | 146406 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing. | Neighbourhood Management | Siobhan Rumble |  | weekly inspections are carried out and all sheest completed. | 2014-06-20 | Fully Completed | Siobhan Rumble | 2014-06-02 13:08 | 2014-06-23 13:10 | 2014-06-02 13:08 | 2014-06-23 11:42 | -21 | In target | 2014-06-02 13:08 | 2014-06-27 11:41 | Janice Wray
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:36 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172176 | Completed | 12i | Information Only | Flat Door | The following flat entrance doors are the original fire rated flat entrance doors and which were fitted with a self closing device. These are flush solid doors and are all close fitting. These flats are numbers 56, 61, 86, 92, 112, 142, 154, 156, 165,166, 174.185, 195, and 206. | If any of these flat entrance doors are replaced in the future then any replacement doors must comply with the requirements of the Building Regulations when installed. For information only - please fully complete | Home Ownership | David Ward |  | None | 2014-12-08 | Fully Completed | David Ward | 2014-12-01 10:36 | 2014-12-22 10:42 | 2014-12-01 10:36 | 2014-12-09 16:27 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172140 | Completed | 1a | High | Electrical Wire Check | According to the contractors label on the main electrical supply/distribution board of this building the next fixed electrical wiring test is due in December of this year. | Can it please be confirmed whether the contractors or the TMO will be responsible for undertaking this buildings fixed electrical wiring test in December 2014? | A & R Contract Management | Alex Bosman |  | INSTALLATION TESTED AND CERT SUPPLIED | 2015-11-17 | Fully Completed | Maria Ares | 2014-12-01 09:25 | 2014-12-22 09:27 | 2014-12-01 09:25 | 2015-11-18 13:48 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:23 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172213 | Completed | 19b | High | Hose Reels | There are fire fighting hose reels in the basement boiler room of this building, these hose reels have not been serviced according to the servicing labels attached to each item since August 2012. I am told that these hose reels are due to be removed as part of the boiler room refurbishment work. | Please can it be confirmed that the fire fighting hose reels in the basement boiler room of this building are being removed as part of the boiler room refurbishment work? If they are not then they should be serviced immediately with any defects found rectified. | A & R Contract Management | Alex Bosman |  | Confirmed fire hose reels will be removed during boiler works | 2015-12-01 | Fully Completed | Maria Ares | 2014-12-01 11:23 | 2014-12-22 11:29 | 2014-12-01 11:23 | 2015-12-02 13:41 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:30 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172214 | Completed | 19c | High | Dry or Wet Riser | The dry rising main in this building is overdue its service according to the last service certificate seen. | The dry rising main in this building should be serviced immediately with any defects found rectified. Is the more recent servicing sheet now available? | A & R Contract Management | Alex Bosman |  | Chub satisfactory test cert held carried out 27.4.2015 | 2015-12-01 | Fully Completed | Maria Ares | 2014-12-01 11:30 | 2014-12-22 11:31 | 2014-12-01 11:30 | 2015-12-02 13:43 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:18 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172239 | Completed | 23a | High | Emergency Lighting | The emergency lighting system installed to cover the common parts of this building appears to be overdue for its annual service, maintenance and discharge test. | I would recommend that the installed emergency lighting system in this building is serviced, tested and a discharge test of the batteries in the units undertaken immediately. Any defects should be rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future annual servicing. | A & R Contract Management | Alex Bosman | 2016-01-21 | AP confirmed service complete 9.12.2015 | 2016-01-21 | Fully Completed | Maria Ares | 2014-12-01 12:18 | 2014-12-22 12:19 | 2014-12-01 12:18 | 2016-01-22 13:02 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:28 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172246 | Completed | 23e | Information Only | Fire Alarm | The fire alarm system installed in this building is due for a test/service and maintenance next month, November 2014. | I would recommend that the fire alarm engineers liaise with the contractors when they undertake the fire alarm system service next month. | A & R Contract Management | Alex Bosman |  | complete - system no longer present | 2015-11-17 | Fully Completed |  |  |  | 2014-12-01 12:28 | 2015-11-18 13:49
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:05 | S217012770016 | GRENFELL WALK 201-211 | 146401 | Completed | 23a | High | Emergency Lighting | The emergency lighting units presently installed on the means of escape routes of Upper Grenfell Walk do not appear on the electrical asset list as supplied by the TMO electrical engineers. Are these installed emergency lighting units being serviced, tested and maintained. | I would recommend that the TMO electrical engineer and the electrical contractor is asked if the installed emergency lighting units in this building is being serviced, tested and maintained. If it is not testing and servicing should be undertaken immediately and any defects etc rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. | A & R Contract Management | Alex Bosman |  | completed 12.08.15 | 2015-11-19 | Fully Completed | Maria Ares | 2014-06-02 13:05 | 2014-06-23 13:06 | 2014-06-02 13:05 | 2015-11-20 12:07 | -21 | In target