## Fire Risk Assessment by Team Us
Fire Risk Assessment by Team / User
Total: 850
Risk Assessment | Process Start Date | Prop ref | Block | Process No | Proc Status | Iitem no | Priority | Category | Risk | Action | Team | Who | Action Due Date | Action taken | Comp date | Full or partial | Reporting User | Feedback Start Date | Feedback Due Date | Closure Start Date | Closure Due Date | Date Difference | In Target | Return Stage Startdate | Return Stage Duedate | Return User
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:08 | S217007970007 | 1 APPLEFORD ROAD 3 4 7 8 10 13-14 | 184117 | Completed | 8a | High | Inspection Regime | In the ground floor level staircase lobby area between flats 8 and 15 there were 2 old televisions, a bedroom units and 8 bikes being stored under the staircase. | I would recommend that all of the storage in this area, apart from the push bikes is removed. If the storage of combustible and household items continues in this area then I would recommend that all items are removed from this area and it is kept completely free of all storage. | Neighbourhood Management | Martin Barr |  | Combustible items have been removed. Only 2 push bikes remain. | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-17 15:08 | 2015-03-10 15:10 | 2015-02-17 15:08 | 2015-06-04 10:46 | -21 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:10 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184119 | Active | 8b | Medium | Miscellaneous | The end window of flat 9 off of the open external balcony has piece of wood/timber over the windows, nailed in to the UPVC window frame. | I would recommend that the occupant of this flat is asked why timber is nailed over the end window? I would recommend that the wood/timber is removed. | Neighbourhood Management | Martin Barr | 2016-01-29 | Joint home visit carried out with the Neighbourhood Offcier Felicia today, tenant was not home. Therefore letter to be hand delivered tomorrow morning advising of what the fire risk assessor has said. It gives the resident until 22/03/2016 to remove the wood/timber. | 2016-03-15 | Partially Completed | Louise Nezandonyi | 2015-02-17 15:10 | 2015-04-18 15:12 | 2015-02-17 15:10 | 2016-03-16 17:06 | -60 | In target | 2015-02-17 15:10 | 2016-03-25 11:53 | Janice Wray
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:13 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184121 | Active | 8c | Medium | Communal Area Storage | On the open external balcony outside of flat 9 there is aCC | I would recommend that all of the old and damaged items | Neighbourhood Management | Martin Barr | 2016-01-29 | Joint home visit carried out with the Neighbourhood Offcier Felicia today, tenant was not home. Therefore letter to be hand delivered tomorrow morning advising of what the fire risk assessor has said. It gives the resident until 22/03/2016 to remove the items. | 2016-03-15 | Partially Completed | Louise Nezandonyi | 2015-02-17 15:13 | 2015-04-18 15:15 | 2015-02-17 15:13 | 2016-03-16 17:09 | -60 | In target | 2015-02-17 15:13 | 2016-03-25 11:53 | Janice Wray
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:15 | S217007970007 | 1 APPLEFORD ROAD 3 4 7 8 10 13-14 | 184124 | Completed | 8d | Medium | Communal Area Storage | On the open external balcony outside of flat 10 there were 6 bags of old plastic bottles and some cardboard boxes. | I would recommend that all of these items are removed from this balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | Items have been removed. | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-17 15:15 | 2015-04-18 15:16 | 2015-02-17 15:15 | 2015-06-04 10:47 | -60 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:17 | S217007970007 | 1 APPLEFORD ROAD 3 4 7 8 10 13-14 | 184127 | Completed | 10 | High | Communal Area Storage | On the external balcony outside flats number 14 and 18 there are charcoal BBQ's, it is not known if the occupants of these flats use these BBQ;s on the balconies, but this is a high fire risk item and a fire hazard. I believe that cooking on a BBQ on a flat balcony is not allowed under the tenancy agreement. | I would recommend that these charcoal BBQ's are removed from these balcony areas outside of these two flats immediately. | Neighbourhood Management | Martin Barr |  | Residents have confirmed removal of items | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-17 15:17 | 2015-03-10 15:18 | 2015-02-17 15:17 | 2015-06-04 10:48 | -21 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:19 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184128 | Completed | 11 | High | Inspection Regime | Pigeon netting has been very badly erected to cover the open external balcony area outside of flat 9. This pigeon netting is partly obstructing the entrance to the balcony from the staircase, it is like the netting was trying to be a screen separating the balcony from the staircase. Do the TMO know that this pigeon netting has been erected? | I would recommend that this pigeon netting is completely removed as it is very badly hung and fixed. If there is a requirement for pigeon netting to cover this open balcony area then is must be securely fixed/fitted and not obstruct the entrance to the balcony. | Neighbourhood Management | Martin Barr |  | This netting has been removed | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-17 15:19 | 2015-03-10 15:20 | 2015-02-17 15:19 | 2015-06-04 10:49 | -21 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:25 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184138 | Completed | 23a | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-17 15:25 | 2015-03-10 15:26 | 2015-02-17 15:25 | 2015-05-19 11:37 | -21 | In target
1 APPLEFORD ROAD - 2015.02.06 | 2015-02-17 15:28 | S217007970005 | 1 APPLEFORD ROAD 1 2 5 6 9 11-12 | 184141 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-17 15:28 | 2015-03-10 15:29 | 2015-02-17 15:28 | 2015-05-19 11:38 | -21 | In target
1 BURNABY STREET - 2013.12.31 | 2013-12-31 13:50 | S217000510001 | BURNABY STREET (1) | 122142 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time | Neighbourhood Management | Wendy Stevenson |  | Keys being pursued as part of initiative with Home Ownership Team and A & R. | 2014-03-17 | Fully Completed | Wendy Stevenson | 2013-12-31 13:50 | 2014-06-29 13:53 | 2013-12-31 13:50 | 2014-03-18 13:58 | -180 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 10:09 | S217007560001 | PEMBRIDGE SQUARE (1) | 136571 | Completed | 8 | High | Communal Area Storage | There is an under floor level cupboard accessed from the first floor level landing, in this area there are cardboard boxes with old light fittings in them. Also an old vacuum cleaner plus a few other items. | I would recommend that all of these items are removed from this under floor area. | Neighbourhood Management | Martin Barr |  | Items have been cleared - job 201404101 | 2014-05-08 | Fully Completed | Martin Barr | 2014-03-26 10:09 | 2014-04-16 10:10 | 2014-03-26 10:09 | 2014-05-12 07:07 | -21 | In target | 2014-03-26 10:09 | 2014-05-16 07:06 | Janice Wray
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 11:02 | S217007560001 | PEMBRIDGE SQUARE (1) | 136595 | Completed | 16 | High | Miscellaneous | There is an escape exit sign displayed by the roof access hatch on the 3rd floor level stating "Roof Escape" indicating that the residents are expected to climb up on to the external flat roof of this building, which has no edge protection. Over the roof escape routes are not a recognised means of escape. | This "Roof Escape" sign should be removed as there is not a suitable over the roof means of escape route. This building has a protected staircase which is a sterile area for residents to use as a means of escape route. Could the ESA remove this? | Neighbourhood Management | Martin Barr |  | The sign has been removed. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 11:02 | 2014-04-16 11:08 | 2014-03-26 11:02 | 2014-04-28 16:10 | -21 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 11:09 | S217007560001 | PEMBRIDGE SQUARE (1) | 136598 | Completed | 17 | Low | Fire Alarm | It is not known if domestic BS 5839 Part 6 fire alarm detectors/sounders are fitted within all the flats of this building, a battery operated device is fitted within flat 5. This was by the LFB, but no domestic detection was not fitted in flat 6. | I have left copies of the LFB leaflet on fitting domestic fire alarm detectors/sounders in this building. I would recommend that the caretaker is also instructed to put a copy of the LFB leaflet in each flats letter box. The residents can then contact the LFB to arrange a home fire safety visit and have domestic detectors/sounders fitted by the LFB if required. | Neighbourhood Management | Martin Barr |  | Leaflets have been dropped to individual letter boxes on the 25th April | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 11:09 | 2014-09-22 11:11 | 2014-03-26 11:09 | 2014-04-28 16:11 | -180 | In target
1 PEMBRIDGE SQUARE- 2014.2.28 | 2014-03-26 11:13 | S217007560001 | PEMBRIDGE SQUARE (1) | 136602 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment, lifts emergency lighting etc and the other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr | 2014-06-12 | ESA confirms monthly emergency lighting check are undertaken and recorded on PDA | 2016-07-12 | Fully Completed | Janice Wray | 2014-03-26 11:13 | 2014-04-16 11:14 | 2014-03-26 11:13 | 2016-07-13 11:36 | -21 | In target
1 ST HELENS GARDENS - 2014.03.06 | 2014-03-13 13:23 | S217010100001 | ST HELENS GARDENS (1) | 134456 | Completed |  | Information Only | Inspection Regime | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Martin Barr |  | Noted. We are compiling a list of these properties before deciding on lock changes. | 2014-04-17 | Fully Completed |  |  |  | 2014-03-13 13:23 | 2014-04-22 08:21
1 SWINBROOK ROAD, LONDON W10 5GJ - 2016.01.05 | 2016-02-17 17:15 | S217010300001 | SWINBROOK ROAD (1) | 244149 | Active | 8 | High | Miscellaneous | There is presently a set of metal step ladders on the half landing area plus some decorating items, dust sheets etc. | I would recommend that the set of metal step ladders on the half landing area are removed in case they fall over and block the staircase. Alternatively if the step ladders were secured to the wall then it could remain in situ. The combustible decorating materials should be removed. | Neighbourhood Management | Louise Nezandonyi | 2016-03-16 |  |  |  | Cyril Morris | 2016-02-17 17:15 | 2016-03-09 17:17 |  |  | 365 | 365 days overdue
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 12:06 | S217007860001 | GOLBORNE GARDENS 1-10 | 182831 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-10 12:06 | 2015-03-03 12:12 | 2015-02-10 12:06 | 2015-05-19 11:39 | -21 | In target
1 TO 10 GOLBORNE GARDENS -2015.02.05 | 2015-02-10 12:14 | S217007860001 | GOLBORNE GARDENS 1-10 | 182835 | Completed | 23d | Medium | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-10 12:14 | 2015-04-11 12:15 | 2015-02-10 12:14 | 2015-05-19 11:40 | -60 | In target
10 ASHBURNHAM ROAD - 2013.09.30 | 2013-10-10 15:32 | S217000190004 | ASHBURNHAM ROAD (10) | 110152 | Completed |  | Low | Miscellaneous | The caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson |  | Keys being pursued as part of initiative with Home Ownership Team and A & R. | 2014-03-17 | Fully Completed | Wendy Stevenson | 2013-10-10 15:32 | 2014-04-08 15:33 | 2013-10-10 15:32 | 2014-03-18 13:58 | -180 | In target
10 ASHBURNHAM ROAD - 2013.09.30 | 2013-10-10 15:37 | S217000190004 | ASHBURNHAM ROAD (10) | 110161 | Completed | 8 | Low | Communal Area Storage | There is an old washing machine at the lower ground floor level at the front of the building outside flat A's entrance door. | I would recommend that this washing machine is removed if it is not needed any more. If the occupant wants this washing machine I would recommend that it is moved away from the base of the steps down to the flats entrance door. | Neighbourhood Management | Wendy Stevenson |  | Washing machine has been removed by occupants. | 2014-03-17 | Fully Completed | Wendy Stevenson | 2013-10-10 15:37 | 2014-04-08 15:38 | 2013-10-10 15:37 | 2014-03-18 12:20 | -180 | In target
10 STADIUM STREET, LONDON SW10 0PU - 2016.05.03 | 2016-05-23 14:57 | S217005190010 | STADIUM STREET (10) | 261961 | Completed | 8 | High | Inspection Regime | There are piles of cardboard boxes located on the staircase half landing between flat 2 and 3. | These boxes should be removed from this staircase half landing, the residents of this building should be reminded that there should be no combustible storage in the protected staircase enclosure. | Neighbourhood Management | Nicola Rees | 2016-06-13 | Email sent to Darrren 02.06.16. This was removed and door knock completed. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-05-23 14:57 | 2016-06-13 14:59 | 2016-05-23 14:57 | 2017-01-16 09:29 | -21 | In target
103 GOLBORNE ROAD, LONDON W10 5NL - 2016.01/07 | 2016-02-16 12:37 | S217008770008 | GOLBORNE ROAD (103) | 243763 | Active | 8 | High | Communal Area Storage | On the staircase half landing there are items of furniture, black bags of clothes etc, these items could provide fuel for a fire and they are increasing the fire loading in the staircase enclosure. | There items of furniture and the black bags should be removed from the staircase half landing. The resident who owns them should be reminder that the staircase should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading of the staircase is kept as low as possible. The push bike in the entrance hall area can remain in that location. | Neighbourhood Management | Louise Nezandonyi | 2016-03-15 |  |  |  | Cyril Morris | 2016-02-16 12:37 | 2016-03-08 12:38 |  |  | 366 | 366 days overdue
105 GOLBORNE ROAD, LONDON W10 5NL - 2016.02.24 | 2016-04-04 16:11 | S217008770009 | GOLBORNE ROAD (105) | 252409 | Completed | 0 | Information Only | Inspection Regime | At the time of this assessment it appeared that the intercom system for visitors to the dwellings of this building was not working. | I would recommend that the flats intercom system is checked and repaired or replaced if necessary so that it is full working order. Could the ESA check please | Neighbourhood Management | Louise Nezandonyi | 2016-05-09 | Rob has checked this and the intercom system was in good working order. | 2016-11-03 | Fully Completed |  |  |  | 2016-04-04 16:11 | 2016-11-07 09:11
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 08:57 | S217009620003 | OXFORD GARDENS (109A) | 197390 | Completed | 8a | High | Inspection Regime | There is a double mattress, pieces of a bed, a 3 piece suite, settee and 2 chairs plus some other household items in the front garden area of 109A. | I would recommend that these items are removed from this area. | Neighbourhood Management | Martin Barr |  | Bulk waste clearances have been raised to remove these items | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-16 08:57 | 2015-06-06 08:59 | 2015-05-16 08:57 | 2015-09-21 14:44 | -21 | In target
109 & 109A OXFORD GARDENS - 2015.05.06 | 2015-05-16 08:59 | S217009620002 | OXFORD GARDENS (109) | 197391 | Completed | 8b | Medium | Communal Area Storage | In the attic area there are some cardboard boxes, bags of clothes and old plastic wrapping. | I would recommend that these items are removed from this area. | Neighbourhood Management | Martin Barr |  | Bulk waste clearance has been ordered to remove these items | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-16 08:59 | 2015-07-15 09:00 | 2015-05-16 08:59 | 2015-09-21 14:45 | -60 | In target
11 AND 12 COLVILLE SQUARE, LONDON W11 2BD - 2016.02.02 | 2016-05-19 09:43 | S217008450002 | COLVILLE SQUARE (11) | 261337 | Active | 8 | Medium | Inspection Regime | At the lower ground floor level in each of the open external areas at the front of the building there is an old storage area located under the public footpath. These were securely boarded up but this boarding has been removed from each area. | I would recommend that the boarding which previously securely covered these two under pavement areas is re-fixed back to stop persons accessing these two areas. Could ESA investigate & order any necessary work | Neighbourhood Management | Louise Nezandonyi | 2016-08-12
11 CREMORNE ROAD, LONDON SW10 ONA - 2016.05.19 | 2016-06-06 16:04 | S217001300001 | CREMORNE ROAD (11) | 264038 | Active | 13 | High | Communal Area Storage | There is a mobility scooter located in the entrance hall area of this building, this scooter was not causing an obstruction and was not being charged at the time of this assessment. It is not known if the TMO have given approval for this mobility scooter to be parked at this location within the communal areas. There is a ramp at the front of this building so I am assuming that the owner of the mobility scooter lives in this building - although it could belong to a visitor? | The TMO's policy is that residents make an application to store a mobility scooter and it will be assessed. (Charging will not be permitted in communal areas.) Has a resident at this block made an application to store a scooter here? Is it known for definite that the owner of this mobility scooter lives in this building or if the scooter's batteries are being charged in this area? If the owner of this mobility scooter lives in this building I would recommend that the owner is asked how and where their scooter is being charged? The charging of the batteries of mobility scooters should not be undertaken on/within the common parts of residential buildings. | Neighbourhood Management | Nicola Rees | 2016-07-05 | [REDACTED] Email sent to the Neighbourhood team and also Aids and Adaptations to see if there is any potenital alternative. Louie Ann has diairised to attend and look at alternatives in March when resident is available. |  | Partially Completed | Nicola Rees | 2016-06-06 16:04 | 2016-06-27 16:06 | 2016-06-06 16:04 | 2017-01-18 09:56 | -21 | In target
110 LANCASTER ROAD - 2014.01.09 | 2014-01-09 14:45 | S217009210004 | LANCASTER ROAD (110) | 123453 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Martin Barr |  | Noted. We are compiling a list of these properties before deciding on lock changes. | 2014-04-17 | Fully Completed |  |  |  | 2014-01-09 14:45 | 2014-04-22 08:19
110 LANCASTER ROAD - 2014.01.09 | 2014-01-09 14:52 | S217009210004 | LANCASTER ROAD (110) | 123457 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | At present no. ESA does not have key to MED. Also this is deemed as a street property which would only be visited quarterly. | 2014-04-17 | Fully Completed | Martin Barr | 2014-01-09 14:52 | 2014-03-10 14:53 | 2014-01-09 14:52 | 2014-04-22 08:26 | -60 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 10:57 | S217009467707 | MORGAN ROAD ODD (1-11) | 102422 | Completed | 8 | Medium | Communal Area Storage | In the electrical room there are empty cardboard boxes and cardboard boxes with old light fittings in them. | I would recommend that all these cardboard boxes and old light fitting are removed from this electrical room. | Neighbourhood Management | Martin Barr | 2013-09-16 | Order raised to clear the electrical cupboard. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 10:57 | 2013-10-18 10:58 | 2013-08-19 10:57 | 2013-11-08 14:53 | -60 | In target
1-11 (ODD) MORGAN ROAD - 2013.02.01 | 2013-08-19 12:07 | S217009467707 | MORGAN ROAD ODD (1-11) | 102449 | Completed | 23a | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr | 2013-09-16 | What is the frrequency of the ESA inspections? ESAs check smaller street properties on a quarterly basis with Neighbourhood Officers. We may need to look into the H&S checks that need to be carried out on street properties as part of the mobile working project for ESAs. A separate form could be developed for basic quarterly H&S checks. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 12:07 | 2013-10-18 12:09 | 2013-08-19 12:07 | 2013-11-08 15:00 | -60 | In target
1-11 MORGAN ROAD, (ODD NUMBERS ONLY) LONDON W10 5YT - 2016.03.04 | 2016-03-21 12:37 | S217009467707 | MORGAN ROAD ODD (1-11) | 250147 | Active | 8 | Medium | Communal Area Storage | In the electrical room there are empty cardboard boxes and cardboard boxes with old light fittings in them. | I would recommend that all these cardboard boxes and old light fitting are removed from this electrical room. | Neighbourhood Management | Louise Nezandonyi | 2016-06-20 |  |  |  | Cyril Morris | 2016-03-21 12:37 | 2016-05-20 12:39 |  |  | 293 | 293 days overdue
1-11 MORGAN ROAD, (ODD NUMBERS ONLY) LONDON W10 5YT - 2016.03.04 | 2016-03-21 15:32 | S217009467707 | MORGAN ROAD ODD (1-11) | 250267 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Louise Nezandonyi | 2016-04-18 | Monthly occupier tests of the emergency lighting is carried out and recorded on Insight | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-03-21 15:32 | 2016-04-11 15:39 | 2016-03-21 15:32 | 2016-04-06 17:31 | -21 | In target
1-11 MORGAN ROAD, (ODD NUMBERS ONLY) LONDON W10 5YT - 2016.03.04 | 2016-03-21 15:39 | S217009467707 | MORGAN ROAD ODD (1-11) | 250277 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Louise Nezandonyi | 2016-04-18 | Yes this canbe confirmed and all records are kept on Insightt | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-03-21 15:39 | 2016-04-11 15:40 | 2016-03-21 15:39 | 2016-04-06 17:29 | -21 | In target
11-18 GOLBORNE GARDENS - 2015.02.05 | 2015-02-10 12:28 | S217008850002 | GOLBORNE GARDENS 11-18 | 182842 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-10 12:28 | 2015-03-03 12:29 | 2015-02-10 12:28 | 2015-05-19 11:43 | -21 | In target
11-18 GOLBORNE GARDENS - 2015.02.05 | 2015-02-10 12:30 | S217008850002 | GOLBORNE GARDENS 11-18 | 182844 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-10 12:30 | 2015-04-11 12:31 | 2015-02-10 12:30 | 2015-05-19 11:43 | -60 | In target
1-17 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:12 | S217010500001 | WAYNFLETE SQUARE 2-11 | 215971 | Completed | 2 | Medium | Inspection Regime | There is not a "No Smoking" sign displayed in the staircase of flats 5 to 11. | I would recommend that a "No Smoking" sign is displayed in the entrance hall area of this staircase. | Neighbourhood Management | Martin Barr |  | Sign has been put up on display | 2015-09-24 | Fully Completed | Martin Barr | 2015-09-10 15:12 | 2015-11-09 15:16 | 2015-09-10 15:12 | 2015-09-25 11:28 | -60 | In target
1-17 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:25 | S217010500001 | WAYNFLETE SQUARE 2-11 | 215980 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 15:25 | 2015-10-01 15:26 | 2015-09-10 15:25 | 2015-09-17 10:48 | -21 | In target
1-17 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:27 | S217010500001 | WAYNFLETE SQUARE 2-11 | 215983 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 15:27 | 2015-10-01 15:28 | 2015-09-10 15:27 | 2015-09-17 10:48 | -21 | In target
1-18 BURLEIGH HOUSE - 2015.05.06 | 2015-05-12 10:18 | S217010080009 | BURLEIGH HOUSE 1-18 | 196495 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-12 10:18 | 2015-06-02 10:19 | 2015-05-12 10:18 | 2015-05-19 11:45 | -21 | In target
118 CAMBRIDGE GARDENS, LONDON W10 6HU - 2016.04.26 | 2016-05-26 14:15 | S217008280003 | CAMBRIDGE GARDENS (118) | 262701 | Active | 9 | High | Communal Area Storage | On the 2nd floor level flat/lift landing area there are household items of furniture. | I would recommend that all the household furniture is removed from this flat/lift landing area. These items are a fuel source for a fire and these landing areas should be maintained free from combustible storage. | Neighbourhood Management | Louise Nezandonyi | 2016-06-16 |  |  |  | Cyril Morris | 2016-05-26 14:15 | 2016-06-16 14:16 |  |  | 266 | 266 days overdue
118 CAMBRIDGE GARDENS, LONDON W10 6HU - 2016.04.26 | 2016-05-26 14:26 | S217008280003 | CAMBRIDGE GARDENS (118) | 262706 | Active | 12b | High | Inspection Regime | At the 2nd floor level the doors which go into the 2 roof space areas have padlocks on them, these are not FB padlocks. | Does the caretaker have access to the keys to these padlocks or are these private storage areas? If they are private areas no action is needed. | Neighbourhood Management | Louise Nezandonyi | 2016-06-16 |  |  |  | Cyril Morris | 2016-05-26 14:26 | 2016-06-16 14:27 |  |  | 266 | 266 days overdue
1-18 DARTREY WALK - 2014.3.12 | 2014-04-10 15:41 | S217012740004 | DARTREY WALK 1-18 | 139373 | Completed | 23 | Information Only | Inspection Regime | The monthly occupier tests and inspections of the dry risers, the external staircases, the lifts and the emergency lighting units. | I have assumed that the monthly occupiers testing and inspections of these items are being undertaken as per the caretaker's checklist and recorded under the tower blocks. This is because this is where these items are located. | Neighbourhood Management | Wendy Stevenson |  |  | 2014-06-17 | Fully Completed |  |  |  | 2014-04-10 15:41 | 2014-06-19 12:31 |  |  | 2014-04-10 15:41 | 2014-06-25 12:31 | Janice Wray
1-18 DARTREY WALK - 2014.3.12 | 2014-04-10 16:02 | S217012740004 | DARTREY WALK 1-18 | 139385 | Completed | 23 | Information Only | Inspection Regime | The monthly occupier tests and inspections of the dry risers, the external staircases, the lifts and the emergency lighting units. | I have assumed that the monthly occupiers testing and inspections of these items are being undertaken as per the caretaker's checklist and recorded under the tower blocks. This is because this is where these items are located. | Neighbourhood Management | Wendy Stevenson |  |  | 2014-06-17 | Fully Completed |  |  |  | 2014-04-10 16:02 | 2014-06-19 12:30 |  |  | 2014-04-10 16:02 | 2014-06-25 12:29 | Janice Wray
123 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:39 | S217002110005 | FINBOROUGH ROAD 123 A-H | 194205 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Kamran Hye |  | John Whall confirms testign & inspection in palce & recorded on PDA | 2015-10-09 | Fully Completed | Janice Wray | 2015-04-27 09:39 | 2015-05-18 09:40 | 2015-04-27 09:39 | 2015-10-12 13:06 | -21 | In target
123 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 09:40 | S217002110005 | FINBOROUGH ROAD 123 A-H | 194206 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | JOhn Whall confirms inspections | 2015-10-09 | Fully Completed | Janice Wray | 2015-04-27 09:40 | 2015-06-26 09:41 | 2015-04-27 09:40 | 2015-10-12 13:07 | -60 | In target
1-26 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 08:56 | S217000830003 | CHELSEA MANOR COURT 1-26 | 207289 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | Fleix (ESA) confirms month;y check in place, recorded on PDA (extinguishers are overdue servicing) | 2015-09-30 | Fully Completed | Janice Wray | 2015-07-17 08:56 | 2015-08-07 08:57 | 2015-07-17 08:56 | 2015-10-01 11:45 | -21 | In target
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:50 | S217012740001 | BERENGER WALK 1-28 | 139350 | Active | 16 | High | Signage | At present some of the signs near the entrances to the walkways are missing or damaged. These signs indicate the walkway name and flat numbers on that walkway this information could aid the emergency services. | I would recommend that a check is carried out to see which signs are missing or damaged and then new signs are provided. These new signs should be permanently fixed to the walls similar to the existing ones, they should be in the same size font as the existing signs and positioned at the entrance to the walkways from the staircase/lift enclosures. | Neighbourhood Management | Wendy Stevenson |  | This was referred back to John Griffin who was thought to have picked this up from Donal. | 2014-04-22 | Partially Completed | Janice Wray | 2014-04-10 14:50 | 2014-05-01 14:51 | 2014-04-10 14:50 | 2014-05-14 15:09 | -21 | In target
1-28 BERENGER WALK - 2014.3.12 | 2014-04-10 14:52 | S217012740001 | BERENGER WALK 1-28 | 139352 | Completed | 23 | Information Only | Inspection Regime | The monthly occupier tests and inspections of the dry risers, the external staircases, the lifts and the emergency lighting units. | I have assumed that the monthly occupiers testing and inspections of these items are being undertaken as per the caretaker's checklist and recorded under the tower blocks. This is because this is where these items are located. | Neighbourhood Management | Wendy Stevenson |  | Confirmed. | 2014-04-10 | Fully Completed |  |  |  | 2014-04-10 14:52 | 2014-04-11 15:54
13 BURNABY STREET - 2013.12.31 | 2013-12-31 14:23 | S217000510003 | BURNABY STREET (13) | 122156 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson | 2014-06-29 |  | 2014-01-10 | Fully Completed |  |  |  | 2013-12-31 14:23 | 2014-01-13 12:10
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:23 | S217009210005 | LANCASTER ROAD (130) | 102667 | Completed | 3 | Medium | Miscellaneous | The rear garden area was over grown with vegetation and a bush is growing out of the wall of the building by the TV cable box. | I would recommend that the over grown vegetation in the rear garden area is cut down along with the bush growing out of the wall by the TV box in the front garden. | Neighbourhood Management | Dominic Davies |  | Garden cleared | 2014-03-14 | Fully Completed | Dominic Davies | 2013-08-19 16:23 | 2013-10-18 16:25 | 2013-08-19 16:23 | 2014-04-07 11:18 | -60 | In target
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:34 | S217009210005 | LANCASTER ROAD (130) | 102676 | Completed | 17 | High | Fire Alarm | There are no TMO employees in this building only residents and this building is fitted with a full fire alarm detection and warning system. I | would recommend that the fire alarm system in this building is connected to a monitoring stationed/service so in the event of an activation of the fire alarm system the fire service or an on duty caretaker is informed. | Neighbourhood Management | Susan Anim-Boadu | 2013-08-30 | Susan, can you please liaise with CAS re monitoring service I have sent an email to Kevin in Cas to connect it to the cas system. To investigate with new CAS Manager | 2016-02-16 | Fully Completed | Susan Anim-Boadu | 2013-08-19 16:34 | 2013-09-09 16:36 | 2013-08-19 16:34 | 2016-02-17 20:35 | -21 | In target | 2013-08-19 16:34 | 2016-02-23 20:30 | Janice Wray
130 LANCASTER ROAD-2013.06.13 | 2013-08-19 16:42 | S217009210005 | LANCASTER ROAD (130) | 102684 | Completed | 23d | High | Fire Alarm | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Susan Anim-Boadu |  | The fire alarm testing is done on a monthly basis. | 2013-08-19 | Fully Completed | Susan Anim-Boadu | 2013-08-19 16:42 | 2013-09-09 16:43 | 2013-08-19 16:42 | 2014-01-08 14:03 | -21 | In target | 2013-08-19 16:42 | 2014-01-14 14:02 | Janice Wray
14 COLVILLE SQUARE 2014.02.06 | 2014-03-07 10:43 | S217008450003 | COLVILLE SQUARE (14) | 133523 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting units and other building structural items are being undertaken as per the caretaker's checklist. With the results recorded as proof of testing and checks having been undertaken. | Neighbourhood Management | Martin Barr |  | Training on lighting testing due 23rd April. Checks will take place after this and once list of locations provided by A&R team. Block checks are completed and records kept. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 10:43 | 2014-03-28 10:44 | 2014-03-07 10:43 | 2014-04-22 08:32 | -21 | In target
140 LEXHAM GARDENS, LONDON W8 6JE - 2016.03.23 | 2016-04-29 10:50 | S217012040001 | LEXHAM GARDENS (140) | 257476 | Active | 8b | Medium | Inspection Regime | No access could be gained to the high level cupboard located above the 1st to 2nd floor half landing area. | I would recommend that the caretaker is asked to undertake a check of this cupboard to see what is in it if anything. | Neighbourhood Management | Nicola Rees | 2016-07-29 | Email sent to John to advise 06.09.16 |  |  | Cyril Morris | 2016-04-29 10:50 | 2016-06-28 10:53 |  |  | 254 | 254 days overdue
140 LEXHAM GARDENS, LONDON W8 6JE - 2016.03.23 | 2016-04-29 10:53 | S217012040001 | LEXHAM GARDENS (140) | 257480 | Completed | 8c | Medium | Communal Area Storage | No access could be gained to the small cupboard located on the 2nd floor landing area. | It is assumed that this is a resident's storage cupboard, if it is not I would recommend that the caretaker is asked to undertake a check of this cupboard to see what is in it if anything. | Neighbourhood Management | Nicola Rees | 2016-07-29 | This is residents storage cupbaord- reported by John as belonging to flat 5. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-04-29 10:53 | 2016-06-28 10:57 | 2016-04-29 10:53 | 2017-01-16 09:28 | -60 | In target
140 LEXHAM GARDENS, LONDON W8 6JE - 2016.03.23 | 2016-04-29 11:23 | S217012040001 | LEXHAM GARDENS (140) | 257502 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-05-31 | Yes this is being completed. | 2016-06-02 | Fully Completed | Nicola Rees | 2016-04-29 11:23 | 2016-05-20 11:25 | 2016-04-29 11:23 | 2016-06-03 12:51 | -21 | In target
140 LEXHAM GARDENS, LONDON W8 6JE - 2016.03.23 | 2016-04-29 11:26 | S217012040001 | LEXHAM GARDENS (140) | 257504 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-05-31 | Yes this is being completed. | 2016-06-02 | Fully Completed | Nicola Rees | 2016-04-29 11:26 | 2016-05-20 11:27 | 2016-04-29 11:26 | 2016-06-03 12:50 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:43 | S217012040001 | LEXHAM GARDENS (140) | 102515 | Completed | 8a | High | Inspection Regime | In the entrance hall area there is a television stand and a wall unit both with books and magazines piled up on them. | These items should be removed immediately from this entrance hall area and it kept free of storage so that the hallway does not become obstructed. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All items removed - ESA John Whall. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 13:43 | 2013-09-09 13:44 | 2013-08-19 13:43 | 2013-09-09 11:22 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:45 | S217012040001 | LEXHAM GARDENS (140) | 102520 | Completed | 8b | High | Communal Area Storage | The 1st to 2nd floor level half landing alcove area has soft chairs, a roll of carpet and a lot of pictures in frames in it. | I would recommend that these items are removed from this alcove area/landing and this area kept free of storage. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All items removed. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 13:45 | 2013-09-09 13:50 | 2013-08-19 13:45 | 2013-09-09 11:23 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:51 | S217012040001 | LEXHAM GARDENS (140) | 102525 | Completed | 8c | High | Communal Area Storage | The basement level large room which has the flats gas meters in it also has a lot of household furniture stored in it, tins of old paint, old televisions etc. | I would recommend that this area is completely tided up and all unwanted or damaged items are removed. The flats gas meters are located within this room and should not be obstructed. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All items removed via ESA. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 13:51 | 2013-09-09 13:52 | 2013-08-19 13:51 | 2013-09-09 11:24 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:52 | S217012040001 | LEXHAM GARDENS (140) | 102527 | Completed | 8d | High | Communal Area Storage | The basement level electrical cupboard has two suitcases stored in it as well as some cardboard boxes. | I would recommend that these items are removed from this electrical cupboard immediately and that this cupboard is kept total free of all storage. | Neighbourhood Management | Wendy Stevenson | 2013-09-06 | All items removed. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 13:52 | 2013-09-09 13:53 | 2013-08-19 13:52 | 2013-09-09 11:25 | -21 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:57 | S217012040001 | LEXHAM GARDENS (140) | 102536 | Completed | 8f | Medium | Communal Area Storage | The external letter boxes fixed to the wall outside the building's entrance door had the letter openings jammed with free leaflets and advertising letters etc and three old empty pizza boxes on top of one column of letter boxes. | I would recommend that the letter boxes are emptied out and all the junk mail etc removed of along with the pizza boxes. | Neighbourhood Management | Wendy Stevenson | 2013-10-18 | All the letter boxes are now fully removed, preventing any future build-up of junk mail. | 2013-10-17 | Fully Completed | Wendy Stevenson | 2013-08-19 13:57 | 2013-10-18 13:57 | 2013-08-19 13:57 | 2013-10-18 16:15 | -60 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 13:58 | S217012040001 | LEXHAM GARDENS (140) | 102539 | Completed | 8g | Medium | Communal Area Storage | The ground floor level under stairs cupboard had a lot of storage in it which was untidy and just pushed in. There is an electrical socket in this cupboard. | I would recommend that all the items are removed from the under stairs cupboard and it is given a good tidy out. | Neighbourhood Management | Wendy Stevenson | 2013-10-28 | Storage area is used by contract cleaners, cleared Friday 18th October. | 2013-10-18 | Fully Completed | Wendy Stevenson | 2013-08-19 13:58 | 2013-10-18 13:59 | 2013-08-19 13:58 | 2013-10-22 11:16 | -60 | In target | 2013-08-19 13:58 | 2013-10-28 09:11 | Wendy Stevenson
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 14:00 | S217012040001 | LEXHAM GARDENS (140) | 102540 | Completed | 8h | Low | Communal Area Storage | No access could be gained to the high level cupboard located above the 1st to 2nd floor half landing area. | I would recommend that the caretaker is asked to undertake a check of this cupboard to see what is in it if anything. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | Cupboard is inaccessible and locked shut, above a stairwell, not flush with the floor. ESA will be asked to arrange a forced entry and re-secure. Update 24th Oct 2013 - cupboard belongs to Flat 7, resident not available for access. ESA will approach and request access. Update 17th Jan 2014 - cupboard contains wooden chairs not belonging to the tenant. The ESA will remove once an adequate ladder is available (error made by RD about which ladder to remove). | 2014-09-30 | Fully Completed | Wendy Stevenson | 2013-08-19 14:00 | 2014-02-15 14:13 | 2013-08-19 14:00 | 2014-10-01 09:57 | -180 | In target | 2013-08-19 14:00 | 2014-10-07 09:56 | Janice Wray
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 14:14 | S217012040001 | LEXHAM GARDENS (140) | 102553 | Completed | 8i | Low | Communal Area Storage | No access could be gained to the small cupboard located on the 2nd floor landing area. | It is assumed that this is a resident's storage cupboard, if it is not I would recommend that the caretaker is asked to undertake a check of this cupboard to see what is in it if anything. | Neighbourhood Management | Wendy Stevenson | 2013-10-18 | Cupboard belongs to Flat 7 - private storage. | 2013-10-17 | Fully Completed | Wendy Stevenson | 2013-08-19 14:14 | 2014-02-15 14:15 | 2013-08-19 14:14 | 2013-10-18 16:27 | -180 | In target
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 14:28 | S217012040001 | LEXHAM GARDENS (140) | 102565 | Completed | 12b | Information Only | Miscellaneous | There is presently an over the roof or stay on the roof means of escape policy for the residents of this building. This is via a pull down fixed ladder over the second to third floor level landing which allows access to the open external roof of this building via a velux type window. | I would recommend that the pull down ladder is removed so that the residents cannot access the open roof area of this building. That is unless the over the roof or stay on the roof escape policy is kept for the residents of this building. | Neighbourhood Management | Olivia Hutchison | 2013-09-12 | Health and Safety will write to residents re change in policy once the ladder and signage has been removed. Ladder cannot be removed by ESA as it is fixed to the ceiling structure. John Whall has raised an order for a contractor to remove, via Carmella Davis CSA. Awaiting order number. ESA confirms ladder now removed. | 2015-08-24 | Fully Completed |  |  |  | 2013-08-19 14:28 | 2015-08-25 12:07 |  |  | 2013-08-19 14:28 | 2014-01-14 10:47 | Janice Wray
140 LEXHAM GARDENS-2013.02.26 | 2013-08-19 16:20 | S217012040001 | LEXHAM GARDENS (140) | 102665 | Completed | 23b | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. C | an it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2013-10-18 | Inspections are being done, sheets completed, and retained. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 16:20 | 2013-10-18 16:21 | 2013-08-19 16:20 | 2013-09-09 11:37 | -60 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:39 | S217012740003 | UPPER BERENGER WALK 1-42 | 139418 | Active | 16 | High | Signage | At present some of the signs near the entrances to the walkways are missing or damaged. These signs indicate the walkway name and flat numbers on that walkway. This information could aid the emergency services. | I would recommend that a check is carried out to see which signs are missing or damaged and then new signs are provided. These new signs should be permanently fixed to the walls similar to the existing ones, they should be in the same size font as the existing signs and positioned at the entrance to the walkways from the staircase/lift enclosures. | Neighbourhood Management | Wendy Stevenson |  | Previously assigned to Donal Daly and John Griffin as an estate project to audit and overhaul all signage on the estate. To re-assign to Repairs. | 2014-05-13 | Partially Completed | Janice Wray | 2014-04-10 16:39 | 2014-05-01 16:41 | 2014-04-10 16:39 | 2014-05-14 15:07 | -21 | In target
1-42 UPPER BERENGER WALK - 2014.3.12 | 2014-04-10 16:45 | S217012740003 | UPPER BERENGER WALK 1-42 | 139420 | Completed | 23b | Information Only | Inspection Regime | The monthly occupier tests and inspections of the dry risers, the external staircases, the lifts and the emergency lighting units. | I have assumed that the monthly occupiers testing and inspections of these items are being undertaken as per the caretaker's checklist and recorded under the tower blocks. This is because this is where these items are located. | Neighbourhood Management | Wendy Stevenson |  | Confirmed. | 2014-04-10 | Fully Completed |  |  |  | 2014-04-10 16:45 | 2014-04-11 16:53
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:16 | S217010567701 | LONGLANDS COURT (1-48) | 103176 | Completed | 8a | High | Communal Area Storage | Outside the flat entrance doors of flats 37 and 38 on the staircase landing there is a small cupboard. | I would recommend that this cupboard is removed from the staircase landing outside flats 37 and 38 entrance doors. | Neighbourhood Management | Martin Barr |  | Cupboard not outside the flats 07-11-13 | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-21 16:16 | 2013-09-11 16:17 | 2013-08-21 16:16 | 2013-11-08 14:11 | -21 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:18 | S217010567701 | LONGLANDS COURT (1-48) | 103177 | Completed | 8b | Medium | Communal Area Storage | In the ground floor electrical cupboard by flats 1 and 2 there were empty cardboard boxes being stored along with old electrical items and old light fittings. | I would recommend that all the storage is removed from this electrical cupboard/room. | Neighbourhood Management | Martin Barr |  | Order raised for clearance of the cupboard. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-21 16:18 | 2013-10-20 16:19 | 2013-08-21 16:18 | 2013-11-08 14:16 | -60 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:33 | S217010567701 | LONGLANDS COURT (1-48) | 103193 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | ESA checks as per the checklist. We are awaiting training from A&R team along with list of sites to be checked. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-21 16:33 | 2013-10-20 16:34 | 2013-08-21 16:33 | 2013-11-08 14:17 | -60 | In target
1-48 LONGLANDS COURT-2013.03.01 | 2013-08-21 16:54 | S217010567701 | LONGLANDS COURT (1-48) | 103205 | Completed | 1b | High | Communal Area Storage | Next to the entrance door of flat [redacted] there is an electrical socket which is used to charge the mobility scooter's battery which was parked outside this flat entrance door in the staircase entrance hall lobby area. | I would recommend that this electrical socket is removed and the charging of the mobility scooter in the means of escape route is stopped immediately. | Neighbourhood Management | Martin Barr |  | We have been unable to find a suitable location for an external charging shed, as there is a bin shed and a dry riser directly outside the building. We have suggested whether a fire rated enclosure inside the building would be satisfactory to the risk assessor before checking if this is feasible. External charging point now installed and communal socket removed - works completed and tenant briefed & agreeable to new arrangement. As previously advised this has been passed to Louie-Ann Miller to deal with as she is in charge of aids and adaptations. The socket was originally put in by adaptations team so the solution to problem needs to be found by them. Louie Ann confirms having difficulty accessing this flat to isolate / remove communal socket - 28th July 2015 | 2015-09-08 | Fully Completed | Martin Barr | 2013-08-21 16:54 | 2013-09-11 16:55 | 2013-08-21 16:54 | 2015-09-10 11:08 | -21 | In target | 2013-08-21 16:54 | 2015-08-04 19:37 | Janice Wray
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:18 | S217008650004 | EDENHAM WAY 15-50 | 207077 | Completed | 3 | High | Miscellaneous | To the side of this building by the bin storage room there is a lot of household furniture, beds, mattresses, bedroom furniture etc. | All of this household furniture should be removed from outside of this building so it cannot be used as fuel by an arsonist. | Neighbourhood Management | Martin Barr |  | This is unfortunately a recurring issue. Whenever we find items in this location we arrange clearances. Area was clear 22/09 | 2015-09-24 | Fully Completed | Martin Barr | 2015-07-16 09:18 | 2015-08-06 09:19 | 2015-07-16 09:18 | 2015-09-25 11:44 | -21 | In target
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:24 | S217008650004 | EDENHAM WAY 15-50 | 207080 | Completed | 12 | Information Only | Miscellaneous | In the ground floor entrance lobby area the door and the frame from the basement is not fire rated, the door is louvered and the frame does not fit in the aperture correctly. The basement area is presently a sterile area. | If the basement area is used as a storage area at any time then a 30 minute fire rated door set must be fitted in the opening from the basement area in to the ground floor entrance lobby area. Otherwise I believe that the presently fitted door is suitable and no action is required. | Neighbourhood Management | Martin Barr | 2016-01-08 | I ahve spoken to Clinton the ESA and he has confirmed that the basement area is not being used for storage. | 2016-01-07 | Fully Completed |  |  |  | 2015-07-16 09:24 | 2016-01-08 11:42 |  |  | 2015-07-16 09:24 | 2015-10-02 17:22 | Louise Nezandonyi
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:32 | S217008650004 | EDENHAM WAY 15-50 | 207084 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? When tested some of the emergency lighting in the basement area did not work. | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-16 09:32 | 2015-08-06 09:35 | 2015-07-16 09:32 | 2015-09-18 17:55 | -21 | In target
15 - 50 EDENHAM WAY - 2015.06.16 | 2015-07-16 09:35 | S217008650004 | EDENHAM WAY 15-50 | 207087 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment etc. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets, or computer record kept/sent as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-07-16 09:35 | 2015-08-06 09:36 | 2015-07-16 09:35 | 2015-09-17 13:12 | -21 | In target
15 BASSETT ROAD -2015.10.30 | 2015-11-16 13:49 | S217008100001 | BASSETT ROAD (15) | 227879 | Completed | 3a | High | Communal Area Storage | There is a double mattress, a bed and other household items on top of the brick built bin cupboards in the front garden of this property. | All of these items should be removed from this bin storage area. | Neighbourhood Management | Louise Nezandonyi | 2016-01-12 | The ESA has confirmed that this has now gone | 2016-01-11 | Fully Completed | Louise Nezandonyi | 2015-11-16 13:49 | 2015-12-07 13:52 | 2015-11-16 13:49 | 2016-01-12 11:50 | -21 | In target | 2015-11-16 13:49 | 2015-12-06 15:30 | Louise Nezandonyi
15 BASSETT ROAD -2015.10.30 | 2015-11-16 13:54 | S217008100001 | BASSETT ROAD (15) | 227885 | Completed | 8a | High | Communal Area Storage | The ground floor level electrical cupboard is being used by residents as a storage area. | All private storage should be removed from this electrical cupboard and the doors kept locked shut. | Neighbourhood Management | Louise Nezandonyi | 2016-01-12 | The ESA has confirmed that this has now been cleard | 2016-01-11 | Fully Completed | Louise Nezandonyi | 2015-11-16 13:54 | 2015-12-07 13:55 | 2015-11-16 13:54 | 2016-01-12 11:49 | -21 | In target | 2015-11-16 13:54 | 2015-12-06 15:31 | Louise Nezandonyi
15 BASSETT ROAD -2015.10.30 | 2015-11-16 13:56 | S217008100001 | BASSETT ROAD (15) | 227887 | Completed | 8b | High | Communal Area Storage | There are 1 or 2 items being stored under the staircase in the ground floor in the entrance hall/lobby area. | There should be no storage of combustible items under the staircase at the ground floor level. The push chair is ok though. | Neighbourhood Management | Louise Nezandonyi | 2016-01-12 | ESA has checked and this has now been cleared | 2016-01-11 | Fully Completed | Louise Nezandonyi | 2015-11-16 13:56 | 2015-12-07 13:57 | 2015-11-16 13:56 | 2016-01-12 11:49 | -21 | In target | 2015-11-16 13:56 | 2015-12-06 15:32 | Louise Nezandonyi
15 BASSETT ROAD -2015.10.30 | 2015-11-16 14:00 | S217008100001 | BASSETT ROAD (15) | 227890 | Completed | 23 | Medium | Inspection Regime | Caretaker inspections of this building. | Can it be confirmed that the caretaker is undertaking the inspections of this building as per the caretakers check list? | Neighbourhood Management | Louise Nezandonyi |  | Confirmed ESA doing regular inspections. These are recorded on the PDA | 2015-11-27 | Fully Completed | Louise Nezandonyi | 2015-11-16 14:00 | 2016-01-15 14:03 | 2015-11-16 14:00 | 2015-11-30 15:33 | -60 | In target | 2015-11-16 14:00 | 2015-12-06 15:32 | Janice Wray
16 ELM PARK GARDENS - 2015.05.22 | 2015-06-08 15:21 | S217001880013 | ELM PARK GARDENS (16) | 200550 | Completed | 23d | High | Inspection Regime | Are the weekly and monthly occupier's tests and inspections of all the mechanical and electrical components that make up the water protection system installed within flat 16A being undertaken according to the manufactures guidance. | Weekly and monthly occupier testing and inspections of the water protection system installed within flat 16A should be undertaken according to the manufactures guidance, with the results recorded in the buildings logbook. | Neighbourhood Management | Kamran Hye |  | completed by porters | 2015-06-16 | Fully Completed | Jimmy Lemos | 2015-06-08 15:21 | 2015-06-29 15:22 | 2015-06-08 15:21 | 2015-07-13 15:17 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:27 | S217002110007 | FINBOROUGH ROAD (169) | 194371 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Kamran Hye |  | Monthly H+S checks been completed and have checked on the insight report. | 2015-11-18 | Fully Completed | Nicola Rees | 2015-04-27 16:27 | 2015-05-18 16:28 | 2015-04-27 16:27 | 2015-11-19 15:53 | -21 | In target
169 FINBOROUGH ROAD - 2015.04.09 | 2015-04-27 16:29 | S217002110007 | FINBOROUGH ROAD (169) | 194372 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | John Whall confirms inspections undertaken | 2015-10-09 | Fully Completed | Janice Wray | 2015-04-27 16:29 | 2015-05-18 16:30 | 2015-04-27 16:29 | 2015-10-12 13:09 | -21 | In target
17 BURNABY STREET - 2014.4.15 | 2014-04-22 14:00 | S217000510003 | BURNABY STREET (13) | 140535 | Completed |  | Information Only | Inspection Regime | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson |  | This property is on the list of street properties for which a mobile locksmith will obtain keys as per plan adopted by Est Servs, Hoem Ownership & A n R. | 2014-05-14 | Fully Completed |  |  |  | 2014-04-22 14:00 | 2014-05-15 08:12
17 BURNABY STREET - 2014.4.15 | 2014-04-22 14:05 | S217000510004 | BURNABY STREET (17) | 140537 | Completed | 3 | Information Only | Miscellaneous | There is no self closing device fitted to the communal front entrance door of this building. | The fitting of a self closing device to the front entrance door of this building would mean that the front door is closed automatically and the security of the building could be improved. | Neighbourhood Management | Wendy Stevenson |  | "For information". We have no key to the MED (has a Banham lock) so awaiting the mobile locksmith operation. | 2014-06-02 | Fully Completed |  |  |  | 2014-04-22 14:05 | 2014-06-03 15:46
17 DANVERS STREET - 2015.10.08 | 2015-10-19 08:06 | S217001420001 | DANVERS STREET (17) | 222471 | Completed | 8 | High | Communal Area Storage | Outside the entrance door of Flat D on the landing of the staircase there are some cardboard boxes and other items being stored. These items could provide fuel for a fire and they increase the fire loading in the staircase enclosure. | I would recommend that the occupant of Flat D is asked to remove the items outside their flat. The resident should be reminder that the staircase should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading of the staircase is kept as low as possible. | Neighbourhood Management | Nicola Rees | 2016-02-22 | Spoke to resident and items removed | 2016-02-22 | Fully Completed | Nicola Rees | 2015-10-19 08:06 | 2015-11-09 08:10 | 2015-10-19 08:06 | 2016-04-08 15:36 | -21 | In target | 2015-10-19 08:06 | 2015-12-08 16:27 | Nicola Rees
176 TO 186 PORTLAND ROAD, EVEN NUMBERS ONLY, LONDON W11 4LU - 2016.12.28 | 2017-01-13 14:25 | S217011900005 | PORTLAND ROAD 176-186 | 274669 | Active | 9 | Information Only | Miscellaneous | The right hand side bin storage shed in the rear garden area is being used to store household furniture. | This is for your information only. | Neighbourhood Management | Martin Barr | 2018-01-12
18 AND 19 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:19 | S217009670006 | PENZANCE STREET 18/19 A-H | 214596 | Completed | 8 | Medium | Inspection Regime | On the balcony outside flat 18C there is an old wardrobe which contains tins of paint and other decorating items. | I would recommend that the wardrobe and its contents are removed from the balcony area. The children's push bikes can remain on this balcony. | Neighbourhood Management | Martin Barr |  | Neghbourhood Officer has written to resident to remove items | 2015-09-21 | Fully Completed | Martin Barr | 2015-09-02 15:19 | 2015-11-01 15:21 | 2015-09-02 15:19 | 2015-11-02 15:58 | -60 | In target
18 AND 19 PENZANCE STREET - 2015.08.13 | 2015-09-02 15:29 | S217009670006 | PENZANCE STREET 18/19 A-H | 214613 | Completed | 14 | Medium | Inspection Regime | In the cupboard off the ground floor level entrance hall area by flat 18A part of the wall above the cupboard door has been removed. | I would recommend that this wall is rebuilt so that there is not a large gap above this door. | Neighbourhood Management | Martin Barr |  | ESA has checked and cannot see any issue with gap above the foor so it appears to have already been rectified | 2015-09-21 | Fully Completed | Martin Barr | 2015-09-02 15:29 | 2015-11-01 15:51 | 2015-09-02 15:29 | 2015-11-02 15:59 | -60 | In target
18 BASING STREET - 2015.08.15 | 2015-09-02 14:47 | S217008090002 | BASING STREET (18) | 214583 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-02 14:47 | 2015-09-23 14:48 | 2015-09-02 14:47 | 2015-09-17 11:36 | -21 | In target
18 BASING STREET - 2015.08.15 | 2015-09-02 14:49 | S217008090002 | BASING STREET (18) | 214585 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the occupier checks of the buildings structure as per the caretakers check list? With the completed sheets, or computer records kept/sent as a record and as proof of testing being undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-02 14:49 | 2015-09-23 14:50 | 2015-09-02 14:49 | 2015-09-17 11:33 | -21 | In target
18 GOLBORNE ROAD, LONDON W10 5PW - 2015.02.12 | 2017-02-01 18:04 | S217008770010 | GOLBORNE ROAD 18 (1-10) | 275256 | Active | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr | 2017-03-01
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:02 | S217009620004 | OXFORD GARDENS (187) | 241803 | Completed | 4 | Medium | Inspection Regime | The is a large Butane gas cylinder/ bottle on the balcony of flat 2, this is a ground floor flat over looking the rear garden. The TMO tenancy agreement does not allow the storage of gas canisters within dwellings or on balconies etc. | The tenant of flat 2 should be asked to remove the gas canister/bottle from this balcony area. | Neighbourhood Management | Louise Nezandonyi | 2016-05-02 | Pat the ESA has confroimed that the items have now been removed | 2016-03-03 | Fully Completed | Louise Nezandonyi | 2016-02-08 11:02 | 2016-04-08 11:11 | 2016-02-08 11:02 | 2016-03-07 17:09 | -60 | In target | 2016-02-08 11:02 | 2016-03-11 17:06 | Louise Nezandonyi
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:11 | S217009620004 | OXFORD GARDENS (187) | 241810 | Completed | 8 | Medium | Inspection Regime | In the garden area down the side of flat 6 there are old push bikes, items of furniture, broken dining chairs and other assorted combustible items. | These items should be removed from this area. | Neighbourhood Management | Louise Nezandonyi | 2016-05-02 | The ESA has checked and the items have been removed. | 2016-03-02 | Fully Completed | Louise Nezandonyi | 2016-02-08 11:11 | 2016-04-08 11:13 | 2016-02-08 11:11 | 2016-03-14 10:51 | -60 | In target | 2016-02-08 11:11 | 2016-03-20 10:50 | Janice Wray
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:17 | S217009620004 | OXFORD GARDENS (187) | 241819 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-03-01 | Yes the emergency lighting is bering tested monthly and thje results are recored on insight as proof of testing having being undertaken | 2016-02-15 | Fully Completed | Louise Nezandonyi | 2016-02-08 11:17 | 2016-02-29 11:18 | 2016-02-08 11:17 | 2016-02-16 16:20 | -21 | In target
187 OXFORD GARDENS, LONDON W10 6NE - 2015.12.15 | 2016-02-08 11:19 | S217009620004 | OXFORD GARDENS (187) | 241820 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-03-01 | The caretaker is tresting and doing inspections of the building structure every Friday morning as well as on a monthly basis | 2016-02-15 | Fully Completed | Louise Nezandonyi | 2016-02-08 11:19 | 2016-02-29 11:20 | 2016-02-08 11:19 | 2016-02-16 16:35 | -21 | In target
19 KELFIELD GARDENS - 2015.10.30 | 2015-11-09 15:53 | S217009010002 | KELFIELD GARDENS (19) | 226609 | Completed | 23 | Medium | Inspection Regime | Caretaker inspections of this buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Louise Nezandonyi |  | We have no key to get into this block, the ESA knows the residents of the two flats so when he does his quarterly checks they will let him in so that the reglar checks are being carried out. Contract Management Team advised that lock change required - in hand | 2015-11-27 | Fully Completed | Louise Nezandonyi | 2015-11-09 15:53 | 2016-01-08 15:54 | 2015-11-09 15:53 | 2015-11-30 15:29 | -60 | In target | 2015-11-09 15:53 | 2015-12-06 15:28 | Janice Wray
191 LADBROKE GROVE, LONDON W10 6HH - 2015.11.03 | 2016-01-25 14:57 | S217009120006 | LADBROKE GROVE (191) | 239396 | Completed | 23b | High | Emergency Lighting | Are there regular occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | The recommendation is monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-02-22 | Regular checks are carried out quarterly by the ESA and the results are recorded as proof | 2016-03-07 | Fully Completed | Louise Nezandonyi | 2016-01-25 14:57 | 2016-02-15 14:58 | 2016-01-25 14:57 | 2016-03-08 16:44 | -21 | In target
191 LADBROKE GROVE, LONDON W10 6HH - 2015.11.03 | 2016-01-25 14:59 | S217009120006 | LADBROKE GROVE (191) | 239399 | Completed | 23c | Medium | Inspection Regime | Caretaker inspections of this buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed electronic sheet kept as a record. | Neighbourhood Management | Louise Nezandonyi | 2016-03-29 | This can be confirmed and the last time the checks took place at this block was on 17th February 2016. | 2016-03-07 | Fully Completed | Louise Nezandonyi | 2016-01-25 14:59 | 2016-03-25 15:01 | 2016-01-25 14:59 | 2016-03-08 16:50 | -60 | In target
1B KENLEY WALK, LONDON W11 4BA - 2017.01.30 | 2017-02-06 16:58 | S217011380001 | KENLEY WALK (1B) | 275376 | Active | 8 | High | Inspection Regime | At the time of this assessment there was a lot of combustible storage, a table, household furniture, suitcases etc in the entrance hall area and under the staircase. | All of these items should be removed from the entrance hall/lobby area and the resident who they belong too reminded that the common parts of this building must be kept free of combustible storage. | Neighbourhood Management | Martin Barr | 2017-03-06
1B KENLEY WALK, LONDON W11 4BA - 2017.01.30 | 2017-02-06 17:01 | S217011380001 | KENLEY WALK (1B) | 275378 | Active | 16 | High | Signage | There is a fire assembly sign on the rear exit door to the garden from the entrance hall area, the rear garden is NOT the buildings fire assembly point. | This fire assembly point sign should be removed from this garden exit door. Could the ESA please remove | Neighbourhood Management | Martin Barr | 2017-03-06
2 RADDINGTON ROAD -2014.3.6 | 2014-03-26 11:17 | S217009860001 | RADDINGTON ROAD (2) | 136603 | Completed | 1 | Information Only | Inspection Regime | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Martin Barr | 2016-01-29 | I have spoken to Maria Ares and we wil lbe arranging a lock change. A new barrel and keys need to be ordered and once these have arrived a date will be arranged for the lock change to take place COMPLETED | 2016-03-10 | Fully Completed |  |  |  | 2014-03-26 11:17 | 2017-03-13 12:44 |  |  | 2014-03-26 11:17 | 2017-03-17 12:43 | Janice Wray
2 RADDINGTON ROAD -2014.3.6 | 2014-03-26 11:21 | S217009860001 | RADDINGTON ROAD (2) | 136605 | Completed | 8 | Medium | Communal Area Storage | On the staircase half landing and on the staircase up to flat B there is a lot of storage. Two bedside units, a small book case, a shoe rack and a coat rail. | I would recommend that all of this combustible storage and these items are removed from the staircase enclosure of this building. | Neighbourhood Management | Martin Barr |  | We don't have keys to access communal space. Until a decision is made to change locks we cannot inspect | 2015-06-03 | Fully Completed | Martin Barr | 2014-03-26 11:21 | 2014-05-25 11:22 | 2014-03-26 11:21 | 2015-06-04 10:50 | -60 | In target
201 LADBROKE GROVE, LONDON W10 6HQ - 2015.11.03 | 2016-01-25 15:25 | S217009120007 | LADBROKE GROVE (201) | 239406 | Completed | 23 | Medium | Inspection Regime | Caretaker inspections of this buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed electronic sheet kept as a record. | Neighbourhood Management | Louise Nezandonyi | 2016-04-04 | The caretaker is carrying out checks in this block quarterly adn records are being kept. | 2016-03-07 | Fully Completed | Louise Nezandonyi | 2016-01-25 15:25 | 2016-03-25 15:28 | 2016-01-25 15:25 | 2016-03-08 17:00 | -60 | In target
21 DANVERS STREET - 2015.10.08 | 2015-10-16 09:09 | S217001420003 | DANVERS STREET (21) | 222239 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of this buildings structure etc as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the inspections and checks of this building as per the caretakers check list. With the completed sheets kept as a record and proof of the inspections etc. The fire extinguisher located in this building is 3 years over due a service/test. | Neighbourhood Management | Nicola Rees |  | Asked Jimmy to check on this extinguisher and ask for this to be removed. 09.11.15 Jimmy advised that this was not there on inspection on the 12.11.15. | 2015-11-12 | Fully Completed | Nicola Rees | 2015-10-16 09:09 | 2015-11-06 09:10 | 2015-10-16 09:09 | 2015-11-16 10:30 | -21 | In target
21 TO 29 NORWOOD ROAD - 2015.09.24 | 2015-10-05 11:37 | S206023300001 | NORWOOD ROAD (21-29) | 219966 | Completed | 8a | High | Inspection Regime | There is a settee on the 2nd floor level staircase landing by flats 6 and 8. | This settee should be removed from this staircase landing. | Neighbourhood Management | Nicola Rees |  | Discussed with Jimmy on 09.11.15. He has already carded the property and going to go back and check. Jimmy has raised an order for this to be removed on the 11.11.15. The Home Ownership team have also been notified around contacting the leaseholder around health and safety. Jimmy to check succesfully removed. OCS confirmed that the sofa was removed and taken to the bulk area last week 26.11.15 | 2015-11-11 | Fully Completed | Nicola Rees | 2015-10-05 11:37 | 2015-10-26 11:39 | 2015-10-05 11:37 | 2015-12-02 15:02 | -21 | In target | 2015-10-05 11:37 | 2015-11-20 18:32 | Nicola Rees
21 TO 29 NORWOOD ROAD - 2015.09.24 | 2015-10-05 11:39 | S206023300001 | NORWOOD ROAD (21-29) | 219968 | Completed | 8b | High | Inspection Regime | There is an area at the end of the garages where on the wall is a sign which says "No large items to be dumped in this area". There are large household items dumped here, TV units, items of furniture and a lot of empty large cardboard boxes. | All of the items should be removed from this area and also any items between or behind the garages as well. The sign says no dumping of large items so may I ask why is the policy as indicated by the sign not being enforced? | Neighbourhood Management | Nicola Rees |  | Jimmy (ESA) has advised that this area is also the bulk area where the cleaning team put their rubbish. I asked if there were alternatives and no suggestions given except that this could be gated up. I have passed this onto Dominic's team for further suggestions on 09.11.15. Jimmy advised that this area is not by the flats. | 2015-11-09 | Fully Completed | Nicola Rees | 2015-10-05 11:39 | 2015-10-26 11:41 | 2015-10-05 11:39 | 2015-11-10 17:58 | -21 | In target
210 LADBROKE GROVE, LONDON W10 5LU - 2015.11.19 | 2016-01-27 09:24 | S217009120003 | LADBROKE GROVE (210) | 239690 | Completed | 23b | High | Inspection Regime | The caretaker recording system, "Insight" has been checked and it appears the caretaker(s) is not undertaking the occupiers monthly tests and inspections of the emergency escape lighting units/system installed within this building. | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded. | Neighbourhood Management | Louise Nezandonyi | 2016-02-25 | It has been conformed with Pat and checked that this is done monthly | 2016-03-08 | Fully Completed | Louise Nezandonyi | 2016-01-27 09:24 | 2016-02-17 09:25 | 2016-01-27 09:24 | 2016-03-09 14:52 | -21 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:43 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102437 | Completed | 3 | Medium | Communal Area Storage | There are off cuts of timber and other rubbish and waste on top of the brick bin cupboards | I would recommend that all the waste/rubbish is removed from on top of the bin cupboards | Neighbourhood Management | Wendy Stevenson | 2013-09-27 | This is a recurring problem issue that gets periodically cleared. Is due for clearance again next week. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 11:43 | 2013-10-18 11:46 | 2013-08-19 11:43 | 2013-11-08 15:08 | -60 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:49 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102441 | Completed | 8a | High | Communal Area Storage | On the first floor level landing there is a small table, pictures in frames piled against the wall and a cardboard box of light shades under the table. | These items should be removed from the staircase landing immediately, as the landing is quite small and these items could cause an obstruction of the means of escape route. | Neighbourhood Management | Wendy Stevenson |  | Items have been stickered to notify residents of removal. Will be removed next week if they remain. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 11:49 | 2013-09-09 11:51 | 2013-08-19 11:49 | 2013-11-08 15:09 | -21 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:52 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102442 | Completed | 8b | Medium | Communal Area Storage | In the electrical room there are old light fittings, a large office type chair and cardboard boxes. | I would recommend that all these items are removed from this electrical room. | Neighbourhood Management | Wendy Stevenson |  | Order raised to clear cupboard. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 11:52 | 2013-10-18 11:53 | 2013-08-19 11:52 | 2013-11-08 14:54 | -60 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 11:59 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102446 | Completed | 23a | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | Can you please confirm that ESA are carrying out these tasks ESA checks as per the H&S checklist. We are awaiting training from A&R team along with list of sites to be checked. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-19 11:59 | 2013-10-18 12:01 | 2013-08-19 11:59 | 2013-11-08 14:46 | -60 | In target
2-12 MORGAN (EVEN)R0AD-2013.02.01 | 2013-08-19 12:03 | S217009467714 | MORGAN ROAD EVEN (2-12) | 102448 | Completed | 23b | Information Only | Inspection Regime | It is not known if there is an emergency lighting system installed within the staircase of this building, please see item 15 above. But there is definitely an emergency lighting unit in the electrical room. | Monthly occupiers testing and inspections of the emergency lighting system installed in this building then should be undertaken by the caretaker with the results recorded as proof of testing having been undertaken. If it is found that the lighting units on the staircase landings are combined emergency lighting units testing of these should also be undertaken. The system should also be added to the contractor's maintenance schedule so that planned preventive maintenance and servicing is undertaken. | Neighbourhood Management | Martin Barr |  | This is for information until confirmation is received from A&R Contract Management re the emergency lighting | 2013-11-07 | Fully Completed |  |  |  | 2013-08-19 12:03 | 2013-11-08 14:58
2-12 MORGAN ROAD, (EVEN NUMBERS ONLY) LONDON W10 5YS - 2016.03.04 | 2016-03-17 16:17 | S217009467714 | MORGAN ROAD EVEN (2-12) | 249746 | Completed | 8 | Medium | Inspection Regime | In the electrical room there are cardboard boxes, some with old light fittings in them and a broken up item of furniture. | I would recommend that all of these items are removed from this electrical room. | Neighbourhood Management | Louise Nezandonyi | 2016-06-16 | Rob the ESA went to check this on 2nd November 2016 and foundthat the area has been cleared of all items Hi Louise Please see attached pictures of the said intake confirming its clear of any items. Regards Rob. | 2016-11-02 | Fully Completed | Louise Nezandonyi | 2016-03-17 16:17 | 2016-05-16 16:19 | 2016-03-17 16:17 | 2016-11-07 12:47 | -60 | In target
2-12 MORGAN ROAD, (EVEN NUMBERS ONLY) LONDON W10 5YS - 2016.03.04 | 2016-03-17 16:26 | S217009467714 | MORGAN ROAD EVEN (2-12) | 249751 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Louise Nezandonyi | 2016-04-18 | Monthly occupier testing and inspections of the emergency lighting is carried out and recorded on Insight | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-03-17 16:26 | 2016-04-07 16:27 | 2016-03-17 16:26 | 2016-04-06 17:33 | -21 | In target
2-12 MORGAN ROAD, (EVEN NUMBERS ONLY) LONDON W10 5YS - 2016.03.04 | 2016-03-17 16:27 | S217009467714 | MORGAN ROAD EVEN (2-12) | 249752 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Louise Nezandonyi | 2016-04-18 | Testing and inspections of this building is carried out and recorded on Insight | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-03-17 16:27 | 2016-04-07 16:28 | 2016-03-17 16:27 | 2016-04-06 17:32 | -21 | In target
23 DANVERS STREET - 2015.10.08 | 2015-10-16 09:11 | S217001420004 | DANVERS STREET (23) | 222240 | Active | 20850 | Medium | Miscellaneous | The London Metropolitan Police fitted a second mortice lock to the communal entrance door of this building. According to one of the occupants of this building a key for this 2nd door lock was given to the Worlds End concierge's office, this is a Banham door lock. The concierge's office does not have this key for this 2nd lock. This door also has a night chain on it so any visitor to this building is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the 2nd lock on this buildings communal front entrance door. The night chain should also be removed from this communal entrance door because if this chain is engaged then persons even with both keys cannot open this door. Access to the common parts of this building should be available to the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-02-05 | Email sent to Jimmy to get additional key as we do not hold this one and also to place an order to remove the chain. 11.04.16. Email sent to chase Jimmy on the 08.11.16 | 2016-02-05 | Partially Completed | Nicola Rees | 2015-10-16 09:11 | 2015-12-15 09:13 | 2015-10-16 09:11 | 2016-02-08 14:41 | -60 | In target | 2015-10-16 09:11 | 2016-02-21 20:53 | Janice Wray
23 FERNSHAW ROAD - 2015.11.11 | 2015-11-16 11:56 | S217002100003 | FERNSHAW ROAD (23) | 227841 | Completed | 3a | High | Miscellaneous | The fire fighter entry over ride device fitted to the entrance door of this building did not function and release the locking device on the door and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride device fitted to the entrance door of this building should be repaired or replaced so that it releases the locking device fitted to the buildings entrance door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. ESA check please & if necessary advise CSC | Neighbourhood Management | Nicola Rees |  | Order raised for this to be repaired on: 201545731 | 2015-12-03 | Fully Completed | Nicola Rees | 2015-11-16 11:56 | 2015-12-07 11:58 | 2015-11-16 11:56 | 2015-12-04 17:42 | -21 | In target | 2015-11-16 11:56 | 2015-12-10 17:41 | Janice Wray
230 LADBROKE GROVE, LONDON W10 5LT - 2016.06.01 | 2016-06-16 15:52 | S217009120004 | LADBROKE GROVE (230) | 265191 | Active | 8a | High | Communal Area Storage | Outside flat C's entrance door on the staircase landing there are combustible items of storage, bags and a DVD player/recorder. | All of these items should be removed from this staircase landing and the staircase enclosure, the push bike on the half landing can remain. But if the occupant of flat C does not remove all of the items of storage or they are place back there again after being removed then the push bike should also be removed. | Neighbourhood Management | Louise Nezandonyi | 2016-07-15 |  |  |  | Cyril Morris | 2016-06-16 15:52 | 2016-07-07 15:54 |  |  | 245 | 245 days overdue
230 LADBROKE GROVE, LONDON W10 5LT - 2016.06.01 | 2016-06-16 15:55 | S217009120004 | LADBROKE GROVE (230) | 265192 | Active | 8b | High | Communal Area Storage | On the external roof at the rear of this building, under the staircase landing window there are old push bikes and parts of bikes along with a sack trolley and tins of paint. | All of the items should be removed from this external roof area. | Neighbourhood Management | Louise Nezandonyi | 2016-07-15 |  |  |  | Cyril Morris | 2016-06-16 15:55 | 2016-07-07 15:56 |  |  | 245 | 245 days overdue
230 LADBROKE GROVE, LONDON W10 5LT - 2016.06.01 | 2016-06-16 15:57 | S217009120004 | LADBROKE GROVE (230) | 265193 | Active | 12 | High | Communal Area Storage | The storage cupboard door located on the ground to first floor half landing was unlocked. | The storage cupboard door located on the ground to first floor half landing should kept locked shut at all times unless somebody is using the cupboard, this may require the fitting of a new lock. | Neighbourhood Management | Louise Nezandonyi | 2016-07-15 |  |  |  | Cyril Morris | 2016-06-16 15:57 | 2016-07-07 16:02 |  |  | 245 | 245 days overdue
24 BURNABY STREET - 2015.09.21 | 2015-10-05 09:40 | S217000510010 | BURNABY STREET (24) | 219902 | Completed | 12 | Medium | Miscellaneous | There is a mortice lock fitted to the entrance door of this building as well as the yale lock. | Can it be confirmed that the mortice lock fitted to the communal entrance door has been disabled so that it cannot be locked. If this mortice lock is functional then I would recommend that a thumb turn device is fitted on the inner face of the door so that the entrance door can be opened from the entrance hall side without the use of a key. Alternatively the mortice lock could disabled or removed completely and the holes in the door suitably filled in for security reasons. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Lock change week beginning 25.01.16 | 2016-02-04 | Fully Completed | Nicola Rees | 2015-10-05 09:40 | 2015-12-04 09:42 | 2015-10-05 09:40 | 2016-02-08 16:19 | -60 | In target | 2015-10-05 09:40 | 2016-02-14 16:18 | Janice Wray
24 BURNABY STREET - 2015.09.21 | 2015-10-05 09:45 | S217000510010 | BURNABY STREET (24) | 219904 | Completed | 23b | High | Emergency Lighting | Are there regular occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | The recommendation is monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Lock change week beg 25.01.15 | 2016-02-04 | Fully Completed | Nicola Rees | 2015-10-05 09:45 | 2015-10-26 09:47 | 2015-10-05 09:45 | 2016-02-08 16:20 | -21 | In target | 2015-10-05 09:45 | 2016-02-14 16:19 | Janice Wray
24 STADIUM STREET - 2013.12.31 | 2013-12-31 14:38 | S217005190011 | STADIUM STREET (24) | 122171 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson | 2014-06-29 |  | 2014-01-10 | Fully Completed |  |  |  | 2013-12-31 14:38 | 2014-01-13 12:12
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 13:14 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215920 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 13:14 | 2015-10-01 13:15 | 2015-09-10 13:14 | 2015-09-17 10:50 | -21 | In target
2-48 SHALFLEET DRIVE, (EVEN NUMBERS ONLY), - 2015.08.13 | 2015-09-10 13:17 | S217009960006 | SHALFLEET DRIVE 2-12 EV | 215921 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 13:17 | 2015-10-01 13:18 | 2015-09-10 13:17 | 2015-09-17 10:49 | -21 | In target
25 BASING STREET - 2015.08.13 | 2015-09-02 14:25 | S217008090003 | BASING STREET (25) | 214573 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-02 14:25 | 2015-09-23 14:26 | 2015-09-02 14:25 | 2015-09-17 12:11 | -21 | In target
25 BASING STREET - 2015.08.13 | 2015-09-02 14:26 | S217008090003 | BASING STREET (25) | 214574 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the occupier checks of the buildings structure as per the caretakers check list? With the completed sheets, or computer records kept/sent as a record and as proof of testing being undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-02 14:26 | 2015-09-23 14:27 | 2015-09-02 14:26 | 2015-09-17 12:11 | -21 | In target
25 DANVERS STREET -2015.10.08 | 2015-10-16 09:26 | S217001420005 | DANVERS STREET (25) | 222247 | Completed |  | Information Only | Inspection Regime | There has been a person sleeping in the lower ground floor/basement level water pump room/area. The police have been informed of these incidents and have visited this premises. | Are the TMO aware of a person sleeping in the lower ground floor/basement level water pump room/area. Also that the police have been informed of this and have visited this premises. | Neighbourhood Management | Nicola Rees | 2015-12-01 | ESA has locked area and provided outreach information to tenant should person return. | 2015-12-01 | Fully Completed |  |  |  | 2015-10-16 09:26 | 2015-12-02 15:05
26 BURNABY STREET, LONDON - 2014.04.13 | 2014-01-31 09:34 | S217000510011 | BURNABY STREET (26) | 127327 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson |  | Keys being pursued as part of initiative with Home Ownership Team and A & R. | 2014-03-17 | Fully Completed |  |  |  | 2014-01-31 09:34 | 2014-03-18 14:00
26 BURNABY STREET, LONDON - 2014.04.13 | 2014-01-31 09:47 | S217000510011 | BURNABY STREET (26) | 127338 | Completed | 8 | Medium | Communal Area Storage | There is a storage area at the lower ground floor level accessed down the metal steps from the footpath, this area extends out under the public footpath. There is a lot of rubbish, old and damaged items as well as an old Christmas tree and tins of paint etc stored/located in this area. | I would recommend that this storage area is completely cleared out and all the old, damaged and unwanted items are removed. | Neighbourhood Management | Wendy Stevenson |  | Removed. 201351986 - ref no. | 2014-02-18 | Fully Completed | Wendy Stevenson | 2014-01-31 09:47 | 2014-04-01 09:48 | 2014-01-31 09:47 | 2014-02-19 14:07 | -60 | In target
275 LADBROKE GROVE - 2015.10.13 | 2015-10-22 12:13 | S217009120009 | LADBROKE GROVE (275) | 223438 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Confirmed ESA doing monthly EL checks and regular inspections. These are recorded on the PDA | 2015-11-27 | Fully Completed | Louise Nezandonyi | 2015-10-22 12:13 | 2015-11-12 12:14 | 2015-10-22 12:13 | 2015-11-30 14:32 | -21 | In target
275 LADBROKE GROVE - 2015.10.13 | 2015-10-22 12:15 | S217009120009 | LADBROKE GROVE (275) | 223439 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the occupier checks of the buildings structure as per the caretakers check list? With the completed sheets, or computer records kept/sent as a record and as proof of testing being undertaken. | Neighbourhood Management | Martin Barr |  | Confirmed ESA doing monthly EL checks and regular inspections. These are recorded on the PDA | 2015-11-27 | Fully Completed | Louise Nezandonyi | 2015-10-22 12:15 | 2015-11-12 12:16 | 2015-10-22 12:15 | 2015-11-30 14:33 | -21 | In target
28 BURNABY STREET - 2015.09.21 | 2015-10-05 09:52 | S217000510012 | BURNABY STREET (28) | 219905 | Completed | 20826 | Information Only | Inspection Regime | The caretaker does not have any keys to the communal front entrance door of this building. There is an access control system with a trade's man's button but no a fire fighter over ride switch fitted. | I would recommend that a key is obtained for the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-02-04 | Lock changes on week beginning 01.02.16. | 2016-02-04 | Fully Completed |  |  |  | 2015-10-05 09:52 | 2016-02-08 16:23 |  |  | 2015-10-05 09:52 | 2016-02-14 16:22 | Janice Wray
28 BURNABY STREET - 2015.09.21 | 2015-10-05 10:01 | S217000510012 | BURNABY STREET (28) | 219912 | Completed | 23b | High | Emergency Lighting | If there are combine normal and emergency lighting in this building are there regular occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | The recommendation is monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-01-25 | Jimmy has completed a check this month on the 12.11.15. Lock changed to this block completed on 25.01.16 | 2016-01-25 | Fully Completed | Nicola Rees | 2015-10-05 10:01 | 2015-10-26 10:02 | 2015-10-05 10:01 | 2016-04-12 16:07 | -21 | In target | 2015-10-05 10:01 | 2015-11-20 18:36 | Nicola Rees
28 BURNABY STREET - 2015.09.21 | 2015-10-05 10:07 | S217000510012 | BURNABY STREET (28) | 219914 | Completed | 23b | High | Emergency Lighting | If there are combine normal and emergency lighting in this building are there regular occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | The recommendation is monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-01-25 | There are issues around access to this block and A+R and this has now been completed on the 25.01.16. ESA advused completing emergency lighting test where applicable. | 2015-01-26 | Fully Completed | Nicola Rees | 2015-10-05 10:07 | 2015-10-26 10:09 | 2015-10-05 10:07 | 2016-04-12 16:09 | -21 | In target | 2015-10-05 10:07 | 2015-11-20 18:26 | Nicola Rees
29 DANVERS STREET-2013.07.23 | 2013-08-21 11:09 | S217001420007 | DANVERS STREET (29) | 103047 | Completed | 8 | High | Communal Area Storage | The lower ground floor level cupboard has a lot of storage in it, the gas meters located in this cupboard are not easily accessible. | I would recommend that this lower ground floor level cupboard is emptied out and tidied up with all old damaged items etc removed, there should be easy access to the gas meters in this cupboard. | Neighbourhood Management | Wendy Stevenson |  | Letters were sent to several addresses in August 2013 by Nicola Rees, requesting removal of all items from communal areas, esp the gas meter cupboards, incl 29. An order was requested by the ESA on 28th August 2013 for removal of remaining items. This was chased by the ESA on 5th September 2013 as no order number has been received. Currently the clearance request is with Chris Baker. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-21 11:09 | 2013-09-11 11:10 | 2013-08-21 11:09 | 2013-09-09 10:44 | -21 | In target
29 DANVERS STREET-2013.07.23 | 2013-08-21 11:15 | S217001420007 | DANVERS STREET (29) | 103051 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. The fire extinguisher was last serviced on the 6th October 2011 so it is out of test date, so it appears that the caretaker's inspections are not being undertaken. | Can it be confirmed that the caretaker(s) are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2013-10-20 | Inspections are taking place monthly and the results noted. This is the only fire extinguisher in place after the rest were removed from site several months ago by contractor RGE. Order raised today for RGE to remove this remaining one. REMOVED | 2013-10-18 | Fully Completed | Wendy Stevenson | 2013-08-21 11:15 | 2013-10-20 11:15 | 2013-08-21 11:15 | 2014-01-08 10:25 | -60 | In target | 2013-08-21 11:15 | 2014-01-14 10:25 | Janice Wray
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:33 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215992 | Completed | 2 | Medium | Signage | There are not any "No Smoking" signs displayed in the end two staircases. | I would recommend that "No Smoking" signs are displayed in the end two staircases. | Neighbourhood Management | Martin Barr |  | Signs have been put up on display | 2015-09-24 | Fully Completed | Martin Barr | 2015-09-10 15:33 | 2015-11-09 15:34 | 2015-09-10 15:33 | 2015-09-25 11:29 | -60 | In target
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:35 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215993 | Completed | 8 | High | Inspection Regime | On the landing area outside flat 35 (TENANT) there are cardboard boxes of household items, a table and a microwave oven. | These items should be removed from this landing area and the residents reminded of the policy of not storing combustible items in the common parts of this building. | Neighbourhood Management | Martin Barr | 2016-01-12 | Os the Esa confirmed that he went here yesterday and everything has been removed. | 2016-01-12 | Fully Completed | Louise Nezandonyi | 2015-09-10 15:35 | 2015-10-01 15:36 | 2015-09-10 15:35 | 2016-01-13 15:32 | -21 | In target | 2015-09-10 15:35 | 2015-12-09 20:37 | Louise Nezandonyi
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:43 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215996 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 15:43 | 2015-10-01 15:44 | 2015-09-10 15:43 | 2015-09-17 10:47 | -21 | In target
29-41 SHALFLEET DRIVE, ODD NUMBERS ONLY AND 43-76 WAYNFLETE SQUARE - 2015.08.13 | 2015-09-10 15:44 | S217009960005 | SHALFLEET DRIVE 29-41 OD | 215997 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 15:44 | 2015-10-01 15:45 | 2015-09-10 15:44 | 2015-09-17 10:46 | -21 | In target
297 LADBROKE GROVE, LONDON W10 6HE - 2015.12.22 | 2016-02-16 11:51 | S217009120010 | LADBROKE GROVE (297) | 243728 | Completed | 3b | High | Miscellaneous | The fire fighter override device fitted to this buildings communal entrance door did not function correctly and release the locking mechanism of the door. This override device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. T | he fire fighter override device fitted to this building communal entrance door should be repaired or replaced so that it releases the locking mechanism of the door. ESA to recheck | Neighbourhood Management | Louise Nezandonyi | 2016-03-15 | This has been nraised by nthe caretaker and job to be completed on 14/03/2016 | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-16 11:51 | 2016-03-08 11:53 | 2016-02-16 11:51 | 2016-03-17 16:29 | -21 | In target
319 (329, 331 & 333) LADBROKE GROVE - 2015.04.22 | 2015-05-01 09:34 | S217009120041 | LADBROKE GROVE 319 A-J + | 195006 | Completed | 10 | High | Communal Area Storage | On the external balcony between flats B and C there is a BBQ, it is not known if the owners uses this BBQ on the balcony. This is a high fire risk item and a fire hazard. I believe that cooking on a BBQ on a flat balcony is not allowed under the tenancy agreement. | I would recommend that the BBQ is removed from this balcony area immediately. I would recommend that the owner of the BBQ is asked where the gas cylinder is kept? It should not be stored in the dwelling etc. | Neighbourhood Management | Martin Barr |  | BBQ has been removed | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-01 09:34 | 2015-05-22 09:38 | 2015-05-01 09:34 | 2015-06-04 13:00 | -21 | In target
32 ST CHARLES SQUARE - 2015.04.20 | 2015-04-27 15:01 | S217010080001 | ST CHARLES SQUARE (32) | 194323 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-04-27 15:01 | 2015-05-18 15:03 | 2015-04-27 15:01 | 2015-05-19 11:47 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:24 | S217009120011 | LADBROKE GROVE (339) | 196439 | Completed | 2 | High | Communal Area Storage | In the lower ground floor level residents storage area there are piles of cigarette ends and other smoking material on the floor, along with spent matches and empty beer cans. It appears that persons are using this area for party's etc. | I would recommend that the floor of this area is cleaned up and all discarded smoking materials and other items are removed. The locks on the doors to this area can be changed so that there is restricted access to this area to stop smoking occurring in this area. | Neighbourhood Management | Martin Barr |  | Area has been cleared. Area is shed area in use by residents so locks have been changed. No further reports of ASB since clean up. | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-12 09:24 | 2015-06-02 09:25 | 2015-05-12 09:24 | 2015-06-04 13:01 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:26 | S217009120011 | LADBROKE GROVE (339) | 196441 | Completed | 8a | High | Miscellaneous | In both of the electrical rooms/cupboards there are empty cardboard boxes. | All waste and combustible storage should be removed from these electrical rooms/cupboards. | Neighbourhood Management | Martin Barr |  | order raised with cleaning team to remove all items | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-12 09:26 | 2015-06-02 09:27 | 2015-05-12 09:26 | 2015-06-04 13:02 | -21 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:29 | S217009120011 | LADBROKE GROVE (339) | 196447 | Completed | 8c | Low |  | At the time of this assessment there were empty and full flat pack boxes in the entrance hall area of the staircase of flats 5 to 8. | It is assumed that the owner of these boxes will have removed them quite quickly, but I would recommend that the caretaker is asked to check that all of these items have been removed from this area. | Neighbourhood Management | Martin Barr |  | Residents have removed boxes | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-12 09:29 | 2015-11-08 09:30 | 2015-05-12 09:29 | 2015-06-04 13:03 | -180 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:31 | S217009120011 | LADBROKE GROVE (339) | 196448 | Completed | 8d | Low | Storage | During the risk assessment access could not be gained to the store room/area at the lower ground floor level of the staircase of flats 1 to 4. This is to the right as you go down the stairs. It is not known what is in this storage area, but it is suitably fire separated from the staircase. | I would recommend that key is obtained to this store room and its contents are checked. A regular check on the contents of this room should be undertaken to see that the storage or use is in accordance with any tenancy agreement if this is a private storage space. | Neighbourhood Management | Martin Barr |  | ESA has keys to this area. It is an old store room and contents are ok. | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-12 09:31 | 2015-11-08 09:35 | 2015-05-12 09:31 | 2015-06-04 13:06 | -180 | In target
339 LADBROKE GROVE - 2015.05.06 | 2015-05-12 09:42 | S217009120011 | LADBROKE GROVE (339) | 196461 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-12 09:42 | 2015-06-02 09:43 | 2015-05-12 09:42 | 2015-05-19 11:46 | -21 | In target
34 GORDON PLACE, LONDON W8 4JE - 2015.12.22 | 2016-02-08 12:50 | S217002320001 | GORDON PLACE (34) | 241895 | Completed | 8 | Medium | Communal Area Storage | The storage brick built cupboard at the basement level of this building, this cupboard contains bags of rubbish and waste as well as full black plastic bins etc. | I would recommend that this cupboard is completely emptied out of all storage and rubbish etc. It can then be used as a bin storage area again. | Neighbourhood Management | Nicola Rees | 2016-05-02 | ESA confirmed that this had been cleared and tidied 16.05.16 | 2016-05-16 | Fully Completed | Nicola Rees | 2016-02-08 12:50 | 2016-04-08 12:55 | 2016-02-08 12:50 | 2016-05-20 16:42 | -60 | In target
34 GORDON PLACE, LONDON W8 4JE - 2015.12.22 | 2016-02-08 13:04 | S217002320001 | GORDON PLACE (34) | 241908 | Active | 23 | Medium | Inspection Regime | Caretaker inspections of this buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed electronic sheet kept as a record. | Neighbourhood Management | Nicola Rees | 2016-05-02 |  |  |  | Cyril Morris | 2016-02-08 13:04 | 2016-04-08 13:06 |  |  | 335 | 335 days overdue
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:29 | S217009620005 | OXFORD GARDENS (34) | 103058 | Completed | 8a | High | Communal Area Storage | There is contractors waste and cardboard boxes of old electrical components etc in the room of the roof level lift motor room. | I would recommend that all the waste and rubbish is removed from this side room off the roof level lift motor room. | Neighbourhood Management | Martin Barr |  | Order raised for cleaning contractors to clear remaining items. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-21 11:29 | 2013-09-11 11:35 | 2013-08-21 11:29 | 2013-10-14 12:02 | -21 | In target
34 OXFORD GARDENS-2013.07.30 | 2013-08-21 11:36 | S217009620005 | OXFORD GARDENS (34) | 103062 | Completed | 8b | High | Communal Area Storage | In the central/common areas of the residents store rooms on each floor level located off the lift lobby area there is storage. The room off the 5th floor level is the worst with old kitchen units and internal doors being stored. | I would recommend that all the residents storage rooms are checked and that all items stored outside the storage cupboards is removed. | Neighbourhood Management | Martin Barr |  | Order raised for clearance of any remaining items by cleaning contractors. Most rooms were clear, with only a small number of items present on recent inspection. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-21 11:36 | 2013-09-11 11:37 | 2013-08-21 11:36 | 2013-10-14 12:11 | -21 | In target
347 WESTBOURNE PARK ROAD - 2015.1.23 | 2015-01-30 12:04 | S217010570002 | WESTBOURNE PARK ROAD (347) | 181042 | Completed | 8 | Medium | Communal Area Storage | There is a 5 drawer bedroom unit, other assorted items of bedroom furniture and an old push chair located under the concrete staircase. | I would recommend that these items are removed from under this staircase. | Neighbourhood Management | Martin Barr |  | A bulk clearance was raised and items were removed | 2015-06-03 | Fully Completed | Martin Barr | 2015-01-30 12:04 | 2015-03-31 12:05 | 2015-01-30 12:04 | 2015-06-04 13:07 | -60 | In target
35 ELM PARK GARDENS - 2015.05.22 | 2015-06-12 11:06 | S217001880004 | ELM PARK GARDENS (35) | 201266 | Active | 23d | High | Inspection Regime | Are the weekly and monthly occupier's tests and inspections of all the mechanical and electrical components that make up the water protection system installed within flat 35B being undertaken according to the manufactures guidance. | Weekly and monthly occupier testing and inspections of the water protection system installed within flat 35B should be undertaken according to the manufactures guidance, with the results recorded in the buildings logbook. | Neighbourhood Management | Kamran Hye |  |  |  |  | Cyril Morris | 2015-06-12 11:06 | 2015-07-03 11:07 |  |  | 615 | 615 days overdue
359 TO 361 FULHAM ROAD, LONDON SW10 9TW - 2016.05.06 | 2016-05-31 16:24 | S217002180003 | FULHAM ROAD (361) | 263255 | Completed | 12b | Medium | Inspection Regime | The lock on the lift hatch does not engage fully. | I would recommend that the gerda lock on the lift hatch is looked at and repaired or replaced as necessary, so that this ceiling hatch can be secured fully. Nicola - could the ESA please investigate what works are required and request an order as appropriate | Neighbourhood Management | Nicola Rees | 2016-08-22 | The ESA had confirmed that this is working but the gerda key is a H12 and not H10 which may have caused the access issue. | 2016-10-04 | Fully Completed | Nicola Rees | 2016-05-31 16:24 | 2016-07-30 16:27 | 2016-05-31 16:24 | 2016-12-02 16:19 | -60 | In target
359 TO 361 FULHAM ROAD, LONDON SW10 9TW - 2016.05.06 | 2016-05-31 16:44 | S217002180003 | FULHAM ROAD (361) | 263274 | Completed | 23b | High | Inspection Regime | Are the monthly occupier's inspections and tests being undertaken on the emergency lighting system/units installed within this building and also the inspections of the buildings structure etc? | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier's tests and inspections of the emergency lighting system installed in this building and the structural items? With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-06-20 | This is being completed. | 2016-12-01 | Fully Completed | Nicola Rees | 2016-05-31 16:44 | 2016-06-21 16:45 | 2016-05-31 16:44 | 2016-12-02 16:15 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 11:44 | S217009700001 | PORTOBELLO ROAD (375) | 201069 | Completed | 8 | Low | Communal Area Storage | During the risk assessment access could not be gained to the three rooms accessed from the end staircase landings. It is not known what is in these 3 rooms, but they are suitably fire separated from the staircase landings. | I would recommend that a check on the contents of these rooms is undertaken, to see that the storage or use of these rooms is in accordance with the tenancy agreements. | Neighbourhood Management | Martin Barr |  | Nobody in the TMO has keys to these rooms. As such lock changes have been ordered to gain access and check contents. Order number 201529950, target date 15/10/15 | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 11:44 | 2015-12-08 11:47 | 2015-06-11 11:44 | 2015-09-21 10:14 | -180 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:24 | Z217012279999 | PORTOBELLO COURT ESTATE | 201106 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 12:24 | 2015-07-02 12:26 | 2015-06-11 12:24 | 2015-09-21 09:40 | -21 | In target
375 PORTOBELLO ROAD - 2015.06.03 | 2015-06-11 12:28 | S217009700001 | PORTOBELLO ROAD (375) | 201107 | Completed | 23e | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 12:28 | 2015-07-02 12:30 | 2015-06-11 12:28 | 2015-09-21 09:39 | -21 | In target
38 EARDLEY CRESCENT - 2015.06.10 | 2015-06-15 11:05 | S217001640001 | EARDLEY CRESCENT (38) | 201469 | Completed | 23b | High | Miscellaneous | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Wendy Stevenson |  | Confirmed / completed. | 2015-06-18 | Fully Completed | Wendy Stevenson | 2015-06-15 11:05 | 2015-07-06 11:06 | 2015-06-15 11:05 | 2015-06-19 17:23 | -21 | In target
38 EARDLEY CRESCENT - 2015.06.10 | 2015-06-15 11:13 | S217001640001 | EARDLEY CRESCENT (38) | 201474 | Completed | 23c | High | Miscellaneous | Is the caretaker undertaking the occupiers tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | Confirmed / completed. | 2015-06-18 | Fully Completed | Wendy Stevenson | 2015-06-15 11:13 | 2015-07-06 11:13 | 2015-06-15 11:13 | 2015-06-19 17:23 | -21 | In target
39 STONELEIGH STREET - 2014.03.06 | 2014-03-13 13:17 | S217010260003 | STONELEIGH STREET (39) | 134450 | Completed |  | Information Only | Inspection Regime | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Martin Barr |  | Noted. We are compiling lists of such properties before looking at lock changes. | 2014-04-17 | Fully Completed |  |  |  | 2014-03-13 13:17 | 2014-04-22 08:18
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 15:27 | S217007860010 | ADAIR ROAD | 201158 | Completed | 8 | High | Inspection Regime | 8In the lower ground floor level external area under the public footpath there is furniture, old mattress dumped and in the residents storage shed area there is also old furniture against the end wall. | I would recommend that all of this dumped rubbish is removed as soon as possible from these two areas. I would recommend that regular inspections should be undertaken of these areas. | Neighbourhood Management | Martin Barr |  | Dumped rubbish was removed | 2015-10-01 | Fully Completed | Martin Barr | 2015-06-11 15:27 | 2015-07-02 15:30 | 2015-06-11 15:27 | 2015-10-16 11:03 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 15:30 | S217007860010 | ADAIR ROAD | 201160 | Completed | 9 | High | Communal Area Storage | In the lower ground floor level external area under the public footpath contractors have left waste and chairs etc where it appears they had a rest area. | I would recommend that all of the waste, the chairs etc are all removed from this area. | Neighbourhood Management | Martin Barr |  | Order with cleaning contractos to remove these items | 2015-10-01 | Fully Completed | Martin Barr | 2015-06-11 15:30 | 2015-07-02 15:32 | 2015-06-11 15:30 | 2015-10-16 11:04 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 15:32 | S217007860010 | ADAIR ROAD | 201163 | Completed | 10 | High | Inspection Regime | There is a charcoal BBQ being stored under the staircase at the ground floor level between flats 2 and 3. | I would recommend that this charcoal BBQ is removed from this area. | Neighbourhood Management | Martin Barr |  | item was remvoed | 2015-10-01 | Fully Completed | Martin Barr | 2015-06-11 15:32 | 2015-07-02 15:34 | 2015-06-11 15:32 | 2015-10-16 11:04 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:05 | S217007860010 | ADAIR ROAD | 201179 | Active | 12b | High | Inspection Regime | A small fence has been erected on the open external balcony between flats 6 and 19, a person cannot now pass along this balcony/walkway. | I would recommend that the fence is removed so that there is passage along this balcony/walkway. | Neighbourhood Management | Martin Barr | 2015-07-02 | The Neighbourhood Officer Felicia and I visted the proeprty on 15/03/2016 and explained to the resident that he needs to remove the gate as it is ab obsruction blocking the walkway access in case of a fire. He asked for a letter to be sent out and this has been sent today giving him until 6th April 2016 to remove the gate otherwise the TMO will remove it. | 2016-03-29 | Partially Completed | Louise Nezandonyi | 2015-06-11 16:05 | 2015-07-02 16:06 | 2015-06-11 16:05 | 2016-03-30 16:29 | -21 | In target | 2015-06-11 16:05 | 2016-04-13 16:14 | Janice Wray
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:09 | S217007860010 | ADAIR ROAD | 201182 | Completed | 23a | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 16:09 | 2015-07-02 16:12 | 2015-06-11 16:09 | 2015-09-21 08:53 | -21 | In target
4 ADAIR ROAD - 2015.06.04 | 2015-06-11 16:14 | S217007860010 | ADAIR ROAD | 201188 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 16:14 | 2015-07-02 16:16 | 2015-06-11 16:14 | 2015-09-21 08:52 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:31 | S217008860001 | HESKETH PLACE (4) | 102566 | Completed | 12a | High | Communal Area Storage | The ground floor cupboard by the rear exit door is not constructed of fire rated materials nor does it have a fire rated door fitted to it. | If this cupboard is to be used for the storage of combustible items then the whole structure should be rebuilt to a minimum of 30 minute fire rated with a FD 30 fire door fitted and this door kept locked shut when not in use. | Neighbourhood Management | Martin Barr | 2013-09-09 | If thisis necessary then should be referred to Response Repairs. If not necessary then ESA should be familiar with requirements on storage here and should monitor storage on regular basis. Job raised for locks to be fitted. Once completed we will arrange a clearance of combustible items Residents are receiving a letter about storage of items in communal areas. This task will not be necessary. Locks are being fitted to the door to prevent unauthorised access and it will not be used for storage. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-19 14:31 | 2013-09-09 14:34 | 2013-08-19 14:31 | 2013-11-08 16:13 | -21 | In target | 2013-08-19 14:31 | 2013-10-22 11:47 | Martin Barr
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:15 | S217008860001 | HESKETH PLACE (4) | 102554 | Completed | 8a | High | Communal Area Storage | On the 1st floor level landing outside flat 6's entrance door there is a pile of small household electrical appliances, kettles, microwave etc. | These items should be removed from the staircase landing and the owner of them informed that the staircase, landings and the corridors are to be kept free of all storage at all times. | Neighbourhood Management | Martin Barr | 2013-09-09 | Items have been removed. A letter is going out to all reisdents to remind them about storage in communal areas, among other things, | 2013-09-09 | Fully Completed | Martin Barr | 2013-08-19 14:15 | 2013-09-09 14:19 | 2013-08-19 14:15 | 2013-10-14 09:14 | -21 | In target
4 HESKETH PLACE - 2013.05.01 | 2013-08-19 14:25 | S217008860001 | HESKETH PLACE (4) | 102563 | Completed | 8b | High | Communal Area Storage | Near to the rear exit door on the ground floor there is a small cupboard which is not constructed of fire rated materials. This cupboard contains items of decorating equipment including dust sheets etc, garden equipment and some cardboard boxes full of combustible items. | As this storage cupboard is not constructed in accordance with the requirements of the Building Regulations, it is not of fire rated materials then all combustible items stored in this cupboard must be removed. Non combustible items could be stored here, garden equipment such as spades and forks etc but a lock should be fitted to each door so that the cupboard can be secured locked shut. Please also see the next item, 12a. | Neighbourhood Management | Martin Barr | 2013-09-09 | Job has been ordered to fit FB locks to the cupboard to prevent residents from storing flammable items Repair target date is 20th November. ESA will check job completion by the end of that week. Cupboards have now had locks fitted, combusitble items will be cleared. Job has been done, this item is now fully completed. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-19 14:25 | 2013-09-09 14:30 | 2013-08-19 14:25 | 2014-01-03 10:23 | -21 | In target | 2013-08-19 14:25 | 2013-11-19 15:30 | Martin Barr
41 CAMBRIDGE GARDENS - 2013.09.18 | 2013-09-18 12:42 | S217008280004 | CAMBRIDGE GARDENS 41 (1-5) | 106584 | Completed | 8a | High | Inspection Regime | In the lower ground floor level cupboard there are folders and books piled up against the installed smoke detector. | All the folders and books piled up against the installed smoke detector in this cupboard should be removed immediately and there should remain a clear area around the installed smoke detector. | Neighbourhood Management | Susan Anim-Boadu |  | The cupboard has been cleared by CY staff. | 2013-09-20 | Fully Completed | Susan Anim-Boadu | 2013-09-18 12:42 | 2013-10-09 12:44 | 2013-09-18 12:42 | 2013-09-23 09:49 | -21 | In target
41 DANVERS STREET -2015.10.06 | 2015-10-21 08:47 | S217001420013 | DANVERS STREET (41) | 222955 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 08:47 | 2015-11-11 08:48 | 2015-10-21 08:47 | 2015-11-16 16:59 | -21 | In target
41 DANVERS STREET -2015.10.06 | 2015-10-21 08:49 | S217001420013 | DANVERS STREET (41) | 222957 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Site visit with RMA Stewart completed to clarify situation with lights at block and ESA clear on what is expected. | 2016-02-02 | Fully Completed | Nicola Rees | 2015-10-21 08:49 | 2015-12-20 08:50 | 2015-10-21 08:49 | 2016-05-03 16:57 | -60 | In target | 2015-10-21 08:49 | 2016-02-21 20:53 | Nicola Rees
43 DANVERS STREET - 2015.10.08 | 2015-10-22 11:42 | S217001420014 | DANVERS STREET (43) | 223406 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-22 11:42 | 2015-11-12 11:43 | 2015-10-22 11:42 | 2015-11-16 16:58 | -21 | In target
43 DANVERS STREET - 2015.10.08 | 2015-10-22 11:43 | S217001420014 | DANVERS STREET (43) | 223412 | Completed | 23c | Medium | Emergency Lighting | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-22 11:43 | 2015-11-12 11:45 | 2015-10-22 11:43 | 2015-11-16 16:59 | -21 | In target
43 UVERDALE ROAD, LONDON SW10 OSN - 2016.06.30 | 2016-06-15 15:48 | S217005650002 | UVERDALE ROAD (43) | 265065 | Completed | 3 | Information Only | Miscellaneous | There were 3 or 4 empty large cardboard boxes in the paved front garden area by the black plastic dust bins. | I would recommend that the caretaker is asked to check that the cardboard boxes have been removed from the paved front garden area by the black plastic dust bins by the bin men. If they have not been removed then they should be removed. | Neighbourhood Management | Nicola Rees | 2016-12-14 | No boxes on site | 2016-09-07 | Fully Completed |  |  |  | 2016-06-15 15:48 | 2016-09-08 14:18
45 DANVERS STREET - 2015.10.06 | 2015-10-21 07:47 | S217001420015 | DANVERS STREET (45) | 222934 | Completed | 8 | Medium | Communal Area Storage | There are black plastic bags in the lower ground floor level cupboard where the water pump and the gas meters are located. It is not known what is in these plastic bags. | I would recommend that the black plastic bags are opened and the contents are looked at, if the contents are private items then the owner should be asked to remove these bags. If the bags contain rubbish and waste they should be removed and disposed of. | Neighbourhood Management | Nicola Rees | 2016-01-18 | Nothing noted during inspection of property at estate inpsection. Keep Moat have confirmed that the work has been completed at this address. Will continue to monitor. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 07:47 | 2015-12-20 07:50 | 2015-10-21 07:47 | 2016-01-19 14:56 | -60 | In target | 2015-10-21 07:47 | 2015-12-08 16:30 | Nicola Rees
45 DANVERS STREET - 2015.10.06 | 2015-10-21 07:52 | S217001420015 | DANVERS STREET (45) | 222938 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 07:52 | 2015-11-11 07:53 | 2015-10-21 07:52 | 2015-11-16 17:00 | -21 | In target
45 DANVERS STREET - 2015.10.06 | 2015-10-21 07:54 | S217001420015 | DANVERS STREET (45) | 222939 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 07:54 | 2015-11-11 07:55 | 2015-10-21 07:54 | 2015-11-16 17:00 | -21 | In target
47 DANVERS STREET - 2015.10.06 | 2015-10-21 14:54 | S217001420016 | DANVERS STREET (47) | 223171 | Completed | 8 | Medium | Communal Area Storage | There are private combustible items storage in the lower ground floor level cupboard which contains the water pump and the gas meters. | I would recommend that all of the combustible storage is removed from this lower ground floor level cupboard. | Neighbourhood Management | Nicola Rees | 2016-01-18 | Estate inspection there was nothing within the combustible storage areas. | 2016-01-18 | Fully Completed | Nicola Rees | 2015-10-21 14:54 | 2015-12-20 14:55 | 2015-10-21 14:54 | 2016-01-19 14:58 | -60 | In target
47 DANVERS STREET - 2015.10.06 | 2015-10-21 15:19 | S217001420016 | DANVERS STREET (47) | 223184 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 15:19 | 2015-11-11 15:20 | 2015-10-21 15:19 | 2015-11-16 16:58 | -21 | In target
47 DANVERS STREET - 2015.10.06 | 2015-10-21 15:20 | S217001420016 | DANVERS STREET (47) | 223186 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 15:20 | 2015-12-20 15:21 | 2015-10-21 15:20 | 2015-11-16 16:59 | -60 | In target
47 UPCERNE ROAD, LONDON SW10 OSF - 2016.05.20 | 2016-05-26 14:40 | S217005620002 | UPCERNE ROAD (47) | 262719 | Active | 12 | Medium | Flat Door | The apartment entrance doors originally had self closing devices fitted. | Please can it be confirmed that the self closing devices to the flat entrance doors of flats B and C are still both connected? If they are not I would recommend that the self closing devices are re-connected or new self closing devices fitted. The Building Regulations requires that flat entrance doors on to internal protected areas should be fitted with self closing devices. Nicola - could the ESA please investigate whether these flat entrance doors are fitted with self-closing devices and if not can an order be raised for them to be installed | Neighbourhood Management | Nicola Rees | 2016-08-26 | Email sent to Darren 02.06.16. Forwarded email to Rahman 06.09.16 |  |  | Cyril Morris | 2016-05-26 14:40 | 2016-07-25 14:41 |  |  | 227 | 227 days overdue
49 DANVERS STREET - 2015.10.6 | 2015-10-21 14:44 | S217001420017 | DANVERS STREET (49) | 223157 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 14:44 | 2015-11-11 14:45 | 2015-10-21 14:44 | 2015-11-16 16:58 | -21 | In target
49 DANVERS STREET - 2015.10.6 | 2015-10-21 14:45 | S217001420017 | DANVERS STREET (49) | 223159 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Visit completed with RMA and the ESA is now clear on how to test the emergency lighting in this block | 2016-02-02 | Fully Completed | Nicola Rees | 2015-10-21 14:45 | 2015-12-20 14:47 | 2015-10-21 14:45 | 2016-05-03 16:58 | -60 | In target | 2015-10-21 14:45 | 2016-02-21 20:55 | Nicola Rees
49 ELM PARK GARDENS - 2015.07.16 | 2015-08-04 09:26 | S217001880021 | ELM PARK GARDENS (49) | 209931 | Active | 23 | High | Emergency Lighting | There is an emergency lighting units/system installed on the staircase landings and in the entrance hall areas of this building. | Can it please be confirmed when the installed emergency lighting system in this building was last serviced, tested and a discharge test of the units batteries undertaken, to the requirements of BS5266. If the last test/service was more that 1 year ago this emergency lighting system should be serviced/tested immediately with any defects etc found rectified and then the system with locations of units etc placed on the contractor's maintenance schedule for future servicing. Are records being kept of all the testing and servicing undertaken? Wendy Stevenson | Neighbourhood Management | Wendy Stevenson |  |  |  |  | Cyril Morris | 2015-08-04 09:26 | 2015-08-25 09:28 |  |  | 562 | 562 days overdue
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 14:55 | S217010567702 | LONGLANDS COURT (49-81) | 103125 | Completed | 8 | Medium | Communal Area Storage | There is some storage in the walkways outside the wire storage cages in the resident's private ground floor storage area. For instance as you walk in the door to the storage area there is an old broken bedroom 5 drawer unit. There are old internal doors lying on top of the cages and there are empty cardboard boxes piled up within some cages. | I would recommend that the residents are asked to remove any items in the walkway areas outside the wire cages. The residents could be asked if they would like to tidy up their cages if a bulk waste collection could be arranged as some items seen were damaged, broken or appear not to have be touched for a very long time. This removal of old items and empty cardboard boxes will reduce the fire loading of the store room. | Neighbourhood Management | Martin Barr |  | Letters have gone out to all residents. Bulk outside the cages has been removed and is removed periodically. The lock on the entry door to the cage area is being changed. Once this happens keys will only be issued to registered users of the cages to control access more effectively. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-21 14:55 | 2013-10-20 15:00 | 2013-08-21 14:55 | 2013-11-08 14:19 | -60 | In target
49-81 LONGLANDS COURT- 2013.03.07 | 2013-08-21 15:15 | S217010567702 | LONGLANDS COURT (49-81) | 103143 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | ESAs complete paper records which are kept and can be checked if required. Project underway to replace these with handheld devices to record checks electronically. |  | Fully Completed | Martin Barr | 2013-08-21 15:15 | 2013-10-20 15:16 | 2013-08-21 15:15 | 2013-11-12 12:19 | -60 | In target
5 BURNABY STREET - 2013.12.31 | 2013-12-31 14:15 | S217000510002 | BURNABY STREET (5) | 122150 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson |  | Keys being pursued as part of initiative with Home Ownership Team and A & R. | 2014-03-17 | Fully Completed | Wendy Stevenson | 2013-12-31 14:15 | 2014-06-29 14:17 | 2013-12-31 14:15 | 2014-03-18 13:59 | -180 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 09:55 | S217001880002 | ELM PARK GARDENS (5) | 102392 | Completed | 8a | High | Communal Area Storage | In the ground floor entrance hall area riser cupboard between flats 21 and 22 there are cardboard boxes of old light fittings, these appear to have been left by contractors. | I would recommend that these cardboard boxes are removed from this cupboard. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc is removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Removed by porters. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 09:55 | 2013-09-09 09:58 | 2013-08-19 09:55 | 2013-09-09 11:39 | -21 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:01 | S217001880002 | ELM PARK GARDENS (5) | 102393 | Completed | 8b | Low | Communal Area Storage | In the roof level cold water tank room there is an old piece of pink carpet on the floor. | Unless there is a reason for this carpet to be located in the roof level cold water tank room I would recommend that it is removed. | Neighbourhood Management | Wendy Stevenson | 2014-02-15 | Removed by porter 4th Sept 2013. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 10:01 | 2014-02-15 10:08 | 2013-08-19 10:01 | 2013-09-11 13:41 | -180 | In target
5 ELM PARK GARDENS - 2013.04.01 | 2013-08-19 10:33 | S217001880002 | ELM PARK GARDENS (5) | 102409 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Porters are completing these tasks and recording outcomes, paper records retained on site. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 10:33 | 2013-09-09 10:47 | 2013-08-19 10:33 | 2013-09-09 11:41 | -21 | In target
5 ELM PARK GARDENS, LONDON SW10 9QQ - 2016.08.08 | 2016-09-21 13:01 | S217001880002 | ELM PARK GARDENS (5) | 271064 | Completed | 8 | Medium | Inspection Regime | In the corner of the ground floor level residents storage area by flats 1 and 2 there is large amount of household items etc not within a caged area just in the walkway. | The household items etc should be removed from the corner of this storage area, in the walkway. Block letter requested from Neighbourhood Officer - 19th Sept. Porters to monitor & ensure area cleared | Neighbourhood Management | Nicola Rees | 2016-12-07 | Email sent to porters for advice on 11.10.16. Checked again 01.12.16 and this was cleared on the second week of October and they are monitoring, | 2016-10-14 | Fully Completed | Nicola Rees | 2016-09-21 13:01 | 2016-11-20 13:03 | 2016-09-21 13:01 | 2016-12-02 16:14 | -60 | In target
5 EXMOOR STREET, LONDON W10 6BB - 2016.05.11 | 2016-05-31 15:51 | S217008700001 | EXMOOR STREET (5) | 263229 | Active | 8 | Information Only | Communal Area Storage | On the landing outside flat 12's entrance door there are children's toys and bikes and a push chair, these items are not presently obstructing the landing nor are they a trip hazard at present. | I would recommend that the caretaker is asked to inspect this area on a regular basis to check that these toys, bikes etc do not obstruct the staircase, become a trip hazard or increase the fire loading of the staircase enclosure. If the staircase landing area does become overloaded with toys, bikes and/or push chairs etc then all items should be removed and a zero tolerance policy should apply to this area with the landing kept completely free of all items. | Neighbourhood Management | Louise Nezandonyi | 2016-11-28
51 - 80 EDENHAM WAY - 2015.06.16 | 2015-06-25 16:04 | S217008650002 | EDENHAM WAY (51-80) | 203417 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the emergency lighting system and also the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets, or computer record kept/sent as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-25 16:04 | 2015-07-16 16:05 | 2015-06-25 16:04 | 2015-09-21 08:49 | -21 | In target
51 AND 53 DANVERS STREET - 2015.10.08 | 2015-10-16 09:39 | S217001420018 | DANVERS STREET (51-53) | 222255 | Completed | 8 | High | Communal Area Storage | 8Outside flat 4's entrance door on the staircase landing there are cardboard boxes of household items. | These cardboard boxes of household items should be removed from the staircase landing. | Neighbourhood Management | Nicola Rees | 2016-04-11 | This has been removed from this area. Confirmed at inspection on | 2016-04-11 | Fully Completed | Nicola Rees | 2015-10-16 09:39 | 2015-11-06 09:40 | 2015-10-16 09:39 | 2016-04-12 16:18 | -21 | In target | 2015-10-16 09:39 | 2015-12-08 16:24 | Nicola Rees
53 AND 55 UPCERNE ROAD, LONDON SW10 OSF - 2016.07.07 | 2016-09-12 12:49 | S217005620005 | UPCERNE ROAD 53 A-C | 270711 | Completed | 3 | Information Only | Inspection Regime | At the time of this assessment there was a large empty cardboard television box and packaging on the public footpath outside of this premises. | I would recommend that the caretaker is asked next time he passes by this property to make certain that cardboard box and the packaging has been removed from the footpath outside of this premises. If it has not then it should be removed. | Neighbourhood Management | Nicola Rees | 2016-10-10 | This was no longer there and had been removed at last site visit. | 2016-12-01 | Fully Completed |  |  |  | 2016-09-12 12:49 | 2016-12-02 16:00
540 KINGS ROAD, LONDON SW10 0UB - 2016.06.20 | 2016-08-31 15:05 | S217002990006 | KINGS ROAD 540 A-D | 270346 | Completed | 8 | Medium | Inspection Regime | In the externally accessed, open fronted lower ground floor level cupboard area, where some of the landlords and dwellings electrical components are located on the wall, there are old push bikes, rusting bike frames and other old and damaged household items. | This area should be tidied up and all of the old and damaged push bikes and other items removed from this area. | Neighbourhood Management | Nicola Rees | 2017-03-01 | This was completed on the 15.09.16 | 2016-09-15 | Fully Completed | Nicola Rees | 2016-08-31 15:05 | 2016-10-30 15:35 | 2016-08-31 15:05 | 2016-10-03 11:59 | -60 | In target
55 GOLBORNE ROAD, LONDON W10 5NR - 2017.01.03 | 2017-02-01 13:38 | S217008770002 | GOLBORNE ROAD (55) | 275214 | Active | 1 | High | Communal Lighting | The landlord's lights in the entrance hall area and on the landings of the staircase are not working. | I would recommend that the landlords lights, the lights covering the common parts of this building are checked and repaired or replaced so that they work correctly and illuminate the staircase, landing and entrance hall area. ESA to check | Neighbourhood Management | Martin Barr | 2017-03-01
55 GOLBORNE ROAD, LONDON W10 5NR - 2017.01.03 | 2017-02-01 13:47 | S217008770002 | GOLBORNE ROAD (55) | 275217 | Active | 8a | High | Storage | There is storage of combustible items in the ground floor entrance hall in the alcove area by the cupboard at the base of the staircase. These items a mattress and furniture as well as a push bike. | All of the combustible items of storage must be removed from the common parts of this building. The residents should be reminder that the staircase enclosure should be maintained free of all items of combustible storage so there is no fuel source for a fire and the fire loading of the staircase is kept as low as possible. The push bike could stay in this area, but if the residents keep storing combustible items in this area then the push bike should also be removed. There will be a "zero tolerance" policy to any storage in the common parts of this building. | Neighbourhood Management | Martin Barr | 2017-03-01
55 GOLBORNE ROAD, LONDON W10 5NR - 2017.01.03 | 2017-02-01 13:49 | S217008770002 | GOLBORNE ROAD (55) | 275219 | Active | 8b | High | Miscellaneous | The ground floor level electrical cupboard has combustible storage in it. | All storage should be removed from this landlords electrical cupboard and the doors secured locked shut. | Neighbourhood Management | Martin Barr | 2017-03-01
55 GOLBORNE ROAD, LONDON W10 5NR - 2017.01.03 | 2017-02-01 13:52 | S217008770002 | GOLBORNE ROAD (55) | 275220 | Active | 8c | Information Only | Storage | There is a cupboard at the base of this staircase off the ground floor level entrance hall area. This cupboard is being used as a residents private storage cupboard. | Does the TMO know that this cupboard is now being used as a resident's private storage cupboard? | Neighbourhood Management | Martin Barr | 2018-02-01
55 GOLBORNE ROAD, LONDON W10 5NR - 2017.01.03 | 2017-02-01 14:03 | S217008770002 | GOLBORNE ROAD (55) | 275225 | Active | 23 | Medium | Inspection Regime | Caretaker/Estates Services Assistants(ESAs) checks and inspections of this building. | Can it be confirmed that the caretakers/ESAs are undertaking the tasks as per the caretakers check list in this building? This is because of the amount of combustible storage in the residential entrance hall area of this building. | Neighbourhood Management | Martin Barr | 2017-04-05
55 STADIUM STREET - 2015.09.22 | 2015-10-05 10:31 | S217005190006 | STADIUM STREET (55) | 219928 | Completed | 12 | Medium | Miscellaneous | There is a mortice lock fitted to the entrance door of this building as well as the yale lock. | Can it be confirmed that the mortice lock fitted to the communal entrance door has been disabled so that it cannot be locked. If this mortice lock is functional then I would recommend that a thumb turn device is fitted on the inner face of the door so that the entrance door can be opened from the entrance hall side without the use of a key. Alternatively the mortice lock could disabled or removed completely and the holes in the door suitably filled in for security reasons. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Lock change etc week beg 25.01.16 | 2016-02-04 | Fully Completed | Nicola Rees | 2015-10-05 10:31 | 2015-12-04 10:32 | 2015-10-05 10:31 | 2016-02-08 16:24 | -60 | In target | 2015-10-05 10:31 | 2016-02-14 16:24 | Janice Wray
57 DANVERS STREET - 2015.10.06 | 2015-10-21 07:41 | S217001420020 | DANVERS STREET (57) | 222931 | Completed | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within the entrance hall/lobby area of this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 07:41 | 2015-11-11 07:42 | 2015-10-21 07:41 | 2015-11-16 16:57 | -21 | In target
57 DANVERS STREET - 2015.10.06 | 2015-10-21 07:42 | S217001420020 | DANVERS STREET (57) | 222932 | Completed | 23c | Medium | Emergency Lighting | Caretaker testing and inspections of the emergency lighting unit and the buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Nicola Rees |  | This is being completed. | 2015-11-13 | Fully Completed | Nicola Rees | 2015-10-21 07:42 | 2015-11-11 07:43 | 2015-10-21 07:42 | 2015-11-16 18:27 | -21 | In target | 2015-10-21 07:42 | 2015-11-20 18:26 | Janice Wray
57AND 59 UPCERNE ROAD, LONDON SW10 OSF - 2016.11.24 | 2016-12-12 10:05 | S217005620007 | UPCERNE ROAD (57-59) | 273692 | Active | 0 | Information Only | Miscellaneous | The TMO and the ESAs/caretakers do not have keys to the locks of this buildings residential entrance door. | I would recommend that keys for the locks fitted to this building's residential entrance door are obtained from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2017-12-11
57AND 59 UPCERNE ROAD, LONDON SW10 OSF - 2016.11.24 | 2016-12-12 10:25 | S217005620007 | UPCERNE ROAD (57-59) | 273700 | Active | 23b | High | Inspection Regime | It is not known if any ESA's/caretaker testing and inspections of the installed emergency lighting units and the buildings structural items are being undertaken? The TMO does not have keys for the locks on this buildings residential entrance door. | Can it be confirmed that the ESA's/caretaker(s) are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Nicola Rees | 2017-01-09 |  |  |  | Cyril Morris | 2016-12-12 10:25 | 2017-01-02 10:26 |  |  | 66 | 66 days overdue
58 ELM PARK GARDENS - 2014.04.15 | 2014-04-22 13:55 | S217001880026 | ELM PARK GARDENS (58) | 140532 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier's tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Wendy Stevenson |  |  | 2014-05-09 | Fully Completed | Wendy Stevenson | 2014-04-22 13:55 | 2014-05-13 13:56 | 2014-04-22 13:55 | 2014-05-12 14:44 | -21 | In target
6 ASHBURNHAM ROAD | 2013-12-31 14:30 | S217000190002 | ASHBURNHAM ROAD (6) | 122161 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have a key to the lock on the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the communal front entrance door lock of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson | 2014-06-29 |  | 2014-01-10 | Fully Completed |  |  |  | 2013-12-31 14:30 | 2014-01-13 12:11
6 DAMER TERRACE, LONDON SW10 ONZ - 2015.12.22 | 2016-02-15 13:10 | S217001400003 | DAMER TERRACE (6) | 243444 | Active | 0 | Medium | Miscellaneous | The caretaker does not have a key to the mortice lock fitted to the communal front entrance door of this building. The TMO have keys for the yale lock though. | I would recommend that a key for the mortice lock fitted to this buildings communal front entrance door is obtained from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-03-14 | Email sent to Gary to ask residents for key 28.04.16. Gary has informed that this is a Banham lock that may need to be addressed and replaced. |  | Partially Completed | Cyril Morris | 2016-02-15 13:10 | 2016-04-15 13:13 |  |  | 328 | 328 days overdue
6 DAMER TERRACE, LONDON SW10 ONZ - 2015.12.22 | 2016-02-15 13:30 | S217001400003 | DAMER TERRACE (6) | 243460 | Active | 8 | High | Communal Area Storage | There are 2 storage cupboards at the lower ground floor level of this building, both of these cupboards contain bags of waste and rubbish as well as old and broken furniture etc. | I would recommend that these two cupboards are tidied up and all old and unwanted items and the bags of rubbish/waste etc are removed. | Neighbourhood Management | Nicola Rees | 2016-03-15 |  |  |  | Cyril Morris | 2016-02-15 13:30 | 2016-03-07 13:32 |  |  | 367 | 367 days overdue
6 DAMER TERRACE, LONDON SW10 ONZ - 2015.12.22 | 2016-02-15 13:32 | S217001400003 | DAMER TERRACE (6) | 243462 | Active | 12 | High | Responsive Item | There is a mortice lock fitted to the communal entrance door of this building as well as a yale lock, this is for security reasons. Both the yale and the mortice lock are used to secure this building's entrance door. | I would strongly recommend that a thumb turn is fitted on the inside face of the mortice lock so that this lock on the communal entrance door can be opened without the use of a key as is the case with the yale lock. Nicola - Alex advises that Maria Areas can arrange for a deadlock which is compatible with a thumb turn on the inside if this is required. | Neighbourhood Management | Nicola Rees | 2016-03-15 | Email sent to reporting repairs 28.04.16 |  | Partially Completed | Cyril Morris | 2016-02-15 13:32 | 2016-03-07 13:34 |  |  | 367 | 367 days overdue
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:42 | S217009920001 | RUNCORN PLACE (6) | 102643 | Completed | 8 | High | Communal Area Storage | On the first floor level landing outside flat 4's entrance door there are decorating dust sheets, cardboard boxes which appear to have been there a while and 4 carrier bags of household rubbish and two black bin bags. | I would recommend that the occupant of this flat is reminded of the "no items in the staircase policy and that all the boxes and bags are removed from this landing. | Neighbourhood Management | Susan Anim-Boadu | 2013-09-09 | Susan - is this an area that you manage? If not please advise asap. The items had been removed by the resident. | 2013-06-18 | Fully Completed | Susan Anim-Boadu | 2013-08-19 15:42 | 2013-09-09 15:44 | 2013-08-19 15:42 | 2013-08-20 15:58 | -21 | In target
6 RUNCORN PLACE - 2013.03.01 | 2013-08-19 15:51 | S217009920001 | RUNCORN PLACE (6) | 102649 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Susan Anim-Boadu | 2013-09-16 | Susan - can you please just confirm the frequency of the inspections in this block The caretakers inspect the building on a daily basis. | 2013-08-19 | Fully Completed | Susan Anim-Boadu | 2013-08-19 15:51 | 2013-10-18 15:54 | 2013-08-19 15:51 | 2014-01-08 13:42 | -60 | In target | 2013-08-19 15:51 | 2014-01-14 13:40 | Janice Wray
6 STANLEY GARDENS - 2013.05.01 | 2013-08-15 10:21 | S217010240001 | STANLEY GARDENS (6) | 101921 | Completed | 8 | High | Communal Area Storage | In the ground floor entrance hall area there is a unit of furniture with the drawers full of plastic bin bags and old newspapers etc, a push bike with a flat tyre which looks like it has not been moved or used in years and the basket on the front has rolls of bin bags in it, there are also large plant pots full of free magazines and leaflets. Also step ladders. | I would recommend that all these items are removed from this entrance hall area, if the item of furniture is to remain so that post etc can be placed on it all the drawers must be empty. If the push bike is not regularly used it should be removed as the entrance hall area should not be used for long term push bike storage. | Neighbourhood Management | Martin Barr | 2013-09-05 | Letter to residents being delivered. Clearance will be arranged after 21st October giving residents time to remove any items they wish to keep. Order for clearance arranged. Area to be monitored for build up. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-15 10:21 | 2013-09-05 10:31 | 2013-08-15 10:21 | 2013-11-08 14:05 | -21 | In target | 2013-08-15 10:21 | 2013-10-22 11:41 | Martin Barr
6 STANLEY GARDENS, LONDON W11 2ND - 2017.01.30 | 2017-02-07 10:08 | S217010240001 | STANLEY GARDENS (6) | 275387 | Active | 8 | High | Inspection Regime | In the ground floor entrance hall area of this building there is a unit of furniture with the drawers full of plastic bin bags, plastic bags of toilet rolls and books. | The unit of furniture can remain but all the drawers should be emptied out and the drawers kept empty. Alternatively the complete item of furniture can be removed from the entrance hall area. | Neighbourhood Management | Martin Barr | 2017-03-07
60 ELSHAM ROAD, LONDON W14 8HD - 2017.01.12 | 2017-01-24 13:52 | S217006350007 | ELSHAM ROAD (60) | 274921 | Active | 23a | High | Emergency Lighting | Are the occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? Along with the other caretakers/Estates Services Assistants (ESAs) checks. | Occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing along with the other caretakers/ESAs checks. | Neighbourhood Management | Nicola Rees | 2017-02-21
60 NEVERN SQUARE, LONDON W10 6HQ- 2015.12.15 | 2016-06-06 16:46 | S217003640001 | NEVERN SQUARE (60) | 264072 | Active | 23b | High | Inspection Regime | It is not known if the caretaker is undertaking the monthly occupiers checks and tests of the installed emergency lighting units. | Can it please be confirmed that the caretaker is undertaking the monthly occupiers checks and tests of the installed emergency lighting units with records being kept as proof of testing? | Neighbourhood Management | Nicola Rees | 2016-07-05 |  |  |  | Cyril Morris | 2016-06-06 16:46 | 2016-06-27 16:48 |  |  | 255 | 255 days overdue
60 NEVERN SQUARE, LONDON W10 6HQ- 2015.12.15 | 2016-06-06 16:48 | S217003640001 | NEVERN SQUARE (60) | 264073 | Active | 23c | Medium | Inspection Regime | Caretaker inspections of this buildings structure. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed electronic sheet kept as a record. | Neighbourhood Management | Nicola Rees | 2016-08-30 |  |  |  | Cyril Morris | 2016-06-06 16:48 | 2016-08-05 16:50 |  |  | 216 | 216 days overdue
61 GOLBORNE ROAD, LONDON W10 5NR - 2016.01.07 | 2016-02-17 12:42 | S217008770004 | GOLBORNE ROAD (61) | 244006 | Active | 1b | High | Miscellaneous | The electrical cupboard by the residential communal entrance door is not locked shut. | This electrical cupboard should be locked shut to stop un authorised access to this electrical cupboard. Fit GERDA Lock ?? Louise - please confirm which lock | Neighbourhood Management | Louise Nezandonyi | 2016-03-16 |  |  |  | Cyril Morris | 2016-02-17 12:42 | 2016-03-09 12:43 |  |  | 365 | 365 days overdue
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 15:57 | S217002110008 | FINBOROUGH ROAD (62) | 102928 | Completed | 3a | High | Communal Area Storage | Next to the recycling bins on the right hand side of this building there are soft chairs from a 3 piece suite and other items of furniture. | I would recommend that this external recycling area is tidied up and all the furniture etc removed, so that these items are not used as a fuel source by an arsonist. The caretaker should be asked to report back immediately that any large items dumped here so that they can be removed. If this continues to be a problem I would recommend that the recycling bins are placed in the yard areas outside the refuse chute bin rooms. | Neighbourhood Management | Wendy Stevenson | 2013-09-10 | Items have been removed. Monitoring will take place and recycling provision reviewed if necessary. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-20 15:57 | 2013-09-10 15:58 | 2013-08-20 15:57 | 2013-09-09 12:07 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:00 | S217002110008 | FINBOROUGH ROAD (62) | 102933 | Completed | 8a | High | Communal Area Storage | In the electrical cupboard of the left hand side central staircase at the lower ground floor level there are cardboard boxes of empty plastic bottles and plastic containers. Along with a wheelbarrow and building materials. | The plastic containers and the boxes of plastic bottles should be removed from this cupboard immediately. It is not known why the building materials are stored here along with the wheelbarrow as this is an electrical cupboard so these items should also be removed. | Neighbourhood Management | Wendy Stevenson | 2013-09-10 | Removed as per ESA Brian Manrique. | 2013-09-10 | Fully Completed | Wendy Stevenson | 2013-08-20 16:00 | 2013-09-10 16:01 | 2013-08-20 16:00 | 2013-09-11 13:28 | -21 | In target
62 FINBOROUGH ROAD - 2013.07.05 | 2013-08-20 16:51 | S217002110008 | FINBOROUGH ROAD (62) | 102974 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the building being undertaken along with the other items on the caretakers checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-04 | ESA does not know how to complete the lighting checks. There are no fire extinguishers on site. Other visual isnpections and tests are done, the results recorded and paperwork retained. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-20 16:51 | 2013-09-10 16:52 | 2013-08-20 16:51 | 2013-09-09 12:08 | -21 | In target
62 FINBOROUGH ROAD, LONDON SW10 9EF - 2016.08.25 | 2017-01-24 15:58 | S217002110008 | FINBOROUGH ROAD (62) | 274936 | Active | 1 | High | Miscellaneous | There is a yellow electrical cable which runs from the lower ground floor electrical cupboard between flats 6 and 8, through the transom light area above this cupboard out through the louvered vents above the exit door and then clipped to and along the rear walls of the gardens of these flats. This cable has bulkhead lights attached to it but is cut as it passes over one of the garden gates. | This yellow electrical cable is plugged into a 3 pin socket within the electrical cupboard so it is not a fixed external lighting system and because the cable is cut it does not work. I would recommend that the reason for this cable and the lights is investigated and that they are removed. That is unless this is meant to be a permanent external lighting system and if this is the case it should be wired in correctly and cover the whole of the exterior rear walkway and just not part of it. Could the ESA investigate please | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 15:58 | 2017-02-14 16:02 |  |  | 23 | 23 days overdue
62 FINBOROUGH ROAD, LONDON SW10 9EF - 2016.08.25 | 2017-01-24 16:02 | S217002110008 | FINBOROUGH ROAD (62) | 274938 | Active | 3a | High | Inspection Regime | Next to the recycling bins on the right hand side of this building there are bulk waste items and household furniture etc. | I would recommend that this external recycling area is tidied up and all the furniture etc removed, so that these items are not used as a fuel source by an arsonist. The caretaker should be asked to report back immediately that any large items dumped here so that they can be removed. If this continues to be a problem I would recommend that the recycling bins are placed in the yard areas outside the bin rooms. Presumably this has now been removed? | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 16:02 | 2017-02-14 16:06 |  |  | 23 | 23 days overdue
62 FINBOROUGH ROAD, LONDON SW10 9EF - 2016.08.25 | 2017-01-25 11:12 | S217002110008 | FINBOROUGH ROAD (62) | 274996 | Active | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections being undertaken within this building? This includes the monthly emergency lighting checks along with the other items on the caretakers checklist, with records kept? | Monthly occupier testing and inspections of the emergency lighting and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2017-02-28 |  |  |  | Cyril Morris | 2017-01-25 11:12 | 2017-02-15 11:14 |  |  | 22 | 22 days overdue
63 ELSHAM ROAD, LONDON W14 8HD - 2017.01.03 | 2017-01-24 11:48 | S217006350008 | ELSHAM ROAD (63) | 274913 | Active | 23a | High | Inspection Regime | Are the occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? Along with the other caretakers/Estates Services Assistants (ESAs) checks. | Occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing along with the other caretakers/ESAs checks. | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 11:48 | 2017-02-14 11:50 |  |  | 23 | 23 days overdue
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 14:52 | S217002110002 | FINBOROUGH ROAD (63) | 189149 | Completed | 8a | High | Communal Area Storage | In the 2nd floor level corridor between flats 12 and 14 there was a dishwasher. | This dishwasher should be removed from this corridor and the building. | Neighbourhood Management | Jimmy Lemos |  | clear | 2015-04-27 | Fully Completed | Jimmy Lemos | 2015-03-20 14:52 | 2015-04-10 15:07 | 2015-03-20 14:52 | 2015-05-06 12:51 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:08 | S217002110002 | FINBOROUGH ROAD (63) | 189157 | Completed | 8b | Medium | Communal Area Storage | In the external yard area outside of the bin store there was an old television, a 3 piece suite, settee and chairs, along with some broken pieces of wooden furniture. | I would recommend that these items are removed from this yard area outside of the bin room. | Neighbourhood Management | Jimmy Lemos |  | bulk collection raised | 2015-03-31 | Fully Completed | Jimmy Lemos | 2015-03-20 15:08 | 2015-05-19 15:08 | 2015-03-20 15:08 | 2015-05-06 12:54 | -60 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:21 | S217002110002 | FINBOROUGH ROAD (63) | 189168 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Jimmy Lemos |  | done | 2015-03-30 | Fully Completed | Jimmy Lemos | 2015-03-20 15:21 | 2015-04-10 15:22 | 2015-03-20 15:21 | 2015-05-06 12:53 | -21 | In target
63 FINBOROUGH ROAD - 2015.03.05 | 2015-03-20 15:23 | S217002110002 | FINBOROUGH ROAD (63) | 189170 | Completed | 23d | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Jimmy Lemos |  |  | 2015-03-30 | Fully Completed | Jimmy Lemos | 2015-03-20 15:23 | 2015-05-19 15:23 | 2015-03-20 15:23 | 2015-05-06 12:52 | -60 | In target
65 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-03-23 16:08 | S217008660001 | ELGIN CRESCENT 65 (1-8) | 250817 | Active | 8a | High | Communal Area Storage | There is some private storage in the roof space of this building. | I would recommend that all the private storage is removed from this roof space area. | Neighbourhood Management | Louise Nezandonyi | 2016-04-20 |  |  |  | Cyril Morris | 2016-03-23 16:08 | 2016-04-13 16:12 |  |  | 330 | 330 days overdue
65 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-03-23 16:33 | S217008660001 | ELGIN CRESCENT 65 (1-8) | 250837 | Active | 12a | High | Flat Door | There is no access to the corridor/lobby area outside flats 2 and 3 because the lobby door is locked shut so it is not known if these two flat entrance doors have been replaced with Manse doors or not. Or if the glazing in the transom areas above these doors has been replaced, the transom light areas above flats 4 and 5 were not replaced. | Can it please be confirmed that the flats entrance doors of flats 2 and 3 have been replaced with Manse doors? Have the transom light areas above these doors been replaced or not? If they have not as per the transom light areas above flats 4 and 5's doors then can it be confirmed that these glazed areas are still fire rated and in a good condition? Does the ESA have keys to this door? Can he confirm the door and transoms are fire-rated? | Neighbourhood Management | Louise Nezandonyi | 2016-04-20 |  |  |  | Cyril Morris | 2016-03-23 16:33 | 2016-04-13 16:35 |  |  | 330 | 330 days overdue
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:23 | S217002110003 | FINBOROUGH ROAD (65) | 189120 | Completed | 8 | Medium | Communal Area Storage | In the external yard area outside of the bin store there was an old fridge/freezer, a settee and some broken up bedroom furniture. | I would recommend that these items are removed from this yard area outside of the bin room. | Neighbourhood Management | Jimmy Lemos |  | CLEAR | 2015-04-13 | Fully Completed | Jimmy Lemos | 2015-03-20 14:23 | 2015-05-19 14:25 | 2015-03-20 14:23 | 2015-05-06 12:55 | -60 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:40 | S217002110003 | FINBOROUGH ROAD (65) | 189139 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Jimmy Lemos |  |  | 2015-03-31 | Fully Completed | Jimmy Lemos | 2015-03-20 14:40 | 2015-04-10 14:41 | 2015-03-20 14:40 | 2015-05-06 12:55 | -21 | In target
65 FINBOROUGH ROAD - 2015.02.05 | 2015-03-20 14:43 | S217002110003 | FINBOROUGH ROAD (65) | 189140 | Completed | 23d | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Jimmy Lemos |  | DONE | 2015-03-30 | Fully Completed | Jimmy Lemos | 2015-03-20 14:43 | 2015-05-19 14:44 | 2015-03-20 14:43 | 2015-05-06 12:54 | -60 | In target
65 STADIUM STREET - 2015.09.22 | 2015-10-05 10:35 | S217005190009 | STADIUM STREET (65) | 219933 | Completed | 208286 | Information Only | Miscellaneous | The caretaker does not have any keys to the communal front entrance door of this building. There is no access control system, trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Lock change completed on week beginning 25.01.16. | 2016-02-04 | Fully Completed |  |  |  | 2015-10-05 10:35 | 2016-02-08 16:26 |  |  | 2015-10-05 10:35 | 2016-02-14 16:25 | Janice Wray
67 ELGIN CRESCENT, LONDON W11 2JE - 2016.02.02 | 2016-04-19 15:07 | S217008660002 | ELGIN CRESCENT 67 (1-10) | 255268 | Active | 0 | Information Only | Inspection Regime | The occupant of flat number 1 has erected a lean too/come out building at the rear of their flat. This structure appears to be a DIY construction and not very structurally sound from a visual inspection of it. This construction has the potential to increase the fire loading of the area and the vertical fire spread depending on what it is being used for. TENANTED | I would recommend that a surveyor is asked to check this structure and a report on its construction compiled. This should include any fire loading issues along with any vertical and horizontal fire spread implications. Also it affects the access to the upper floor level windows at the rear of the property. | Neighbourhood Management | Louise Nezandonyi | 2016-05-17
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:32 | S217001880006 | ELM PARK GARDENS (67) | 102458 | Completed | 8a | High | Communal Area Storage | On the flat/lift lobby area of flats 34 to 36 there is a drinks cabinet/sideboard this contains glasses and crockery etc. | I would recommend that this item of furniture is removed from the flat/lift lobby area. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Porter Martin Walsh attempted to speak to the resident on 4th Sept but she was not home (Flat 37) and so he left a sticker requesting removal. The resident objected, speaking to the Neighbourhood Officer Nicola Rees. Nicola has explained to the resident that removal is essential because of fire safety. However, the resident has challenged the instruction to remove the item, on the basis that the cabinet has not posed a problem at previous FRA inspections. Item removed 23rd Sept 2013. | 2013-09-23 | Fully Completed | Wendy Stevenson | 2013-08-19 12:32 | 2013-09-09 12:36 | 2013-08-19 12:32 | 2014-01-08 10:23 | -21 | In target | 2013-08-19 12:32 | 2014-01-14 10:22 | Janice Wray
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:36 | S217001880006 | ELM PARK GARDENS (67) | 102462 | Completed | 8b | High | Communal Area Storage | In the 5th floor level riser cupboard between flats 16 and 17 there are cardboard boxes of Christmas decorations, boxes of clothes and pictures and a mirror. | I would recommend that these personal items are removed from this riser cupboard. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Items removed by the Porter, Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:36 | 2013-09-09 12:38 | 2013-08-19 12:36 | 2013-09-09 11:49 | -21 | In target
67 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 13:57 | S217001880006 | ELM PARK GARDENS (67) | 102538 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and the fire extinguishers in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system and the fire extinguishers in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Fire extinguishers have been removed. All checks are being done, results recorded and retained. Porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 13:57 | 2013-09-09 14:00 | 2013-08-19 13:57 | 2013-09-09 12:25 | -21 | In target
68 FLOOD STREET, LONDON SW3 5TE -2016.03.15 | 2016-04-20 10:18 | S217002130001 | FLOOD STREET (68) | 255398 | Completed | 23f | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and emergency lighting units. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building including monthly testing of the emergency lighting units, with the completed sheets kept as a record and proof of testing. | Neighbourhood Management | Nicola Rees | 2016-05-25 | Yes this is being completed but we have required there to be cover as ESA has recently been on long term sick, | 2016-06-02 | Fully Completed | Nicola Rees | 2016-04-20 10:18 | 2016-05-11 10:20 | 2016-04-20 10:18 | 2016-06-03 12:52 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:15 | S217010200001 | ST QUINTIN AVENUE (69) | 199066 | Completed | 1c | Information Only | Miscellaneous | For your infor-mation The lights in the ground floor level entrance hall area are on 24 hours a day. | Are these light meant to be on a timer or sensor? If so is this device working correctly? | Neighbourhood Management | Kamran Hye |  |  | 2015-05-28 | Fully Completed |  |  |  | 2015-05-28 11:15 | 2015-05-29 13:08
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:18 | S217010200001 | ST QUINTIN AVENUE (69) | 199067 | Completed | 3 | High | Miscellaneous | The fire fighter entry over ride device fitted next to this buildings entrance door could not be tested as the "drop key" would not fit in the hole of the device. This over ride devices allow the Fire and Rescue Service to access the building in an emergency without the use of a key. | I would recommend that the aperture size of the fire fighters over ride device is changed so that a normal size drop key can be used to release the door locking mechanism. Could the ESA please investigate | Neighbourhood Management | Martin Barr |  | This has been reported to repairs team to fix, order number 201529658 | 2015-09-16 | Fully Completed | Martin Barr | 2015-05-28 11:18 | 2015-06-18 11:19 | 2015-05-28 11:18 | 2015-09-21 14:53 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:28 | S217010200001 | ST QUINTIN AVENUE (69) | 199073 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-28 11:28 | 2015-06-18 11:29 | 2015-05-28 11:28 | 2015-09-21 09:42 | -21 | In target
69 ST QUINTINS AVENUE - 2015.05.13 | 2015-05-28 11:34 | S217010200001 | ST QUINTIN AVENUE (69) | 199076 | Completed | 23c | High | Inspection Regime | It appears that caretaker testing and inspections of the portable fire extinguishers, the buildings structure etc are not being undertaken | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-28 11:34 | 2015-06-18 11:35 | 2015-05-28 11:34 | 2015-09-21 09:41 | -21 | In target
7 DAMER TERRACE, LONDON SW10 ONZ - 2016.06.20 | 2016-09-02 12:28 | S217001400004 | DAMER TERRACE (7) | 270451 | Active | 0 | Information Only | Inspection Regime | The caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key for both of the locks fitted to the communal front entrance door of this building is obtained from a resident, so that access can be gained by the TMO at any time. Nicola Rees | Neighbourhood Management | Nicola Rees | 2017-09-01
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:10 | S217001880003 | ELM PARK GARDENS (7) | 102451 | Completed | 8 | High | Communal Area Storage | In the second floor level riser cupboard between flats 7 and 8 there are cardboard boxes of old light fittings, these appear to have been left by contractors. | I would recommend that these cardboard boxes are removed from this cupboard. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc is removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All items removed. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:10 | 2013-09-09 12:17 | 2013-08-19 12:10 | 2013-09-09 11:42 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:37 | S217001880003 | ELM PARK GARDENS (7) | 102463 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All being done by the porters on site, results recorded and retained. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:37 | 2013-09-09 12:38 | 2013-08-19 12:37 | 2013-09-09 11:43 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:50 | S217001880008 | ELM PARK GARDENS (93) | 102467 | Completed | 8a | High | Inspection Regime | On the staircase landing on the floor level of flats 32 to 34 there is an upholstered chair, this chair is reducing the width of the staircase and could be an obstruction and trip hazard. On the staircase landing above this one there is a small table. | This chair and the table should be removed from these staircase landings immediately. The staircases should be kept free of items of furniture and combustible storage. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Items removed via porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:50 | 2013-09-09 12:52 | 2013-08-19 12:50 | 2013-09-09 11:50 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:52 | S217001880008 | ELM PARK GARDENS (93) | 102470 | Completed | 8b | High | Inspection Regime | In the 3rd floor level riser cupboard between flats 30 and 31 there is a large mirror being stored and a cardboard box. | I would recommend that these items are removed from this cupboard. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Items removed via porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:52 | 2013-09-09 12:53 | 2013-08-19 12:52 | 2013-09-09 11:51 | -21 | In target
7 ELM PARK GARDENS - 2013.05.01 | 2013-08-19 12:54 | S217001880008 | ELM PARK GARDENS (93) | 102471 | Completed | 8c | High | Inspection Regime | In the 5th floor level riser cupboard between flats 36 and 37 there are cardboard boxes of old telephones and some old light fittings. | I would recommend that these cardboard boxes are removed from this cupboard. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc is removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Items removed via porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:54 | 2013-09-09 12:55 | 2013-08-19 12:54 | 2013-09-09 11:52 | -21 | In target
7 ELM PARK GARDENS, LONDON SW10 9QG - 2016.08.08 | 2016-08-31 11:26 | S217001880003 | ELM PARK GARDENS (7) | 270304 | Completed | 12b | High | Responsive Item | The refuse chute hopper flap/opening does not shut fully in the staircase of flats 21 to 40 on the half landing between the 5th and 6th floor levels. | This refuse chute hopper flap/opening should be repaired or replaced so that it shuts fully. Asked Porters to confirm is work ordered | Neighbourhood Management | Nicola Rees | 2016-09-27 | This has been repaired and confirmed by porters under reference 201622614. | 2016-09-06 | Fully Completed | Nicola Rees | 2016-08-31 11:26 | 2016-09-21 11:29 | 2016-08-31 11:26 | 2016-09-07 16:09 | -21 | In target
70 PHILBEACH GARDENS - 2014.05.01 | 2014-05-13 13:44 | S217006630004 | PHILBEACH GARDENS (70) | 143511 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson |  | Confirmed that this testing / inspecting / recording is being done monthly. | 2014-05-14 | Fully Completed | Wendy Stevenson | 2014-05-13 13:44 | 2014-06-03 13:46 | 2014-05-13 13:44 | 2014-05-15 08:05 | -21 | In target
70 PHILBEACH GARDENS - 2014.05.01 | 2014-05-13 13:46 | S217006630004 | PHILBEACH GARDENS (70) | 143512 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker (s) are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson |  | Confirmed - being done monthly. | 2014-05-14 | Fully Completed | Wendy Stevenson | 2014-05-13 13:46 | 2014-06-03 13:48 | 2014-05-13 13:46 | 2014-05-15 08:06 | -21 | In target
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:47 | S217010350001 | TAVISTOCK ROAD (70-80) | 104403 | Completed | 8a | High | Communal Area Storage | The residents store rooms on each floor level were at the time of this assessment piled high with the old carpet removed from the corridors etc. | All these old carpet should be removed from these residents stores, I would recommend that the store rooms are also tidied up at the same time. | Neighbourhood Management | Martin Barr |  | ESA will inspect the area on Monday 14th October and order clearance based on the amount of material left. Clearance of items has been ordered. | 2013-10-11 | Fully Completed | Martin Barr | 2013-09-02 12:47 | 2013-09-23 12:48 | 2013-09-02 12:47 | 2013-11-12 12:28 | -21 | In target | 2013-09-02 12:47 | 2013-10-22 13:11 | Martin Barr
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 12:48 | S217010350001 | TAVISTOCK ROAD (70-80) | 104404 | Completed | 8b | High | Communal Area Storage | In the roof level cold water tank room there is a lot of contractors waste. | I would recommend that all the contractors waste is removed from the roof level cold water tank room. | Neighbourhood Management | Martin Barr |  | ESA will inspect the area on Monday 14th October and order clearance based on the amount of material left. Order has been raised for clearance. | 2013-10-11 | Fully Completed | Martin Barr | 2013-09-02 12:48 | 2013-09-23 12:49 | 2013-09-02 12:48 | 2013-11-12 12:28 | -21 | In target | 2013-09-02 12:48 | 2013-10-22 13:13 | Martin Barr
70 TAVISTOCK ROAD -2013.07.22 | 2013-09-02 16:19 | S217010350001 | TAVISTOCK ROAD (70-80) | 104500 | Completed | 23d | High | Inspection Regime | There are no records of the monthly occupiers tests and inspections of the emergency lighting system, fire extinguishers etc , these tests are being undertaken by the caretaker according to the manager. | I would recommend that copies of the caretakers checklist are kept on site so that it can be proven that these tests and checks are being undertaken. | Neighbourhood Management | Martin Barr | 2017-03-10 | ESA Checklists are currently completed manually. A handheld system is being developed whereby the checklists will be electronically recorded and accessible at all TMO locations through the EDM system. Until that time the checklists can be made available if needed. Electronic PDA recording of monthly inspection now in place | 2017-03-10 | Fully Completed | Martin Barr | 2013-09-02 16:19 | 2013-09-23 16:21 | 2013-09-02 16:19 | 2017-03-13 12:30 | -21 | In target | 2013-09-02 16:19 | 2017-03-17 12:29 | Janice Wray
75 ELSHAM ROAD, LONDON W14 8HH - 2017.01.12 | 2017-01-24 10:45 | S217006350011 | ELSHAM ROAD (75) | 274904 | Active | 8 | High | Inspection Regime | In the entrance hall area outside flat B there was a computer table and 2 other items of furniture being stored. | This furniture/storage should be removed from the entrance hall area outside flat B's entrance door. | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 10:45 | 2017-02-14 10:46 |  |  | 23 | 23 days overdue
75 ELSHAM ROAD, LONDON W14 8HH - 2017.01.12 | 2017-01-24 10:47 | S217006350011 | ELSHAM ROAD (75) | 274905 | Active | 23a | High | Inspection Regime | Are the occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? Along with the other caretakers/Estates Services Assistants (ESAs) checks. | Occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing along with the other caretakers/ESAs checks. | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 10:47 | 2017-02-14 10:48 |  |  | 23 | 23 days overdue
76 LOTS ROAD, LONDON SW10 OQD - 2016.05.19 | 2016-05-26 11:44 | S217003270008 | LOTS ROAD (76) | 262633 | Completed | 00 | Information Only | Inspection Regime | The caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted, so any visitor is dependant on an occupant opening the communal front entrance door. | I would recommend that keys for the three locks fitted to the communal front entrance door of this building are obtained from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-08-25 | This one is a Banham lock. Can we get some information from A+R around the next steps for progressing these? Thanks | 2016-09-30 | Fully Completed |  |  |  | 2016-05-26 11:44 | 2016-10-12 21:18 |  |  | 2016-05-26 11:44 | 2016-10-18 21:17 | Janice Wray
77 ELSHAM ROAD, LONDON W14 8HH - 2017.01.12 | 2017-01-24 11:05 | S217006350012 | ELSHAM ROAD (77) | 274908 | Active | 23a | High | Inspection Regime | Are the occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? Along with the other caretakers/Estates Services Assistants (ESAs) checks. | Occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing along with the other caretakers/ESAs checks. | Neighbourhood Management | Nicola Rees | 2017-02-21
79 - 94 CHELSEA MANOR COURT - 2015.07.07 | 2015-07-17 09:04 | S217000830006 | CHELSEA MANOR COURT 79-94 | 207295 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | Felix (ESA) confirms inspections in place | 2015-09-30 | Fully Completed | Janice Wray | 2015-07-17 09:04 | 2015-08-07 09:05 | 2015-07-17 09:04 | 2015-10-01 11:49 | -21 | In target
8 ASHBURNHAM ROAD - 2013.9.30 | 2013-10-10 15:00 | S217000190003 | ASHBURNHAM ROAD (8) | 110131 | Completed |  | Low | Miscellaneous | The caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson |  | Keys being pursued as part of inititaive with LHS & A & R. | 2014-03-17 | Fully Completed | Wendy Stevenson | 2013-10-10 15:00 | 2014-04-08 15:16 | 2013-10-10 15:00 | 2014-03-18 12:24 | -180 | In target
8 DAMER TERRACE - 2014.08.14 | 2014-08-22 12:05 | S217001400005 | DAMER TERRACE (8) | 158514 | Completed | 8 | Information Only | Communal Area Storage | Items left in the entrance hall/lobby area of this building, push bikes etc or combustible items. The entrance hall area was completely free of any items at the time of this assessment. | I would recommend that if it is reported that push bikes etc or combustible items are being left in the entrance hall area of this building and/or that they are obstructing either the flat entrance doors or the building entrance door then the occupants are written by the TMO reminding them that items should not be left here. | Neighbourhood Management | Wendy Stevenson |  | No action necessary. | 2014-08-22 | Fully Completed |  |  |  | 2014-08-22 12:05 | 2014-08-26 12:28
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:43 | S217002110009 | FINBOROUGH ROAD (80) | 122179 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Wendy Stevenson | 2014-06-29 |  | 2014-01-10 | Fully Completed |  |  |  | 2013-12-31 14:43 | 2014-01-13 12:12
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:49 | S217002110009 | FINBOROUGH ROAD (80) | 122183 | Completed | 8a | High | Communal Area Storage | In the lower ground floor electrical room there is an old damaged push bike, broken furniture, items of furniture like bedside units, old tins of paint, pieces of wood and decorating materials. | I would recommend that all items of storage are removed from this electrical room. | Neighbourhood Management | Wendy Stevenson |  | Items removed by OCS - delay until now because property is on a red route so no stopping allowed of vehicles. | 2014-05-09 | Fully Completed | Wendy Stevenson | 2013-12-31 14:49 | 2014-01-21 14:50 | 2013-12-31 14:49 | 2014-05-12 14:32 | -21 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:51 | S217002110009 | FINBOROUGH ROAD (80) | 122185 | Completed | 8b | Medium | Communal Area Storage | On the half landing area of the staircase there are presently 2 locked metal lockers and some exercise equipment including an exercise bike, this half landing is wide enough to accommodate these items and the staircase was not obstructed, the lockers are in an alcove and there are no ignition sources in this area. But there are combustible items stored on top of the metal lockers. | The items stored on top of these metal lockers should be removed, this is in case they fall off and obstruct the staircase. I would recommend that when the caretaker checks this building if combustible items again start to be stored here along with the metal exercise equipment then all the items on this half landing should be removed. The caretakers should also check that the staircase is not obstructed. | Neighbourhood Management | Wendy Stevenson |  | Items on top of cupbaords removed. On latest inspection everything else as found by the fire risk assessor. Monthly checks will monitor for any change. Items removed by OCS - delay because property is on a red route so no stopping allowed of vehicles. |  | Fully Completed | Wendy Stevenson | 2013-12-31 14:51 | 2014-03-01 14:52 | 2013-12-31 14:51 | 2014-05-12 14:34 | -60 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 14:53 | S217002110009 | FINBOROUGH ROAD (80) | 122188 | Completed | 8c | Medium | Communal Area Storage | In the lower ground floor brick built bin storage cupboards there are old bags of plaster, which have gone hard. | I would recommend that the bags of old plaster are removed from these bin cupboards. | Neighbourhood Management | Wendy Stevenson |  | Items removed by OCS - delay because property is on a red route so no stopping allowed of vehicles. | 2014-05-09 | Fully Completed | Wendy Stevenson | 2013-12-31 14:53 | 2014-03-01 14:53 | 2013-12-31 14:53 | 2014-05-12 14:35 | -60 | In target
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 15:04 | S217002110009 | FINBOROUGH ROAD (80) | 122198 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2014-01-21 | ESA's don't know how to test the emergency lighting, training is forthcoming. Training scheduled for 4th Feb 2014 to address this. | 2014-01-06 | Fully Completed | Wendy Stevenson | 2013-12-31 15:04 | 2014-01-21 15:04 | 2013-12-31 15:04 | 2014-01-08 15:56 | -21 | In target | 2013-12-31 15:04 | 2014-01-14 15:55 | Janice Wray
80 FINBOROUGH ROAD - 2013.12.31 | 2013-12-31 15:05 | S217002110009 | FINBOROUGH ROAD (80) | 122199 | Completed | 23b | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | Checks are being done on a monthly basis, the results recorded and retained. | 2014-01-06 | Fully Completed | Wendy Stevenson | 2013-12-31 15:05 | 2014-03-01 15:06 | 2013-12-31 15:05 | 2014-01-07 17:55 | -60 | In target
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 10:47 | S217002110010 | FINBOROUGH ROAD (82) | 239725 | Completed | 8 | Medium | Inspection Regime | There are old and damaged items of furniture etc being stored in the lower ground floor level electrical room. | Removed all of the storage from this electrical room. Raised by email - ESA confirms part of old bike & metal footstool store - order raised for removal, Removal complete? | Neighbourhood Management | Nicola Rees | 2016-04-28 | Order raised 201604230. This has been cleared. | 2016-04-19 | Fully Completed | Nicola Rees | 2016-01-27 10:47 | 2016-03-27 10:49 | 2016-01-27 10:47 | 2016-05-03 12:47 | -60 | In target
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 10:58 | S217002110010 | FINBOROUGH ROAD (82) | 239728 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-02-25 |  |  |  | Cyril Morris | 2016-01-27 10:58 | 2016-02-17 10:59 |  |  | 386 | 386 days overdue
82 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 10:59 | S217002110010 | FINBOROUGH ROAD (82) | 239729 | Active | 23c | Medium | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-04-28 |  |  |  | Cyril Morris | 2016-01-27 10:59 | 2016-03-27 11:01 |  |  | 347 | 347 days overdue
82 LOTS ROAD, LONDON SW10 OQD - 2016.05.19 | 2016-05-26 11:37 | S217003270010 | LOTS ROAD (82) | 262627 | Active | 12 | High | Flat Door | A cat flap has been fitted in the entrance door of flat C. | The entrance door to a flat on a protected staircase must be 30 minute fire rated (FD30) so that the compartmentation of the protected staircase enclosure is maintained and this is a requirement of the Building Regulations. There are fire rated cat flaps fitted with intumescent infills which means that the door remains FD30, but these must be fitted correctly. Can it be confirmed that flat C's entrance door is FD 30, if it is not it must be replaced with a self closing FD 30 door fitted with intumescent strips and cold smoke seals, so complying with the requirements of the Building Regulations. | Neighbourhood Management | Angelique Noble | 2016-06-16 | This cat flap belongs to [redacted] and he confirmed the make of the cat flap which is Cat Mate electronic 254. They advised that it is not fd and not sure if any cat flaps meet this requirement. He is going to wirte in with alternative flap which meets regulations or a cover which we have found. The deadline for this is February 2017, if this does not happen then recharge for door will take place. |  | Partially Completed | Angelique Noble | 2016-05-26 11:37 | 2016-06-16 11:38 |  |  | 266 | 266 days overdue
82 REDCLIFFE SQUARE, LONDON SW10 9BL - 2015.11.30 | 2016-01-28 12:26 | S217004540001 | REDCLIFFE SQUARE 82 A-E | 240038 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-02-26 | This is going to be added to the weekly inspection list for this area as of 14.11.16 | 2016-11-07 | Fully Completed | Nicola Rees | 2016-01-28 12:26 | 2016-02-18 12:29 | 2016-01-28 12:26 | 2016-11-09 16:02 | -21 | In target
82 REDCLIFFE SQUARE, LONDON SW10 9BL - 2015.11.30 | 2016-01-28 12:30 | S217004540001 | REDCLIFFE SQUARE 82 A-E | 240040 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-04-27 | This is going to be added to the weekly inspection list as part of the same complex as 123-125 Finborough commencing the 14.11.16 | 2016-11-08 | Fully Completed | Nicola Rees | 2016-01-28 12:30 | 2016-03-28 12:31 | 2016-01-28 12:30 | 2016-11-09 16:03 | -60 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:00 | S217010567703 | LONGLANDS COURT (82-87) | 103425 | Completed | 8 | Low | Communal Area Storage | There were a lot of items stored in the walkways outside the lower ground floor resident's storage cages/areas. This storage was no obstructing walkway areas but it is outside the designated storage cages. | I would recommend that the residents are asked to tidy up all the stored items in the walkways outside the storage cages/areas in the lower ground floor area. Also the caretakers should check to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that this area is tidy with no excessive amounts of combustible items etc. | Neighbourhood Management | Martin Barr |  | Leasehold team have advised the owner responsible not to store items outisde the caged area. Area was cleared of bulk waste before OCS attended. | 2013-10-22 | Fully Completed | Martin Barr | 2013-08-23 10:00 | 2014-02-19 10:01 | 2013-08-23 10:00 | 2013-11-08 14:39 | -180 | In target
82-87 LONGLANDS COURT-2013.03.01 | 2013-08-23 10:11 | S217010567703 | LONGLANDS COURT (82-87) | 103435 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | ESAs complete paper records which are kept and can be checked if required. Project underway to replace these with handheld devices to record checks electronically. |  | Fully Completed | Martin Barr | 2013-08-23 10:11 | 2013-10-22 10:12 | 2013-08-23 10:11 | 2013-11-12 12:20 | -60 | In target
83 PRINCEDALE ROAD - 2014.03.17 | 2014-03-20 15:25 | S217009770001 | PRINCEDALE ROAD (83) | 135647 | Completed |  | Information Only | Miscellaneous | It appears that the caretaker does not have any keys to the communal front entrance door of this building. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that keys are obtained for the locks on the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Martin Barr |  | Noted. We are compiling a list of these properties before deciding on lock changes. | 2014-04-17 | Fully Completed |  |  |  | 2014-03-20 15:25 | 2014-04-22 08:22
84 EDITH GROVE - 2015.11.11 | 2015-11-16 14:55 | S217001780004 | EDITH GROVE (84) | 227916 | Completed | 8 | Medium | Communal Area Storage | At the basement level in the internal lobby area outside the basement flats entrance door and also in the storage cupboard there is combustible items being stored. | I would recommend that the occupant of the basement flat is asked to tidy up and remove any rubbish, waste and old items from both of these areas. If they do not I would recommend that all items are removed from these areas and these areas are maintained free of all storage, ie sterile areas. | Neighbourhood Management | Nicola Rees | 2016-04-25 | This has been completed this week. Confirmed by ESA, | 2016-04-28 | Fully Completed | Nicola Rees | 2015-11-16 14:55 | 2016-01-15 14:56 | 2015-11-16 14:55 | 2016-04-29 17:04 | -60 | In target
84 FINBOROUGH ROAD, LONDON SW10 9AH - 2016.09.20 | 2016-09-26 12:04 | S217002110011 | FINBOROUGH ROAD (84) | 271196 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-10-24 |  |  |  | Cyril Morris | 2016-09-26 12:04 | 2016-10-17 12:05 |  |  | 143 | 143 days overdue
84 FINBOROUGH ROAD, LONDON SW10 9AH - 2016.09.20 | 2016-09-26 12:06 | S217002110011 | FINBOROUGH ROAD (84) | 271197 | Active | 23c | Medium | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-12-19 |  |  |  | Cyril Morris | 2016-09-26 12:06 | 2016-11-25 12:07 |  |  | 104 | 104 days overdue
84 REDCLIFFE SQUARE, LONDON SW10 9BL - 2015.11.30 | 2016-01-28 12:53 | S217004540002 | REDCLIFFE SQUARE 84 A-F | 240054 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-02-26 | This is to be added to the weekly check list for this patch as same complex as 123-125 Finborough Rd. Added on the 14.11.16 | 2016-11-08 | Fully Completed | Nicola Rees | 2016-01-28 12:53 | 2016-02-18 12:56 | 2016-01-28 12:53 | 2016-11-09 16:04 | -21 | In target
85 GOLBORNE ROAD, LONDON W10 5NL - 2016.01.07 | 2016-01-28 12:40 | S217008770007 | GOLBORNE ROAD (85) | 240044 | Completed | 8 | High | Inspection Regime | At the time of this fire risk assessment there was a push chair in the ground floor level entrance hall area by the store cupboard. This push chair had combustible items piled up on it. | All the items plied up on the push chair should be removed immediately. The push chair minus all of the combustible items can be left in the entrance hall area. If the owner of the push chair keeps piling combustible items up on the push chair then the push chair should also be removed and the residential common parts of this building keep a sterile area. | Neighbourhood Management | Louise Nezandonyi | 2016-02-26 | Clinotn has checked today and the items in the pushchair have been removed and it is now only the opush chair that remains. | 2016-03-08 | Fully Completed | Louise Nezandonyi | 2016-01-28 12:40 | 2016-02-18 12:42 | 2016-01-28 12:40 | 2016-03-09 15:58 | -21 | In target | 2016-01-28 12:40 | 2016-02-23 20:48 | Louise Nezandonyi
85 LADBROKE GROVE, LONDON W10 2HB - 2015.11.03 | 2016-01-25 16:16 | S217009120005 | LADBROKE GROVE (85) | 239421 | Completed | 23b | High | Inspection Regime | The caretaker recording system, "Insight" has been checked and the caretaker(s) are not undertaking the occupiers monthly tests and inspections of the emergency escape lighting units/system installed within this building. | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded. Carl has agreed to meet Pat (ESA) on site to show him how to test the EL at this block. | Neighbourhood Management | Louise Nezandonyi | 2016-02-22 | Pat has spokent to Carl and he is aware of where the emergency escape lighting units are and will be testing this every month from now on. | 2016-03-08 | Fully Completed | Louise Nezandonyi | 2016-01-25 16:16 | 2016-02-15 16:18 | 2016-01-25 16:16 | 2016-03-09 13:46 | -21 | In target
86 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:26 | S217002110012 | FINBOROUGH ROAD (86) | 239754 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-02-25 |  |  |  | Cyril Morris | 2016-01-27 11:26 | 2016-02-17 11:27 |  |  | 386 | 386 days overdue
86 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:28 | S217002110012 | FINBOROUGH ROAD (86) | 239755 | Active | 23c | Medium | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-04-28 |  |  |  | Cyril Morris | 2016-01-27 11:28 | 2016-03-27 11:29 |  |  | 347 | 347 days overdue
88 AND 90 BRAMLEY ROAD - 2015.09.29 | 2015-10-05 15:08 | S217008220001 | BRAMLEY ROAD (86-90) | 220062 | Completed | 8 | Information Only | Communal Area Storage | There is a table on the large open 1st floor level staircase landing along with children's bikes etc. The ground floor level entrance hall areas was clear of all items of storage. | As long as these are the only items on this 1st floor level landing area I believe that this is acceptable. If boxes of combustible items are stored here or household items or any items in the ground floor level entrance hall area, then everything must be removed from both areas. | Neighbourhood Management | Martin Barr |  | This has been an issue in the past but residents have been spoken to and area is monitores | 2015-10-30 | Fully Completed |  |  |  | 2015-10-05 15:08 | 2015-11-02 10:02
88 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:33 | S217002110013 | FINBOROUGH ROAD (88) | 239759 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-02-25 |  |  |  | Cyril Morris | 2016-01-27 11:33 | 2016-02-17 11:34 |  |  | 386 | 386 days overdue
88 FINBOROUGH ROAD, LONDON SW10 9ED - 2015.11.30 | 2016-01-27 11:35 | S217002110013 | FINBOROUGH ROAD (88) | 239760 | Active | 23c | Medium | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? | Neighbourhood Management | Nicola Rees | 2016-04-28 |  |  |  | Cyril Morris | 2016-01-27 11:35 | 2016-03-27 11:37 |  |  | 347 | 347 days overdue
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-23 14:46 | S217010567704 | LONGLANDS COURT (88-93) | 103559 | Completed | 8 | Medium | Inspection Regime | No access could be gained to the main lower ground floor resident's storage room/area. The caretaker does not have a key to the second door which has been installed inside the buildings original door to this area. Apparently only two residents have keys to this area. | I would recommend that the caretaker obtains a key for this area and that he undertakes a check of this room/area to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that this room/area is tidy with no excessive amounts of combustible items etc. | Neighbourhood Management | Martin Barr |  | These are resident private storage areas. The TMO does not hold keys for any private storage areas across our stock. | 2014-06-05 | Fully Completed | Martin Barr | 2013-08-23 14:46 | 2013-10-22 14:47 | 2013-08-23 14:46 | 2014-06-06 09:31 | -60 | In target
88-93 LONGLANDS COURT-2013.03.01 | 2013-08-21 14:46 | S217010567704 | LONGLANDS COURT (88-93) | 103119 | Completed | 23b | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | ESAs complete paper forms at present and these are kept and can be checked if required. Project underway to replace forms with electronically collected records. |  | Fully Completed | Martin Barr | 2013-08-21 14:46 | 2013-10-20 14:47 | 2013-08-21 14:46 | 2013-11-12 12:18 | -60 | In target
89 ELSHAM ROAD, LONDON W14 8HH -2017.01.03 | 2017-01-24 12:05 | S217006350014 | ELSHAM ROAD (89) | 274915 | Active | 23a | High | Inspection Regime | Are the occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? Along with the other caretakers/Estates Services Assistants (ESAs) checks. | Occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing along with the other caretakers/ESAs checks. | Neighbourhood Management | Nicola Rees | 2017-02-21 |  |  |  | Cyril Morris | 2017-01-24 12:05 | 2017-02-14 12:07 |  |  | 23 | 23 days overdue
9 COLVILLE SQUARE, LONDON W11 2BD - 2016.02.02 | 2016-02-19 16:28 | S217008450001 | COLVILLE SQUARE (9) | 244693 | Completed | 8 | High | Communal Area Storage | There is a washing machine on the landing area of the staircase outside flat E. | This washing machine should be removed from this staircase landing. | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | REMOVED COMPLETED | 2016-10-19 | Fully Completed | Janice Wray | 2016-02-19 16:28 | 2016-03-11 16:29 | 2016-02-19 16:28 | 2016-10-20 12:18 | -21 | In target
9 STADIUM STREET - 2015.09.22 | 2015-10-05 10:39 | S217005190002 | STADIUM STREET (9) | 219937 | Completed | 208296 | Information Only | Miscellaneous | The caretaker does not have any keys to the communal front entrance door of this building. There is no access control system, trade's man's button or a fire fighter over ride switch fitted so any visitor is dependant on an occupant coming to open the communal front entrance door. | I would recommend that a key is obtained for the communal front entrance door of this building from a resident, so that access can be gained by the TMO at any time. | Neighbourhood Management | Nicola Rees | 2016-02-02 | Lock change completed on week beginning 25.01.15 | 2016-02-04 | Fully Completed |  |  |  | 2015-10-05 10:39 | 2016-02-08 16:27 |  |  | 2015-10-05 10:39 | 2016-02-14 16:26 | Janice Wray
9 STADIUM STREET - 2015.09.22 | 2015-10-05 10:47 | S217005190002 | STADIUM STREET (9) | 219943 | Active | 12 | High | Flat Door | The flat entrance door of flat B has been changed from the originally fitted door. Leasehold Property Assessor advises that from his records it seems that this door was "changed in 2013 before this apartment sold" | Can it please be confirmed that the flat entrance door of flat B is a certified 30 minute self closing fire rated door conforming to all the requirements of the Building regulations, ie with intumescent strips and cold smoke seals fitted? (FD30s) If it is not then a self closing FD30s door must be fitted immediately. | Neighbourhood Management | Nazrul Islam | 2015-11-11 | lessee emailed 11.11.15 | 2015-11-11 | Partially Completed | David Ward | 2015-10-05 10:47 | 2015-10-26 10:49 | 2015-10-05 10:47 | 2015-11-12 11:16 | -21 | In target | 2015-10-05 10:47 | 2015-11-20 18:33 | David Ward
9, 10 AND 11 RADDINGTON ROAD, LONDON W10 5TG - 2015.12.22 | 2016-02-08 11:37 | S217009860005 | RADDINGTON ROAD | 241833 | Active | 8a | Medium | Inspection Regime | During this risk assessment access could not be gained to the 2nd floor level lobby area of the residents storage area of staircase number 10, next to flat 10E. There is a padlock on this door, there is an access hatch to the roof level from this area. | I would recommend that access is gained to this lobby area and any storage in the lobby area outside of the storage cupboards is removed. The padlock on this door should be removed so that access to the roof hatch is available at all times. | Neighbourhood Management | Louise Nezandonyi | 2016-05-02 |  |  |  | Cyril Morris | 2016-02-08 11:37 | 2016-04-08 11:59 |  |  | 335 | 335 days overdue
9, 10 AND 11 RADDINGTON ROAD, LONDON W10 5TG - 2015.12.22 | 2016-02-08 12:12 | S217009860005 | RADDINGTON ROAD | 241869 | Active | 8b | Low | Communal Area Storage | During this risk assessment access could not be gained to the 1st floor level lobby area of the residents storage area of staircase number 10, next to flat 10C. There is a padlock on this door. | I would recommend that access is gained to this lobby area and any storage in the lobby area outside of the storage cupboards is removed. The padlock on this door should be removed. | Neighbourhood Management | Louise Nezandonyi | 2016-07-18 |  |  |  | Cyril Morris | 2016-02-08 12:12 | 2016-08-06 12:15 |  |  | 215 | 215 days overdue
91 OXFORD GARDENS, LONDON W10 5UL - 2016.09.29 | 2016-10-18 16:39 | S217009620001 | OXFORD GARDENS (91) | 271998 | Active | 0 | Information Only | Miscellaneous | The Estates Service Assistant (ESA), caretaker has a key to the communal front entrance door of this building but the TMO have no spare keys for this buildings entrance door. There is no trade's man's button or a fire fighter over ride switch fitted so any visitor are dependant on an occupant opening the communal front entrance door to allow access. | I would recommend that copies of the key held by the ESA for the buildings front entrance doors are taken and these copies kept by the TMO, so that access can be gained by any TMO employee at any time. Could we get come copies cut please | Neighbourhood Management | Louise Nezandonyi | 2017-10-18
91 OXFORD GARDENS, LONDON W10 5UL - 2016.09.29 | 2016-10-18 16:43 | S217009620001 | OXFORD GARDENS (91) | 272000 | Active | 8a | High | Inspection Regime | In the entrance hall area there is a large item of furniture with 2 drawers, the drawers contain refuse sacks etc. Post/mail for the residents is placed on this unit. This item of furniture is too large, post could be placed on the top of the electrical cupboard. | This item of furniture should be removed from the entrance hall/lobby area. The metal step ladders are not combustible and can stay as long as they are securely fastened to the wall so that they do not fall over. | Neighbourhood Management | Louise Nezandonyi | 2016-11-15 |  |  |  | Cyril Morris | 2016-10-18 16:43 | 2016-11-08 16:45 |  |  | 121 | 121 days overdue
91 OXFORD GARDENS, LONDON W10 5UL - 2016.09.29 | 2016-10-18 16:46 | S217009620001 | OXFORD GARDENS (91) | 272003 | Active | 8b | High | Inspection Regime | On the ground to 1st floor level half landing area there is a 3 drawer bedroom unit and a cane conservatory type chair with padded cushions on it. | These items of furniture should be removed from this staircase half landing area. It is the TMOs policy that there is no combustible storage on staircase landings. | Neighbourhood Management | Louise Nezandonyi | 2016-11-15 |  |  |  | Cyril Morris | 2016-10-18 16:46 | 2016-11-08 16:47 |  |  | 121 | 121 days overdue
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 12:58 | S217001880008 | ELM PARK GARDENS (93) | 102474 | Completed | 8a | High | Inspection Regime | On the staircase landing on the floor level of flats 32 to 34 there is an upholstered chair, this chair is reducing the width of the staircase and could be an obstruction and trip hazard. On the staircase landing above this one there is a small table. | This chair and the table should be removed from these staircase landings immediately. The staircases should be kept free of items of furniture and combustible storage. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Table removed. Chair pushed away from staircase and landing and placed directly outside Flat 32 where it is no longer a hazard. Via porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 12:58 | 2013-09-09 12:59 | 2013-08-19 12:58 | 2013-09-09 11:53 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:00 | S217001880008 | ELM PARK GARDENS (93) | 102478 | Completed | 8b | High | Inspection Regime | In the 3rd floor level riser cupboard between flats 30 and 31 there is a large mirror being stored and a cardboard box. | I would recommend that these items are removed from this cupboard. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Removed via porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 13:00 | 2013-09-09 13:00 | 2013-08-19 13:00 | 2013-09-09 11:54 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:01 | S217001880008 | ELM PARK GARDENS (93) | 102481 | Completed | 8c | High | Inspection Regime | In the 5th floor level riser cupboard between flats 36 and 37 there are cardboard boxes of old telephones and some old light fittings. | I would recommend that these cardboard boxes are removed from this cupboard. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc is removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Items removed by porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 13:01 | 2013-09-09 13:02 | 2013-08-19 13:01 | 2013-09-09 11:55 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:03 | S217001880008 | ELM PARK GARDENS (93) | 102483 | Completed | 8d | High | Inspection Regime | On the staircase landing off the flat/lift lobby area of flats 38 to 40 there is an old piece of carpet laid on the landing floor. This carpet is not fitted or laid correctly, this could cause a person to trip and fall down the stairs. | I would recommend that this carpet is removed from this staircase landing area. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Removed by porter Martin Walsh. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 13:03 | 2013-09-09 13:04 | 2013-08-19 13:03 | 2013-09-09 11:56 | -21 | In target
93 ELM PARK GARDENS-2013.05.07 | 2013-08-19 13:18 | S217001880008 | ELM PARK GARDENS (93) | 102497 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system and the fire extinguishers in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | Fire extinguishers have been removed. All tests are being done and results recorded / retained. | 2013-09-04 | Fully Completed | Wendy Stevenson | 2013-08-19 13:18 | 2013-09-09 13:20 | 2013-08-19 13:18 | 2013-09-09 12:24 | -21 | In target
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 11:21 | S217009120002 | LADBROKE GROVE (94) | 101682 | Completed | 8 | High | Communal Area Storage | In the entrance hall area and under the staircase there are decorating items being stored, piles of dust sheets, tins of paint, wall papering pasting table and step ladders of various sizes. This is as well as push chairs and bicycles etc. | All the storage under the staircase and in the entrance hall area should be removed immediately. If all the storage is removed I believe that the push chairs and bicycles can remain. If combustible items and storage that could obstruct the means of escape continues to be left in this area then I would recommend that this entrance hall area and the under stairs area is kept completely clear and free of all items. | Neighbourhood Management | Martin Barr | 2013-09-04 | Residents have been advised previously and items now removed apart from bicycles and pushchairs. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-14 11:21 | 2013-09-04 14:45 | 2013-08-14 11:21 | 2013-10-14 13:06 | -21 | In target
94 LADBROKE GROVE - 2013.05.01 | 2013-08-14 15:25 | S217009120002 | LADBROKE GROVE (94) | 101787 | Completed | 23a | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record | Neighbourhood Management | Martin Barr | 2013-10-14 | Checks undertaken as per the current checklist. This process is to be reviewed before implementing an electronic system for recording checks. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-14 15:25 | 2013-10-13 15:27 | 2013-08-14 15:25 | 2013-10-14 13:07 | -60 | In target
94 LADBROKE GROVE, LONDON W11 2HE - 2016.03.04 | 2016-04-04 16:05 | S217009120002 | LADBROKE GROVE (94) | 252406 | Active | 8 | High | Communal Area Storage | In the entrance hall area and under the staircase there are decorating items being stored, a tool box, dust sheets, a wall papering/pasting table, step ladders and pieces of timber/MDF of various sizes. This is as well as push chairs and bicycles etc. | All the storage under the staircase should be removed immediately. If all the storage is removed the push chairs and bicycles can remain. If the storage is not remove and this area kept free of all storage then no items should be allowed to be placed in this area. This includes any push chairs and bikes etc. | Neighbourhood Management | Louise Nezandonyi | 2016-05-09 | ESA Pat will deliver a letter to the residents tomorrow and have until 13/04/2016 | 2016-04-05 | Partially Completed | Louise Nezandonyi | 2016-04-04 16:05 | 2016-04-25 16:06 | 2016-04-04 16:05 | 2016-04-06 14:55 | -21 | In target | 2016-04-04 16:05 | 2016-04-13 17:01 | Janice Wray
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:28 | S217010567705 | LONGLANDS COURT (94-102) | 103374 | Completed | 8 | Medium | Communal Area Storage | No access could be gained to the four lower ground floor level resident's storage rooms/areas. The caretaker does not have keys to these rooms/areas. | I would recommend that the caretaker obtains a key for each of the residents storage rooms/areas and that he undertakes a check of these rooms/areas to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that the rooms are tidy with no excessive amounts of combustible items etc be stored. | Neighbourhood Management | Martin Barr |  | These are resident private storage areas. The TMO does not hold keys for any private storage areas across our stock. | 2014-06-05 | Fully Completed | Martin Barr | 2013-08-22 16:28 | 2013-10-21 16:29 | 2013-08-22 16:28 | 2014-06-06 09:31 | -60 | In target
94-102 LONGLANDS COURT-2013.03.01 | 2013-08-22 16:42 | S217010567705 | LONGLANDS COURT (94-102) | 103388 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record. | Neighbourhood Management | Martin Barr |  | ESAs complete paper records which are kept and can be checked if required. Project underway to replace these with handheld devices to record checks electronically. |  | Fully Completed | Martin Barr | 2013-08-22 16:42 | 2013-10-21 16:48 | 2013-08-22 16:42 | 2013-11-12 12:20 | -60 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 09:32 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214837 | Completed | 8 | Medium | Inspection Regime | There are cardboard boxed piled up outside flat 199's entrance door. | The boxes should not be stored here, they should be removed. | Neighbourhood Management | Martin Barr | 2016-01-08 | Jimmy the ESA has been to check and he has confirmed that the boxes have been removed. | 2016-01-08 | Fully Completed | Louise Nezandonyi | 2015-09-04 09:32 | 2015-09-25 09:33 | 2015-09-04 09:32 | 2016-01-11 11:10 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 12:12 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214920 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-04 12:12 | 2015-09-25 12:13 | 2015-09-04 12:12 | 2015-09-17 11:22 | -21 | In target
ACKLAM ROAD, FLATS 19 TO 221 - 2015 .08 .27 | 2015-09-04 12:15 | S217007850014 | ACKLAM ROAD 19-37 115-143 ODDS | 214922 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-04 12:15 | 2015-09-25 12:16 | 2015-09-04 12:15 | 2015-09-17 11:21 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 10:56 | S217007970002 | ADAIR TOWER | 133530 | Completed | 1 | High | Inspection Regime | Some of the electrical portable appliances in the cleaner's rest room do not have portable appliance test (PAT) labels attached to them. | Any portable electrical appliances in the cleaners rest room without in date portable appliance test (PAT) labels attached to them should be tested by a suitably qualified person and portable appliance test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. | Neighbourhood Management | Martin Barr |  | Have emailed Janice Wray to enquire who carried out PAT testing for TMO. We can arrange PAT testing at this location which shouldn't be problematic. OCS have confirmed they PAT test in their locations. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 10:56 | 2014-03-28 10:58 | 2014-03-07 10:56 | 2014-09-01 09:12 | -21 | In target | 2014-03-07 10:56 | 2014-05-12 09:55 | Martin Barr
ADAIR TOWER - 2014.02.20 | 2014-03-07 11:01 | S217007970002 | ADAIR TOWER | 133533 | Completed | 8 | High | Communal Area Storage | On the 13th floor level flat/lift lobby area there is an internal household door and some empty cardboard boxes. | These items should be removed from this flat/lift lobby area. | Neighbourhood Management | Martin Barr |  | These items were removed. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 11:01 | 2014-03-28 11:02 | 2014-03-07 11:01 | 2014-04-22 08:44 | -21 | In target
ADAIR TOWER - 2014.02.20 | 2014-03-07 12:40 | S217007970002 | ADAIR TOWER | 133612 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire extinguishers, dry riser, the lifts and emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment, lifts emergency lighting etc and the other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Training on lighting testing & fire fighting equipment due 23rd April. Checks will take place after this and once list of locations provided by A&R team. Block checks are completed and records kept. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 12:40 | 2014-03-28 12:41 | 2014-03-07 12:40 | 2014-04-22 08:45 | -21 | In target
ADAIR TOWER, APPLEFORD ROAD LONDON W10 5EA - 2016.09..28 | 2016-10-07 11:15 | S217007970002 | ADAIR TOWER | 271656 | Active | 23d | High | Inspection Regime | Are the occupiers monthly tests and inspections of the fire systems in this building being undertaken as per the caretakers check list? | Can it please be confirmed that the occupiers monthly tests and inspections of the fire systems in this building being undertaken as per the caretakers check list? | Neighbourhood Management | Louise Nezandonyi | 2016-11-04 |  |  |  | Cyril Morris | 2016-10-07 11:15 | 2016-10-28 11:16 |  |  | 132 | 132 days overdue
AGNES HOUSE - 2014.08.14 | 2014-08-20 10:42 | S217010050010 | AGNES HOUSE | 158164 | Completed | 8 | High | Communal Area Storage | In the landing alcove area by flats 17 and 18 there was an internal door leaned against the wall. | I would recommend that this door is removed from the alcove on this landing. | Neighbourhood Management | Martin Barr |  | Internal door was removed | 2015-06-03 | Fully Completed | Martin Barr | 2014-08-20 10:42 | 2014-09-10 10:44 | 2014-08-20 10:42 | 2015-06-04 12:47 | -21 | In target
AGNES HOUSE - 2014.08.14 | 2014-08-20 11:01 | S217010050010 | AGNES HOUSE | 158176 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-20 11:01 | 2014-10-19 11:02 | 2014-08-20 11:01 | 2014-09-01 16:47 | -60 | In target
APOLLO HOUSE - 2015.01.28 | 2015-02-03 11:31 | S217012760010 | APOLLO HOUSE | 181556 | Completed | 8 | Low | Inspection Regime | During the risk assessment access could not be gained to the half landing store rooms in the building as the caretaker does not have keys for these areas. It is not known what is in these store rooms, but they are suitably fire separated from the staircase landings. | I would recommend that keys are obtained to the locks of these store room doors as these are presently not private storage areas but common parts of the building, under the control of the TMO. Once keys have been obtained for these storerooms a regular check on their contents should be undertaken to see that the storage or use is in accordance with the tenancy agreements. I would recommend that access to these storage rooms is then controlled/restricted to known persons only. | Neighbourhood Management | Wendy Stevenson |  | order raised 17/03/15 201460861 completed | 2015-05-07 | Fully Completed | Janice Wray | 2015-02-03 11:31 | 2015-08-02 11:33 | 2015-02-03 11:31 | 2015-05-11 09:53 | -180 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-01 16:52 | S217008190003 | APPLEFORD HOUSE 1-12 | 204392 | Completed | 3b | High | Inspection Regime | The gate at the ground floor level used to access the staircase of flats 9 to 12 did not lock. | I would recommend that the lock on this gate is checked and repaired or replaced so that is locks the gate securely. | Neighbourhood Management | Martin Barr |  | This was completed under order number 201529387 | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-01 16:52 | 2015-07-22 16:53 | 2015-07-01 16:52 | 2015-10-16 11:05 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 10:39 | S217008190003 | APPLEFORD HOUSE 1-12 | 204475 | Completed | 8a | High | Communal Area Storage | At the lower ground floor level there is waste and rubbish dumped in the walkway/corridor outside of the residents storage sheds/cupboards. There are 4 or 5 push bikes in this area as well. | I would recommend that all waste and rubbish is removed from the walkway/corridor outside of the residents storage sheds/cupboards. This walkway should be a clear pathway with no storage or rubbish in it. The bikes could stay as long as they do not obstruct the walkway or the gates. | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-02 10:39 | 2015-07-23 10:42 | 2015-07-02 10:39 | 2015-10-16 11:16 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 10:46 | S217008190003 | APPLEFORD HOUSE 1-12 | 204480 | Completed | 8b | High | Inspection Regime | At the lower ground floor level there is a large pile of rubble and bricks in the walkway/ corridor outside of the residents storage sheds/cupboards, under flats 3 and 4. | I would recommend that all this rubble and builders waste etc is removed from this area. | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-02 10:46 | 2015-07-23 11:31 | 2015-07-02 10:46 | 2015-10-16 11:17 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 11:32 | S217008190003 | APPLEFORD HOUSE 1-12 | 204527 | Completed | 8c | High | Communal Area Storage | At the lower ground floor level there are residents storage sheds/cupboards some of these have old and damaged items in them piled up. | I would recommend that all of the residents storage sheds/cupboards are checked and any which contain old and damaged items, or the one with coal in it are emptied out. This will reduce the fire loading of this area. I would recommend that regular inspections should be undertaken of this storage area and that this area is maintained free of any waste with the doors of the storage sheds/cupboards locked shut if they are in use. | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-02 11:32 | 2015-07-23 11:33 | 2015-07-02 11:32 | 2015-10-16 11:17 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 11:37 | S217008190003 | APPLEFORD HOUSE 1-12 | 204529 | Completed | 12 | High | Communal Area Storage | Some of the doors to the resident's storage areas at the lower ground floor level have been pulled off or are damaged. | I would recommend that all of the doors to these resident's storage sheds/cupboards are checked and any damaged doors which do not lock are repaired or replaced. | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-02 11:37 | 2015-07-23 11:41 | 2015-07-02 11:37 | 2015-10-16 11:17 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 11:44 | S217008190003 | APPLEFORD HOUSE 1-12 | 204538 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-07-02 11:44 | 2015-07-23 11:45 | 2015-07-02 11:44 | 2015-09-21 08:48 | -21 | In target
APPLEFORD HOUSE -2015.06.22 | 2015-07-02 11:47 | S217008190003 | APPLEFORD HOUSE 1-12 | 204545 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-02 11:47 | 2015-07-23 11:48 | 2015-07-02 11:47 | 2015-09-18 18:01 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:19 | S217007970004 | APPLEFORD HOUSE 13-28 | 206054 | Completed | 8 | High | Communal Area Storage | At the lower ground floor level there are residents storage sheds/cupboards some of these have old and damaged items in them piled up. One cupboard has piles of coal in it. | I would recommend that all of the residents storage sheds/cupboards are checked and any which contain old and damaged items, or the one with coal in it are emptied out. This will reduce the fire loading of this area. I would recommend that regular inspections should be undertaken of this storage area and that this area is maintained free of any waste with the doors of the storage sheds/cupboards locked shut if they are in use. | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-10 13:19 | 2015-07-31 13:21 | 2015-07-10 13:19 | 2015-10-16 11:18 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:21 | S217007970004 | APPLEFORD HOUSE 13-28 | 206055 | Completed | 12 | High | Communal Area Storage | Some of the doors to the resident's storage areas at the lower ground floor level have been pulled off or are damaged. | I would recommend that all of the doors to these resident's storage sheds/cupboards are checked and any damaged doors which do not lock are repaired or replaced. Martin - could you please inspect & refer any necessary repairs / replacement to RD | Neighbourhood Management | Martin Barr |  | Storage sheds are currently locked off to residents. There are repairs needed to get them back into use. At present we are undertaking an audit of them to see the scope of work needed and whether budgets are available to do the necessary work. Until this happens no work will be done to them unless it is urgently required. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-10 13:21 | 2015-07-31 13:23 | 2015-07-10 13:21 | 2015-10-16 11:18 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:25 | S217007970004 | APPLEFORD HOUSE 13-28 | 206058 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-10 13:25 | 2015-07-31 13:27 | 2015-07-10 13:25 | 2015-09-18 17:56 | -21 | In target
APPLEFORD HOUSE, FLATS 13 TO 28 - 2015.06.22 | 2015-07-10 13:30 | S217007970004 | APPLEFORD HOUSE 13-28 | 206060 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-10 13:30 | 2015-07-31 13:31 | 2015-07-10 13:30 | 2015-09-18 17:55 | -21 | In target
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:30 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101947 | Completed | 8a | Medium | Communal Area Storage | There is contractors waste, combustible material and decorating equipment and items stored in both riser cupboards on the 1st floor level and in the double riser cupboards on the 8th and 13th floor level flat/lift lobby areas. | I would recommend that all the contractors waste and other material is removed from these riser cupboards. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc has been removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | Clearance completed 18th Oct 2013. ESA's have been instructed to inspect all intake cupboards on a monthly basis. | 2013-10-18 | Fully Completed | Wendy Stevenson | 2013-08-15 11:30 | 2013-10-14 11:33 | 2013-08-15 11:30 | 2013-10-21 12:23 | -60 | In target | 2013-08-15 11:30 | 2013-10-23 16:49 | Wendy Stevenson
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:33 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101949 | Completed | 8b | Medium | Communal Area Storage | On the 10th floor level flat/lift lobby area there are household items, chairs and bags of clothes. | These bags and household items should be removed from the flat/lift lobby area. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | Clearance arranged 16th Oct 2013 and completed 18th Oct 2013. | 2013-10-18 | Fully Completed | Wendy Stevenson | 2013-08-15 11:33 | 2013-10-14 11:36 | 2013-08-15 11:33 | 2013-10-21 12:23 | -60 | In target | 2013-08-15 11:33 | 2013-10-23 16:50 | Wendy Stevenson
ASHBURNHAM TOWER - 2013.04.01 | 2013-08-15 11:39 | S217012740012 | ASHBURNHAM TOWER 1-50 | 101953 | Completed | 8d | Low | Communal Area Storage | In the double riser cupboards on the 10th and 15th floor levels there are push bikes being stored. | Are the TMO aware that push bikes are being stored in these 2 riser cupboards? The owners of these bikes must have keys to the locks on these cupboards to access the push bikes. | Neighbourhood Management | Wendy Stevenson | 2013-10-31 | Upon inspection today they were already gone. | 2013-10-16 | Fully Completed | Wendy Stevenson | 2013-08-15 11:39 | 2014-02-11 11:41 | 2013-08-15 11:39 | 2013-10-17 16:32 | -180 | In target
ASHBURNHAM TOWER, ON THE WORLDS END ESTATE, BLANTYRE STREET, LONDON SW10 0EE -2016.07.28 | 2016-09-16 12:46 | S217012740012 | ASHBURNHAM TOWER 1-50 | 270857 | Completed | 12d | High | Inspection Regime | The staircase doors of this building have been retrospectively fitted with combined cold smoke seals and intumescent strips. The there strips missing or damaged from the 6th and 15th floor level doors. | Any missing and damaged combined cold smoke seals and intumescent strips should be replaced. The caretakers etc should be checking all the buildings fire doors for damaged strips and seals, where they are fitted and recording these door checks. | Neighbourhood Management | Nicola Rees | 2016-10-14 | There has been order raised for this on system. ESA made aware but further training may be required on this issue please. | 2016-10-11 | Fully Completed | Nicola Rees | 2016-09-16 12:46 | 2016-10-07 15:45 | 2016-09-16 12:46 | 2016-10-12 12:07 | -21 | In target
ASHBURNHAM TOWER, ON THE WORLDS END ESTATE, BLANTYRE STREET, LONDON SW10 0EE -2016.07.28 | 2016-09-16 16:25 | S217012740012 | ASHBURNHAM TOWER 1-50 | 270890 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-10-14 | Yes this has been conducted. | 2016-10-10 | Fully Completed | Nicola Rees | 2016-09-16 16:25 | 2016-10-07 16:26 | 2016-09-16 16:25 | 2016-10-11 13:51 | -21 | In target
BALFOUR HOUSE, 90 ST CHARLES SQUARE, LONDON W10 6ED - 2016.07.21 | 2016-09-16 11:13 | S217010080002 | BALFOUR HOUSE | 270851 | Active | 12h | High | Flat Door | The flat entrance door fitted to flat 5 has a cat flap in it. TENANTS DOOR | A new certified self closing 30 minute fire rated door, fitted with cold smoke seals and intumescent strips and complying with all the requirements of the Building Regulations should be fitted to this flat. The cat flap in this door makes it not a fire rated door. Queried with Neighbourhood Manager who advises that Neighbourhood Officer should write to tenant advising that the fire integrity of the door has been breached by the installation of the cat flap and so we will need to fit a replacement door. This new door must not be breached. Once this is completed an order will be raised for installation of a new door. | Neighbourhood Management | Emlyn Osborne | 2016-10-14 |  |  |  | Cyril Morris | 2016-09-16 11:13 | 2016-10-07 11:15 |  |  | 153 | 153 days overdue
BARANDON WALK - 2014.11.6 | 2014-11-28 14:47 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 171973 | Completed | 8a | High | Storage | In electrical intake rooms 2 and 4 there is a lot of cardboard boxes being stored and old light fittings. | All this storage should be removed from these electrical intake rooms. Could Inspectors arrange clearance please | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | Instruction issued for clearance of these rooms by Siobhan Rumble | 2015-01-23 | Fully Completed | Siobhan Rumble | 2014-11-28 14:47 | 2014-12-19 14:49 | 2014-11-28 14:47 | 2015-01-26 13:56 | -21 | In target | 2014-11-28 14:47 | 2015-01-30 13:54 | Janice Wray
BARANDON WALK - 2014.11.6 | 2014-11-28 14:50 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 171977 | Completed | 8b | High | Communal Area Storage | Residents are storing items outside their flats entrance doors. 1. There is a table and a wooden storage unit outside flat 439. 2. There are items of furniture etc by the refuse chute next to flat 501. | I would recommend that the residents are asked to remove the items outside their flats. The residents should be reminded that the walkways should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading is kept as low as possible. (The LFB insist that the 3 finger blocks must be "zero tolerance" in relation to storage within the communal areas.) | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | Siobhan confirms items outside 439 have been stickered and the residetns given 7 days to remove them. Items by refuse chute removed | 2015-01-23 | Fully Completed | Siobhan Rumble | 2014-11-28 14:50 | 2014-12-19 14:51 | 2014-11-28 14:50 | 2015-01-26 12:52 | -21 | In target | 2014-11-28 14:50 | 2015-01-30 12:52 | Janice Wray
BARANDON WALK - 2014.11.6 | 2014-11-28 15:47 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172070 | Completed | 23b | High | Fire Alarm | Are the weekly occupier's tests of the fire alarm system in this building being undertaken. | Can it be confirmed that the caretaker(s) are undertaking the weekly occupiers testing of the fire alarm system in this building, there were no records of any testing or a fire logbook available at the time of this assessment. | Neighbourhood Management | Siobhan Rumble | 2015-03-09 | Paul states he has never done or been told to test the roof window alarm and they currently out of action whilst the possibiloity of replacing them with fixed vents is investigated by the Head of Contract Management. | 2015-03-11 | Fully Completed | Siobhan Rumble | 2014-11-28 15:47 | 2014-12-19 15:48 | 2014-11-28 15:47 | 2015-03-12 16:08 | -21 | In target | 2014-11-28 15:47 | 2015-03-18 16:06 | Janice Wray
BARANDON WALK - 2014.11.6 | 2014-11-28 15:50 | S217012770011 | BARANDON WALK 301-39 & 401-39 | 172083 | Completed | 23d | High | Inspection Regime | Are the monthly occupier testing and inspections of the emergency escape lighting system, the fire extinguishers and the buildings structural inspections being undertaken? | Can it be confirmed that the caretakers are undertaking the occupiers monthly testing and inspections of the installed systems, as per the caretakers check list in these buildings? With the results completed records kept as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | Monthly testing being done but not recorded - now being recorded Extinguishers being inspected | 2015-01-23 | Fully Completed | Siobhan Rumble | 2014-11-28 15:50 | 2014-12-19 15:51 | 2014-11-28 15:50 | 2015-01-26 12:55 | -21 | In target | 2014-11-28 15:50 | 2015-01-30 12:53 | Janice Wray
BARKIS HOUES - 2014.7.22 | 2014-08-04 13:14 | S217010050002 | BARKIS HOUSE | 155848 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-04 13:14 | 2014-08-25 13:16 | 2014-08-04 13:14 | 2014-09-01 16:22 | -21 | In target
BEAUFORT HOUSE - 2015.06.15 | 2015-06-25 14:22 | S217000310007 | BEAUFORT HOUSE | 203355 | Completed | 8 | Medium | Communal Area Storage | At the basement level of this building there is a residents storage area, some items are piled up in the open areas others are located within rooms. | I would recommend that the residents would have items stored here are asked to tidy up this area and dispose of all unwanted items. Some items here look like they have not been touched for years. | Neighbourhood Management | Wendy Stevenson |  | ESA confirms this has been referred to Neighbourhood Officer. | 2015-10-09 | Partially Completed | Janice Wray | 2015-06-25 14:22 | 2015-08-24 14:24 | 2015-06-25 14:22 | 2015-10-12 13:38 | -60 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:17 | S217012740002 | BERENGER TOWER 1-51 | 102372 | Completed | 8a | High | Communal Area Storage | On the 15th floor level flat/lift lobby area there is an old television, a fridge freezer, bedroom furniture and a small dining table and chairs. | These items should be removed from this flat/lift lobby area immediately and the resident who owns them reminded that the flat/lift lobby areas are not to be used for storage. | Neighbourhood Management | Wendy Stevenson | 2013-09-09 | All removed, confirmed via ESA Felix Akumanyi. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-19 09:17 | 2013-09-09 09:20 | 2013-08-19 09:17 | 2013-09-09 12:22 | -21 | In target
BERENGER TOWER - 2013.04.01 | 2013-08-19 09:20 | S217012740002 | BERENGER TOWER 1-51 | 102373 | Completed | 8b | Medium | Communal Area Storage | There are push bikes being stored in the 5th floor level riser cupboards on the flat/lift lobby area and bags of cement and contractors waste are in the 4th floor level cupboards. | I would recommend that all these items are removed from these riser cupboards. | Neighbourhood Management | Wendy Stevenson | 2013-10-18 | Cement and contractors' waste has been removed but 2 bikes remain. Olivia Hutchison has written to Flat 6 who it is believed owns the bikes. One bike is old, the other in a reasonable state. Olivia to authorise disposal, depending on content of recent letter. Update 3/3/14 - bikes removed 28/2/14. | 2014-02-28 | Fully Completed | Wendy Stevenson | 2013-08-19 09:20 | 2013-10-18 09:21 | 2013-08-19 09:20 | 2014-03-04 13:36 | -60 | In target | 2013-08-19 09:20 | 2013-11-05 12:28 | Wendy Stevenson
BERENGER TOWER, BLANTYRE STREET, LONDON SW10 0EF - 2016.07.28 | 2016-08-22 10:39 | S217012740002 | BERENGER TOWER 1-51 | 269926 | Completed | 2 | High | Inspection Regime | On the 5th and the 17th flat/lift lobby areas there are used cigarette ends on the floors and other discarded, used smoking material. | All used smoking material and cigarette ends etc should be removed from these 2 flat/lift lobby areas. The residents on these floor levels should be informed of the TMO's no smoking policy. Could the ESA monitor & report back | Neighbourhood Management | Nicola Rees | 2016-09-12 | Material removed from these areas and cleaned. | 2016-09-15 | Fully Completed | Nicola Rees | 2016-08-22 10:39 | 2016-09-12 10:44 | 2016-08-22 10:39 | 2016-10-03 12:07 | -21 | In target
BERENGER TOWER, BLANTYRE STREET, LONDON SW10 0EF - 2016.07.28 | 2016-08-22 11:31 | S217012740002 | BERENGER TOWER 1-51 | 269953 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and checks on the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. Extinguishers identified as un -serviced which ESA should have picked up on monthly H&S inspection | Neighbourhood Management | Nicola Rees | 2016-09-12 | The temporary ESA was unclear about their location but is now aware. | 2016-10-10 | Fully Completed | Nicola Rees | 2016-08-22 11:31 | 2016-09-12 11:33 | 2016-08-22 11:31 | 2016-10-11 16:34 | -21 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:10 | S217012740014 | BLANTYRE TOWER 1-65 | 102163 | Completed | 8a | Medium | Communal Area Storage | There is contractors waste, combustible material and decorating equipment and items stored in the double riser cupboard on the ground floor level. | I would recommend that all the contractors waste and other material is removed from this riser cupboard. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc has been removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | All clear today. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 07:10 | 2013-10-15 07:13 | 2013-08-16 07:10 | 2013-10-16 16:10 | -60 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:14 | S217012740014 | BLANTYRE TOWER 1-65 | 102164 | Completed | 8b | Medium | Communal Area Storage | On the 9th floor level flat/lift lobby area there are off cuts of timber and wooden shelves. | These shelves and piece of timber should be removed from this flat/lift lobby area. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | All clear. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 07:14 | 2013-10-15 07:17 | 2013-08-16 07:14 | 2013-10-16 16:11 | -60 | In target
BLANTYRE TOWER - 2013.05.01 | 2013-08-16 07:18 | S217012740014 | BLANTYRE TOWER 1-65 | 102165 | Completed | 8c | Low | Miscellaneous | The 17th floor level flat/lift lobby area has been covered with laminate flooring, at present this floor covering is in good condition and well fitted and does not I believe pose any type of hazard. But the floor covering could deteriorate, lift etc and become a trip hazard. | I would recommend that the floor covering on this floor level is monitored by the caretakers on their monthly inspections and if it becomes a trip hazard by lifting or being damaged then the laminate flooring should be repaired or removed. | Neighbourhood Management | Wendy Stevenson | 2014-02-12 | To complete this action please just confirm that this is inspected regularly by the ESA. What is the frequency of these inspections? Inspections carried out three times weekly and logged by the ESA. Felix has been instructed today to pay attention to any changing condition of this flooring. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 07:18 | 2014-02-12 07:21 | 2013-08-16 07:18 | 2013-10-16 14:19 | -180 | In target
BLANTYRE TOWER,BLANTYRE STREET LONDON SW10 0EH - 2016.07.28 | 2016-09-21 11:09 | S217012740014 | BLANTYRE TOWER 1-65 | 271037 | Completed | 12e | Information Only | Inspection Regime | The 17th floor level flat/lift lobby area has been covered with laminate flooring, at present this floor covering is in good condition and well fitted and does not I believe pose any type of hazard. But the floor covering could deteriorate, lift etc and become a trip hazard. | I would recommend that the floor covering on this floor level is monitored by the caretakers on their monthly inspections and if it becomes a trip hazard by lifting or being damaged then the laminate flooring should be repaired or removed. | Neighbourhood Management | Nicola Rees | 2017-09-21 | The ESA has been advised of this information at 1:1 on 07.10.16. We will also look at documenting this information on our local knowledge data base which we are creating so dont lose this advice. | 2016-10-11 | Fully Completed |  |  |  | 2016-09-21 11:09 | 2016-10-12 12:16
BLANTYRE TOWER,BLANTYRE STREET LONDON SW10 0EH - 2016.07.28 | 2016-09-21 11:27 | S217012740014 | BLANTYRE TOWER 1-65 | 271046 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and checks on the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-10-19 | Yes this is being completed. | 2016-12-01 | Fully Completed | Nicola Rees | 2016-09-21 11:27 | 2016-10-12 11:28 | 2016-09-21 11:27 | 2016-12-02 15:57 | -21 | In target
BLECHYNDEN HOUSE - 2014.4.7 | 2014-05-06 15:03 | S217009090001 | BLECHYNDEN HOUSE | 142415 | Completed | 21b | High | Miscellaneous | There are automatic opening ventilation units/smoke control installed on the windows in the corridors of this building, also in the walls and in the top floor level corridor ceiling. | Have all of the staff who are employed in Whitchurch House and the caretakers who visit this building been given specific instructions on how to use these installed units and how the units interface with the fire alarm system including making certain that the windows that open are not obstructed with pots of plants etc. | Neighbourhood Management | Hash Chamchoun | 2014-05-12 | On site SHO aware of how units operate and interface with fire alarm system. SHO tests system weekly and monitors to ensure windows automatically close after each test. Outstanding actions to be picked up by H&S Team: Arrange for on site SHO to have key for the vent controls. Check that local caretaker has been instructed. | 2014-05-12 | Fully Completed | Hash Chamchoun | 2014-05-06 15:03 | 2014-05-27 15:04 | 2014-05-06 15:03 | 2014-05-13 12:29 | -21 | In target | 2014-05-06 15:03 | 2014-05-19 12:29 | Janice Wray
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:42 | S217008190001 | BOSWORTH HOUSE | 184206 | Completed | 8a | High | Communal Area Storage | At the base of the left hand staircase, as you look at this building from the rear car parking area, there is a damaged motor scooter stored in the entrance lobby area. | I would recommend that this scooter is removed from this area. | Neighbourhood Management | Martin Barr |  | Scooter was not there on Estate Inspection on 18th March 2051 | 2015-03-18 | Fully Completed | Martin Barr | 2015-02-18 09:42 | 2015-03-11 09:44 | 2015-02-18 09:42 | 2015-03-20 09:43 | -21 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:46 | S217008190001 | BOSWORTH HOUSE | 184207 | Completed | 8b | Medium | Communal Area Storage | At the lower ground floor level of this building there are storage cupboards, these are mostly all empty. But some have contractors waste in them, old bricks, pieces of timber, plasterboard old pieces of kitchen units etc. | I would recommend that these storage cupboards are emptied out completely and in future this area regularly checked to see that waste is not left here. | Neighbourhood Management | Martin Barr |  | This area is kept locked and nobody has access currently. The contents of the few sheds with any items in will be dealt with when we carry out the borough wide shed audit due this year | 2015-03-18 | Fully Completed | Martin Barr | 2015-02-18 09:46 | 2015-04-19 09:47 | 2015-02-18 09:46 | 2015-03-20 09:44 | -60 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:48 | S217008190001 | BOSWORTH HOUSE | 184208 | Completed | 8c | Medium | Miscellaneous | The door to the cupboard/room on the lower ground floor level at the base of the left hand left hand staircase, as you look at this building from the rear car parking area, could not be opened. | The door to this room/cupboard should be repaired so that it can be opened and/or a new lock fitted and it should be confirmed that this cupboard/room is clear of all items of storage etc. | Neighbourhood Management | Martin Barr |  | The door is accessible but is being kept locked as we are not intending residents to access this area at present. There is work needed before the sheds can be brought back into use | 2015-03-19 | Fully Completed | Martin Barr | 2015-02-18 09:48 | 2015-04-19 09:49 | 2015-02-18 09:48 | 2015-03-20 09:46 | -60 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 09:58 | S217008190001 | BOSWORTH HOUSE | 184214 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Lighting is tested, record keeping will be through the ESA mobile working platform going live in April 2015 | 2015-03-18 | Fully Completed | Martin Barr | 2015-02-18 09:58 | 2015-03-11 09:59 | 2015-02-18 09:58 | 2015-03-20 09:47 | -21 | In target
BOSWORTH HOUSE - 2015.02.05 | 2015-02-18 10:00 | S217008190001 | BOSWORTH HOUSE | 184215 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. Martin Barr | Neighbourhood Management | Martin Barr |  | Yes. Record keeping will be electronic from April 2015 | 2015-03-18 | Fully Completed | Martin Barr | 2015-02-18 10:00 | 2015-03-11 10:01 | 2015-02-18 10:00 | 2015-03-20 09:47 | -21 | In target
BOWLING GREEN HOUSE, APOLLO PLACE, LONDON SW10 0DN - 2015.1.6 | 2015-01-30 13:24 | S217012760011 | BOWLING GREEN HOUSE | 181065 | Completed | 8a | Medium | Communal Area Storage | In the ground floor electrical room under the staircase there are two empty cardboard boxes and plus some bags of what looks like rubbish. | I would recommend that these combustible items are removed from this electrical room and that it is maintained free of all rubbixh and waste. | Neighbourhood Management | Jimmy Lemos |  |  | 2015-04-30 | Fully Completed | Jimmy Lemos | 2015-01-30 13:24 | 2015-03-31 13:25 | 2015-01-30 13:24 | 2015-05-08 12:54 | -60 | In target
BOWLING GREEN HOUSE, APOLLO PLACE, LONDON SW10 0DN - 2015.1.6 | 2015-01-30 13:26 | S217012760011 | BOWLING GREEN HOUSE | 181066 | Completed | 8b | Low | Communal Area Storage | During the risk assessment access could not be gained to the half landing store rooms in the building as the caretaker does not have keys for these areas. It is not known what is in these store rooms, but they are suitably fire separated from the staircase landings. | I would recommend that keys are obtained to the locks of these store room doors as these are presently not private storage areas but common parts of the building, under the control of the TMO. Once keys have been obtained for these storerooms a regular check on their contents should be undertaken to see that the storage / use is in accordance with the tenancy agreement. I would recommend that access to these storage rooms is then controlled/restricted to known persons only. | Neighbourhood Management | Wendy Stevenson |  | completed 20/03/15 ref 201460861 the new keys are with ESA Kebra Smith | 2015-05-07 | Fully Completed | Janice Wray | 2015-01-30 13:26 | 2015-07-29 13:28 | 2015-01-30 13:26 | 2015-05-11 09:55 | -180 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 13:50 | S217008220002 | BRAMLEY HOUSE | 199106 | Completed |  | Medium | Miscellaneous | There was no access to the external roof area as each staircase gate on the 4th floor level which gives access to the roof area is secured by chains and padlocks. | Can it be confirmed that the TMO have the keys to these padlocks and that the roof area is free of all storage as are the roof level areas at the head of each staircase? | Neighbourhood Management | Martin Barr |  | ESA has keys and area is free of stored belongings | 2015-09-24 | Fully Completed | Martin Barr | 2015-05-28 13:50 | 2015-07-27 13:52 | 2015-05-28 13:50 | 2015-09-25 11:31 | -60 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 13:53 | S217008220002 | BRAMLEY HOUSE | 199107 | Completed |  | Medium | Miscellaneous | There was no access to the basement area as the door which gives access to the basement area is secured by a chain and padlock. | Can it be confirmed that the TMO have the key to this padlock and that the basement area is free of all unauthorised storage? | Neighbourhood Management | Martin Barr |  | ESA has keys and area is free of stored belongings | 2015-09-24 | Fully Completed | Martin Barr | 2015-05-28 13:53 | 2015-07-27 13:54 | 2015-05-28 13:53 | 2015-09-25 11:31 | -60 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 13:55 | S217008220002 | BRAMLEY HOUSE | 199108 | Completed |  | Medium | Miscellaneous | There was no access to the room under staircase 2, by flat 11's entrance door, because this door could not be opened. | Can it be confirmed that the TMO have a key this door and that this area is free of all unauthorised storage? | Neighbourhood Management | Martin Barr |  | ESA has keys and area is free of stored belongings | 2015-09-24 | Fully Completed | Martin Barr | 2015-05-28 13:55 | 2015-07-27 13:56 | 2015-05-28 13:55 | 2015-09-25 11:31 | -60 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 13:57 | S217008220002 | BRAMLEY HOUSE | 199109 | Completed | 12a | High | Communal Area Storage | There are some pots of plants on the balcony wall in front of flat 40 and a lot more plants on the balcony floor outside of the flat door. These pots of plants are restriction the width of the balcony and also there could fall off the balcony wal onto persons below. | I would recommend that the pots of plants are removed from the balcony wall and some are removed from the floor of the balcony so they are not a trip hazard or are reducing the width of the means of escape route. A few pots of plants etc are I believe acceptable against the wall of the open balconies. | Neighbourhood Management | Martin Barr |  | ESA has spoken with flat 40. The plants on balcony are fixed in place so any risk of falling is negated. They have reduced number of plants to avoid trip hazard. ESA has requested Neighbourhood Team write to residents on thsi stairway as a general issue | 2015-10-01 | Fully Completed | Martin Barr | 2015-05-28 13:57 | 2015-06-18 13:58 | 2015-05-28 13:57 | 2015-11-02 10:01 | -21 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 14:08 | S217008220002 | BRAMLEY HOUSE | 199114 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-28 14:08 | 2015-06-18 14:09 | 2015-05-28 14:08 | 2015-09-21 09:40 | -21 | In target
BRAMLEY HOUSE - 2015.05.13 | 2015-05-28 14:10 | S217008220002 | BRAMLEY HOUSE | 199115 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure.. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-28 14:10 | 2015-06-18 14:11 | 2015-05-28 14:10 | 2015-09-21 09:40 | -21 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:24 | S217011160001 | BROADWOOD TERRACE 1-24 | 186479 | Completed | 8 | High | Communal Area Storage | There is a push bike chained to the staircase handrail, next to house 23, this bike is blocking the staircase door and therefore the means of escape route. | This push bike should be removed from this area immediately, this staircase is a means of escape route and also an access route for the fire service to these dwellings from Warwick Rd. | Neighbourhood Management | Jimmy Lemos |  | completed by Kamran | 2015-05-28 | Fully Completed | Jimmy Lemos | 2015-03-04 16:24 | 2015-03-25 16:25 | 2015-03-04 16:24 | 2015-05-29 13:04 | -21 | In target
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:33 | S217011160001 | BROADWOOD TERRACE 1-24 | 186488 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Kamran Hye |  | Kamran Hyde has confirm that the above inspections had been completed. | 2015-05-13 | Fully Completed | Jimmy Lemos | 2015-03-04 16:33 | 2015-03-25 16:34 | 2015-03-04 16:33 | 2015-05-15 15:20 | -21 | In target | 2015-03-04 16:33 | 2015-05-20 12:23 | Jimmy Lemos
BROADWOOD TERRACE - 2015.02.12 | 2015-03-04 16:37 | S217011160001 | BROADWOOD TERRACE 1-24 | 186492 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier tests as per the caretakers check list for the residential areas of this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | Kamran Hyde has confirm that the above inspections had been completed.by John Whall. | 2015-05-13 | Fully Completed | Jimmy Lemos | 2015-03-04 16:37 | 2015-03-25 16:38 | 2015-03-04 16:37 | 2015-05-15 15:21 | -21 | In target | 2015-03-04 16:37 | 2015-05-20 12:26 | Jimmy Lemos
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:03 | S217010820001 | BRUCE HOUSE | 214300 | Completed | 1 | High | Miscellaneous | Access could not be gained to the electrical room/cupboard near to flat 3, as this door could not be opened. Therefore it is not known if there is a contractors test label on the electrical supply board within this area. | Please can it be confirmed that the 5 year fixed electrical wiring test was undertaken on the electrical circuits of the electrical supply board in this area on the 17th November 2014. The date the other parts of this building were tested? If no electrical fixed wiring test has been undertaken in the last 5 years then one should be undertaken with any defects found rectified. | Neighbourhood Management | Martin Barr |  | ESA opened the cupboard and test was carried out on 17th November 2014 | 2015-09-18 | Fully Completed | Martin Barr | 2015-09-01 12:03 | 2015-09-22 12:05 | 2015-09-01 12:03 | 2015-09-21 14:55 | -21 | In target
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:05 | S217010820001 | BRUCE HOUSE | 214302 | Completed | 3 | High | Miscellaneous | The fire fighter entry over ride device fitted to the entrance gate of this building between flats 2 and 3 did not function and release the locking device on the gate. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride device fitted to this entrance gate should be repaired or replaced so that it releases the locking device fitted to the gate. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. Is this now resolved? | Neighbourhood Management | Martin Barr |  | This was checked by ESA on 14/09/15 and fire over ride switch worked without any issue | 2015-09-14 | Fully Completed | Martin Barr | 2015-09-01 12:05 | 2015-09-22 12:07 | 2015-09-01 12:05 | 2015-09-21 14:56 | -21 | In target
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:08 | S217010820001 | BRUCE HOUSE | 214304 | Completed | 12a | High | Miscellaneous | No access could be gained to the electrical room/cupboard between flats 2 and 3, the door could not be opened and the door frame of this area appears to be coming away from the brick work. There are holes in the door frame where an electrical cable has been passed through the frame and repairs not undertaken. | I would recommend that this door frame is checked and repaired or replaced as necessary so that the door can be opened, the door frame does not have holes in it and the door frame is fixed firmly to the brick work around the door opening. If access is available could this treated as a responsive repair | Neighbourhood Management | Martin Barr |  | ESA confirms that the brick work and holes were repaired around the door frame and the intake cupboard is now ok. | 2015-09-18 | Fully Completed | Martin Barr | 2015-09-01 12:08 | 2015-09-22 12:09 | 2015-09-01 12:08 | 2015-09-21 14:58 | -21 | In target
BRUCE HOUSE - 2015.07.16 | 2015-09-01 12:32 | S217010820001 | BRUCE HOUSE | 214311 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-01 12:32 | 2015-09-22 12:33 | 2015-09-01 12:32 | 2015-09-17 12:13 | -21 | In target
BRUNEL HOUSE - 2015.01.28 | 2015-02-03 11:58 | S217000980001 | BRUNEL HOUSE | 181593 | Completed | 23c | High | Inspection Regime | It appears that the monthly occupier tests and inspections of the emergency lighting, fire extinguishers and buildings structure etc in this building are not being undertaken. | Can it be confirmed that the monthly occupier testing and inspections of the emergency lighting, fire extinguishers and other items in this building are being undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson |  | Jimmy (ESA) confirms regualr inspections undertaken & recorded on PDA | 2015-09-30 | Fully Completed | Janice Wray | 2015-02-03 11:58 | 2015-02-24 11:59 | 2015-02-03 11:58 | 2015-10-01 16:51 | -21 | In target | 2015-02-03 11:58 | 2015-10-07 16:50 | Janice Wray
BURGESSFIELD-2013.06.20 | 2013-08-30 15:00 | S217010650001 | BURGESS FIELDS | 104238 | Completed | 23d | High | Inspection Regime | There are no records of the monthly occupiers tests and inspections of the emergency lighting system, fire extinguishers etc , these tests are being undertaken by the caretaker according to the manager. | I would recommend that copies of the caretakers checklist are kept on site so that it can be proven that these tests and checks are being undertaken. | Neighbourhood Management | Martin Barr |  | Block check records are kept electronically for the time being. They can be provided if needed. In future we hope to have checks completed on PDAs whilch will automatically log the records against the block files on the EDM system. | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-30 15:00 | 2013-09-20 15:01 | 2013-08-30 15:00 | 2013-11-08 14:48 | -21 | In target
BURLEIGH HOUSE, BEAUFORT STREET, LONDON SW3 5BE - 2016.02.11 | 2016-04-04 15:40 | S217000310002 | BURLEIGH HOUSE BEAUFORT STREET | 252382 | Completed | 8 | High | Communal Area Storage | On the staircase half landing below flats 16 to 18 there is an item of furniture with books and folders etc on it. Along with pots of plants. | This item of furniture and all the books, folders and plants should be removed from this half landing area. The staircase half landings should be free of all storage. The pots of plants on the landing area outside flats 16 to 18 are acceptable but the plants must not obstruct the staircase. | Neighbourhood Management | Nicola Rees | 2016-05-09 | Email sent to Jimmy 11.4.16 who confirmed on 14.04.16 that this is no longer there. | 2016-04-15 | Fully Completed | Nicola Rees | 2016-04-04 15:40 | 2016-04-25 15:43 | 2016-04-04 15:40 | 2016-04-18 17:34 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:32 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134514 | Completed | 2 | Medium | Signage | Some of the "No Smoking" signs displayed in this building are defaced, damaged or missing. | New "No Smoking" signs should be displayed in this building where the old ones are defaced, damaged or missing. THIS APPLIES TO BOTH BLOCKS | Neighbourhood Management | Janice Jones |  | Signs now in place | 2015-07-03 | Fully Completed | Janice Wray | 2014-03-13 15:32 | 2014-05-12 15:34 | 2014-03-13 15:32 | 2015-07-06 16:04 | -60 | In target | 2014-03-13 15:32 | 2015-07-10 16:03 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:39 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134517 | Completed | 8a | High | Inspection Regime | In the electrical cupboards there are old tins of paint, cardboard boxes with old light fittings in them and some contractors waste. | I would recommend that all the electrical cupboards are emptied out of all storage. | Neighbourhood Management | Janice Jones |  | Another for the Robert to progress please - completed | 2015-06-19 | Fully Completed | Janice Wray | 2014-03-13 15:39 | 2014-04-03 15:40 | 2014-03-13 15:39 | 2015-06-22 16:33 | -21 | In target | 2014-03-13 15:39 | 2015-06-26 16:32 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:40 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134519 | Completed | 8b | High | Inspection Regime | In the residents storage areas off the 3rd floor level corridor have a lot of waste, old broken furniture or rubbish in them as well personnel belonging's | I would recommend that the storage areas are tidied up and any old/damaged furniture and waste is removed from these areas. | Neighbourhood Management | Janice Jones | 2014-05-06 | Believe you are already progressing this - are these areas to be cleared & taken out of use for storage? Please confirm when these areas are cleared Housing Manager confirms residents were instructed to clear these areas an this has been completed. ESA to monitor | 2016-02-05 | Fully Completed | Janice Wray | 2014-03-13 15:40 | 2014-04-03 15:42 | 2014-03-13 15:40 | 2016-02-08 09:30 | -21 | In target | 2014-03-13 15:40 | 2016-02-12 09:29 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 15:44 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134521 | Completed | 12a | High | Miscellaneous | 12a High The 4 resident's storage areas off the 3rd floor level corridor are not separated from the corridor by fire rated materials. Presently there are wire mesh fences with wire mesh gates separating these storage areas from the corridor. | I would recommend that the 4 residents storage areas are separated off from the corridor using a minimum of 30 minute fire rated materials. This is so that the corridor is a fire protected structure and if a fire was to start in one of these store areas then the corridor would not become smoke logged and would be maintained free to use by the residents who may wish to leave their dwelling or the building. Alternatively these 4 storage areas could be emptied out, locked shut and maintained free of all storage. Siobhan Rumble advises that these areas are to be cleared so this work will not be required, however removal must be given priority | Neighbourhood Management | Janice Jones | 2014-05-06 | Hi Janice I spoke to Siobhan about this and I beleive the plan is to take these areas out of use for storage. Could you please update me on progress with this and what is the anticipated timescale for completion Hosuing Manager confirms residents instructed to clear these areas - now complete. ESA to monitor Please fully complete action when areas have cleared | 2016-02-05 | Fully Completed | Janice Wray | 2014-03-13 15:44 | 2014-04-03 15:45 | 2014-03-13 15:44 | 2016-02-08 09:33 | -21 | In target | 2014-03-13 15:44 | 2016-02-12 09:31 | Janice Wray
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:02 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134543 | Completed | 23b | High | Inspection Regime | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. Are these included in the Inspectors regular checks? | Neighbourhood Management | Siobhan Rumble |  | there are no fire alarms in the buldings except Grenfell Tower | 2014-03-18 | Fully Completed | Siobhan Rumble | 2014-03-13 16:02 | 2014-04-03 16:04 | 2014-03-13 16:02 | 2014-03-19 16:01 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:09 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134546 | Completed | 23e | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. Please confirm that Inspectors are carrying out these checks NOTE: THIS APPLIES TO BOTH BLOCKS | Neighbourhood Management | Siobhan Rumble |  | these are done by RGE 6 monthly under contract. inspectors check the block lighting to check if all bulbs and emergency lighting are working and records are kept | 2014-03-18 | Fully Completed | Siobhan Rumble | 2014-03-13 16:09 | 2014-04-03 16:15 | 2014-03-13 16:09 | 2014-03-19 16:03 | -21 | In target
CAMELFORD AND UPPER CAMELFORD WALKS, 2013 .12..20 | 2014-03-13 16:15 | S217011760002 | CAMELFORD WALK LOWER 1-9 & UPPER 1-20 | 134548 | Completed | 23f | High | Fire Extinguisher | Are the monthly occupier tests and inspections of the fire extinguishers and building being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. Please confirm that the Inspectors are carrying out these checks NOTE: THIS APPLIES TO BOTH BLOCKS | Neighbourhood Management | Siobhan Rumble |  | fire extinguishers where to all be removed as H&S said the intakes do not require them, Grenfell Tower has them because we have offices. | 2014-03-18 | Fully Completed | Siobhan Rumble | 2014-03-13 16:15 | 2014-04-03 16:17 | 2014-03-13 16:15 | 2014-03-19 16:05 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 14:55 | S217007500001 | CAMPDEN HOUSES | 271076 | Active | 1b | High | Miscellaneous | It is not known if there are any portable electrical appliances in the cleaners room located next to flat 109. | If there are any portable electrical appliances in the cleaner's room located next to flat 109 have these portable electrical appliances in date PAT testing labels on them? If not they should be PAT with any items that fail being repaired or replaced. Can John advise on this please & let Janice know? | Neighbourhood Management | Nicola Rees | 2016-10-19 | These are not PAT tested. I have sent email to OCS on the 09.01.17 and also have advised Abhaya and Janice. | 2017-01-13 | Partially Completed | Nicola Rees | 2016-09-21 14:55 | 2016-10-12 14:57 | 2016-09-21 14:55 | 2017-01-16 10:53 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 15:06 | S217007500001 | CAMPDEN HOUSES | 271079 | Completed | 2 | High | Inspection Regime | On the treads of the metal staircase up to the roof level by flat 34 there is an ash tray and used smoking materials. | This ash tray and the used smoking materials should be removed and the residents of flats 32, 33 and 34 reminded that smoking is not allowed in the common parts of this building. | Neighbourhood Management | Nicola Rees | 2016-10-19 | Email sent to John 01.12.16. Robert Regan has checked this area today (17.01.17) and also I have checked this a couple of weeks ago. Nothing noted on both visits. Door knock completed and residents advised that they dont smoke. | 2017-01-17 | Fully Completed | Nicola Rees | 2016-09-21 15:06 | 2016-10-12 15:08 | 2016-09-21 15:06 | 2017-01-18 16:39 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 15:17 | S217007500001 | CAMPDEN HOUSES | 271081 | Completed | 8 | High | Inspection Regime | In the ground floor level electrical room opposite flat 54 there is a timber window frame and panes of glass. . | These items should be removed from this electrical room. Above these now been removed? | Neighbourhood Management | Nicola Rees | 2016-10-19 | Cleaning order raised 01.12.16 and email sent to ESA. I noticed this at inspection last week and escalated order NR 16.01.17. The contents have now changed and is now cleaning products -email sent to the cleaning team to advise of concerns. We will continue to monitor this area. | 2017-01-17 | Fully Completed | Nicola Rees | 2016-09-21 15:17 | 2016-10-12 15:40 | 2016-09-21 15:17 | 2017-01-18 17:02 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 16:22 | S217007500001 | CAMPDEN HOUSES | 271092 | Completed | 14b | High | Inspection Regime | A ceiling tile has been removed and a cable installed above flat 89's flat entrance door. | What is this cable? Where does it go? Have any compartment walls been breached? Why has the ceiling tile not been replaced correctly? Can John investigate please ? | Neighbourhood Management | Nicola Rees | 2016-10-19 | Robert Regan has advised that the cable is BT wires going into a false ceiling and that there's substantial BT wiring up in this area.. He has tidied this up at the ceiling level so this is replaced correctly | 2016-12-01 | Fully Completed | Nicola Rees | 2016-09-21 16:22 | 2016-10-12 16:23 | 2016-09-21 16:22 | 2017-01-18 17:05 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 16:30 | S217007500001 | CAMPDEN HOUSES | 271097 | Completed | 23d | High | Fire Extinguisher | It is not known if there are any fire extinguishers located in the cleaner's room next to flat 109. | Any fire extinguishers in the cleaners room should be serviced and tested at the same time as all the other fire extinguishers located within this building. Could John please check and advise | Neighbourhood Management | Nicola Rees | 2016-10-19 | Email sent to John 01.12.16. Phoned Napolean from OCS who is the supervisor who advised that there is no fire extinguisher in this room. | 2017-01-17 | Fully Completed | Nicola Rees | 2016-09-21 16:30 | 2016-10-12 16:31 | 2016-09-21 16:30 | 2017-01-18 09:52 | -21 | In target
CAMPDEN HOUSES, PEEL STREET, LONDON W8 7PJ - 2016.08.22 | 2016-09-21 16:32 | S217007500001 | CAMPDEN HOUSES | 271098 | Completed | 23e | High | Fire Extinguisher | It is not known if any caretaker testing and inspections of the fire fighting equipment, emergency lighting and the buildings structural items are being undertaken? | Can it be confirmed that the caretaker(s) are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Nicola Rees | 2016-10-19 | This is being completed. | 2016-12-01 | Fully Completed | Nicola Rees | 2016-09-21 16:32 | 2016-10-12 16:33 | 2016-09-21 16:32 | 2016-12-02 15:51 | -21 | In target
CAR PARK UNDER 67 ELM PARK GARDENS 2014 .1.6 | 2014-01-21 16:34 | S217001886602 | ELM PARK GARDENS PARKING (67) | 125374 | Completed | 23a | High | Miscellaneous | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, the sprinkler system and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2014-01-22 | Confirmed & completed. | 2014-01-22 | Fully Completed | Wendy Stevenson | 2014-01-21 16:34 | 2014-02-11 16:35 | 2014-01-21 16:34 | 2014-01-23 18:52 | -21 | In target
CAR PARK UNDER 7 ELM PARK GARDENS 2014.01.06 | 2014-01-31 14:34 | S217001886601 | ELM PARK GARDENS PARKING (5/7) | 127517 | Completed | 23b | High | Emergency Lighting | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, the sprinkler system and the buildings structure. | The caretakers cannot be undertaking the monthly occupier tests of the installed systems/equipment/fittings because the fire equipment is 4 years out of test date? Monthly occupiers tests of the installed systems/equipment/fittings etc must be undertaken with the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2014-02-21 | Visual inspections are taking place by the porters monthly. Safety testing needs to be referred to A & R. | 2014-02-05 | Fully Completed | Wendy Stevenson | 2014-01-31 14:34 | 2014-02-21 14:35 | 2014-01-31 14:34 | 2014-02-06 17:47 | -21 | In target
CARTON HOUSE - 2014.4.22 | 2014-05-14 11:26 | S217010050007 | CARTON HOUSE | 143683 | Completed | 11 | High |  | There is a large amount pigeon droppings in the staircase by flat 47 on the ninth floor level. These pigeon droppings are making the staircase slippery. | I would recommend that the staircase is cleaned up of all the pigeon droppings and it is investigated why there is so much guano on this staircase. There is no guano on any other part of this staircase or on the staircase at the other end of the building. Martin Barr / Chris Baker | Neighbourhood Management | Chris Baker |  | Pigeon mess cleaned and removed. | 2014-05-19 | Fully Completed | Chris Baker | 2014-05-14 11:26 | 2014-06-04 11:27 | 2014-05-14 11:26 | 2014-05-27 11:24 | -21 | In target
CARTON HOUSE - 2014.4.22 | 2014-05-14 12:01 | S217010050007 | CARTON HOUSE | 143697 | Completed | 19 | High | Miscellaneous | The dry rising main inlet valve for this building is obscured and covered over by shrubs etc and the fire service would find it hard the access this dry riser inlet. | The shrubs and plants obscuring the dry rising main inlet valve should be cut away and regular checks are made so that this inlet valve remains visible at all times. | Neighbourhood Management | Dominic Davies |  |  | 2014-10-24 | Fully Completed | Dominic Davies | 2014-05-14 12:01 | 2014-06-04 12:03 | 2014-05-14 12:01 | 2014-10-27 12:48 | -21 | In target
CARTON HOUSE - 2014.4.22 | 2014-05-14 12:04 | S217010050007 | CARTON HOUSE | 143702 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-09-05 | Fully Completed | Martin Barr | 2014-05-14 12:04 | 2014-06-04 12:05 | 2014-05-14 12:04 | 2014-09-10 11:01 | -21 | In target | 2014-05-14 12:04 | 2014-09-16 11:01 | Janice Wray
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 13:04 | S217002090001 | CECIL COURT | 257290 | Completed | 2 | High | Inspection Regime | At the roof level there is a large amount of discarded used smoking material on the open roof or in the small room next to the lift motor room. | All of the used smoking material should be removed from this external roof area including in the room next to the lift motor room. | Neighbourhood Management | Nicola Rees | 2016-05-25 | This was removed by OCS on 20.09.16. | 2016-09-20 | Fully Completed | Nicola Rees | 2016-04-28 13:04 | 2016-05-19 13:08 | 2016-04-28 13:04 | 2016-09-29 17:40 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 13:09 | S217002090001 | CECIL COURT | 257293 | Completed | 8a | High | Inspection Regime | It appears that persons are using the open external roof area for drinking sessions, please see item 2 above and there are empty beer cans, wine bottles etc and other waste and rubbish on the open external roof area and in the small room next to the lift motor room. | All of the rubbish and waste etc should be removed from this external roof area and the room next to the lift motor room including the plastic chairs. | Neighbourhood Management | Nicola Rees | 2016-05-26 | OCS have cleaned this area on 20.09.16 | 2016-09-20 | Fully Completed | Nicola Rees | 2016-04-28 13:09 | 2016-05-19 13:11 | 2016-04-28 13:09 | 2016-09-29 17:41 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 14:51 | S217002090001 | CECIL COURT | 257339 | Completed | 8a | High | Inspection Regime | It appears that persons are using the open external roof area for drinking sessions, please see item 2 above and there are empty beer cans, wine bottles etc and other waste and rubbish on the open external roof area and in the small room next to the lift motor room. | All of the rubbish and waste etc should be removed from this external roof area and the room next to the lift motor room including the plastic chairs. | Neighbourhood Management | Nicola Rees | 2016-05-26 | Completed 20.09.16 . | 2016-09-20 | Fully Completed | Nicola Rees | 2016-04-28 14:51 | 2016-05-19 14:52 | 2016-04-28 14:51 | 2016-09-29 17:42 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 14:53 | S217002090001 | CECIL COURT | 257341 | Completed | 8b | High | Inspection Regime | The roof hatch to the external roof area is not locked shut and is accessible to any occupant of this building. | The roof hatch to the external roof area should be secured locked shut, so there is no access to the external roof area unless they are authorised persons, lift engineers etc. | Neighbourhood Management | Nicola Rees | 2016-05-26 | There was additional mortice lock put on this door under 201608041. | 2016-05-23 | Fully Completed | Nicola Rees | 2016-04-28 14:53 | 2016-05-19 14:54 | 2016-04-28 14:53 | 2016-09-29 17:50 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 15:24 | S217002090001 | CECIL COURT | 257357 | Completed | 16 | High | Signage | There is escape exit sign displayed by the roof access hatch at the 5th floor level stating "Roof Escape" indicating that the residents are expected to use the metal roof level bridge to leave this building in the event of an emergency having first climbed up a pull down ladder to access the open roof. At the roof level though the emergency escape signage directs you in the opposite direction to the metal bridge, to the roof of the adjoining building. | I am assuming that the TMO are not expecting the residents of this building to use the metal bridge or climb over the open external roofs of this building as a means of escape route? I would recommend that all of the signage stating "Roof Escape" and the directional arrows on the external roof area are removed. Please see item 15b above if the TMO are going to say that there is an over the roof emergency escape route. If the over the roof escape route is not used then the "roof hatch" should be secured locked shut. Nicola - are you able to have this signage removed asap | Neighbourhood Management | Nicola Rees | 2016-05-27 | This was completed under reference 201604823 | 2016-05-06 | Fully Completed | Nicola Rees | 2016-04-28 15:24 | 2016-05-19 15:26 | 2016-04-28 15:24 | 2016-09-29 17:47 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 16:28 | S217002090001 | CECIL COURT | 257401 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of this building. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building? If he is, has it been recorded that the battery domestic detectors in this building are hanging off the ceilings or have the batteries removed and that there is all the waste and rubbish on the external roof? | Neighbourhood Management | Nicola Rees | 2016-05-27 | The esa has been completing inspections but concerns noted and raised with esa. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-04-28 16:28 | 2016-05-19 16:29 | 2016-04-28 16:28 | 2017-01-16 09:26 | -21 | In target
CECIL COURT, FAWCETT STREET, LONDON SW10 9HP - 2016.03.26 | 2016-04-28 16:31 | S217002090001 | CECIL COURT | 257404 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency escape lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-05-27 | This is being completed. | 2016-11-08 | Fully Completed | Nicola Rees | 2016-04-28 16:31 | 2016-05-19 16:33 | 2016-04-28 16:31 | 2016-11-09 15:40 | -21 | In target
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 10:49 | S217012760007 | CHELSEA FARM HOUSE | 274028 | Active | 0 | Information Only | Miscellaneous | The third floor level studios in this building are now being used as artists studios/workshops not as residential dwellings. | I would recommend that the buildings file is checked to see that the following information is contained within it. 1. That there is a planning application for change of use from residential to commercial use. 2. A Buildings Regulations completion Certificate has been issued by the Building Control Body for any work undertaken. 3. New Electrical certificates for any electrical wiring work undertaken. If any of the information is missing this should be asked for from the relevant person/authority. This is so that if this building is audited by the Fire Authority under the Fire Safety Order documentation can be provided. | Neighbourhood Management | Nick Rendle | 2017-12-20
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 10:52 | S217012760007 | CHELSEA FARM HOUSE | 274029 | Active | 17 | High | Smoke Alarms | It is not known if the studios on the third floor level have any automatic smoke or heat detection within them. | Can it be confirmed that the 6 studios on the third floor level have appropriate automatic heat and smoke detection within them along with warning devices? This item should be covered in the studio's FRAs. Nick | Neighbourhood Management | Nick Rendle | 2017-01-17
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 10:57 | S217012760007 | CHELSEA FARM HOUSE | 274030 | Active | 18 | High | Fire Extinguisher | It is not known if the studios on the third floor level have any fire extinguishers or fire blankets etc provided within in them appropriate to the risk or hazard within each unit. This is because the TMO does not provide fire fighting equipment in the common parts of its residential buildings. | Can it be confirmed by RBKC that the 6 studios on the third floor level have appropriate fire extinguishers or fire blankets etc provided within them suitable to the hazards in the rooms and that the occupants of these studios are suitably trained to use the equipment provided. This item should be covered in the studio's FRAs. | Neighbourhood Management | Nick Rendle | 2017-01-17
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 11:14 | S217012760007 | CHELSEA FARM HOUSE | 274032 | Active | 20 and 21 | High | Miscellaneous | Fire training etc and all management policies, procedures and arrangements for the occupiers of the 6 third floor studios. | Can it be confirmed that fire risk assessments for the individual studios cover all the management policies, procedures and training etc required by the Regulatory Reform (Fire Safety) Order 2005. | Neighbourhood Management | Nick Rendle | 2017-01-17
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 11:16 | S217012760007 | CHELSEA FARM HOUSE | 274033 | Active | 22a | High | Miscellaneous | The person responsible in RBKC for leasing the 6, third floor level studios should be asked for the each studio occupier's Fire Risk Assessments and significant findings. This is so any hazards or risks identified can be assessed by the TMO including any flammable or dangerous substances connected with painting etc. | Ask RBKC for the 6 individual studios Fire Risk Assessments and significant findings. | Neighbourhood Management | Nick Rendle | 2017-01-17
CHELSEA FARM HOUSE AND STUDIOS, MILMAN STREET, LONDON SW10 0BY - 2016.11.21 | 2016-12-20 11:18 | S217012760007 | CHELSEA FARM HOUSE | 274034 | Active | 22b | High | Miscellaneous | The relevant parts of these significant findings of this FRA should be passed on to the appropriate person within RBKC so that they can co-ordinating the actions required for the occupiers of the studios and so that the studio occupiers know their evacuation strategy etc. | Pass on any relevant information from these significant findings to the appropriate person within RBKC so that they can inform the individual studio occupiers. | Neighbourhood Management | Nick Rendle | 2017-01-17
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 15:48 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102310 | Completed | 8a | High | Miscellaneous | On the 12th floor level flat/lift lobby area old pieces of carpet have been laid on the floor in an haphazard way. This in not a single piece of carpet and could be a trip hazard. | I would recommend that these old pieces of carpet are removed as they are not laid level or secured in any way so persons and could be a trip hazard. . | Neighbourhood Management | Wendy Stevenson | 2013-09-06 | ESA Felix Akumanyi spoke to the resident of Flat 43 on 6th Sept 2013 but she refuses to remove the carpet as it has been there for 10 years. Neighbourhood Team Leader Olivia Hutchison has agreed to write to the resident. I have written to all residents on 13th Floor advising that we will be removing the carpet tiles on the week beginning 20th January. Please re-allocate to Wendy so Estate Services can arrange removal of carpet tiles. Some confusion as assessor only requires regualr inspection & monitoring of carpet tiles on 13th floor. Included in regular inspections. | 2014-01-20 | Fully Completed | Wendy Stevenson | 2013-08-16 15:48 | 2013-09-06 15:50 | 2013-08-16 15:48 | 2014-01-21 14:46 | -21 | In target | 2013-08-16 15:48 | 2014-01-27 14:45 | Janice Wray
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 15:52 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102311 | Completed | 8b | Medium | Communal Area Storage | There is contractors waste and combustible material, old kitchen unit, stored in the double riser cupboards on the 1st, 3rd and 5th floor level flat/lift lobby areas. | I would recommend that all the contractors waste and other material is removed from these riser cupboards. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc has been removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | All clear. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 15:52 | 2013-10-15 16:06 | 2013-08-16 15:52 | 2013-10-16 16:12 | -60 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:06 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102320 | Completed | 8c | Medium | Communal Area Storage | On the 7th floor level flat/lift lobby area there is an old wardrobe, rolled up pieces of old carpet and two bedside units. | The items of furniture and carpet should be removed from this flat/lift lobby area and the owner (s) of them reminded that items should not be stored on the flat/lift lobby areas. | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | All clear. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:06 | 2013-10-15 16:15 | 2013-08-16 16:06 | 2013-10-16 16:13 | -60 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:15 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102322 | Completed | 8d | Medium | Communal Area Storage | On the 13th floor level there are household items in bags on the floor next to the refuse chute. | These bags of household items should be removed from the flat/lift lobby area. | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | All clear. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:15 | 2013-10-15 16:17 | 2013-08-16 16:15 | 2013-10-16 16:12 | -60 | In target
CHELSEA REACH TOWER - 2013.04.01 | 2013-08-16 16:21 | S217012740016 | CHELSEA REACH TOWER 1-65 | 102330 | Completed | 8f | Low | Miscellaneous | The majority of the flat/lift lobby area on floor level 13 has been covered with carpet tiles, at present this floor covering is in good condition and well fitted and does not I believe pose any type of hazard. But the floor covering could deteriorate and become a trip hazard. | I would recommend that the floor covering on this floor level is monitored by the caretakers on their monthly inspections and if it becomes a trip hazard or an obstruction then the carpet tiles are removed or re-fixed/repaired. | Neighbourhood Management | Wendy Stevenson | 2014-02-12 | Can you please just confirm the frequency of the ESAs inspections in this area and that this items is being monitored as part of these. Inspections are 3 times per week. The ESA Felix has been asked to keep an eye on this area of carpet. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:21 | 2014-02-12 16:24 | 2013-08-16 16:21 | 2013-10-16 14:41 | -180 | In target
CHELSEA REACH TOWER, BLANTYRE STREET, LONDON SW10 0EG - 2016.08.05 | 2016-09-20 10:46 | S217012740016 | CHELSEA REACH TOWER 1-65 | 270949 | Completed | 8a | High | Inspection Regime | There are cardboard boxes, black plastic bags and household items being stored on the 13th floor level flat/lift lobby area. | All of this combustible storage should be removed from this flat/lift lobby area. | Neighbourhood Management | Nicola Rees | 2016-10-18 | This is no longer there. | 2016-10-07 | Fully Completed | Nicola Rees | 2016-09-20 10:46 | 2016-10-11 10:48 | 2016-09-20 10:46 | 2016-10-12 12:07 | -21 | In target
CHELSEA REACH TOWER, BLANTYRE STREET, LONDON SW10 0EG - 2016.08.05 | 2016-09-20 10:53 | S217012740016 | CHELSEA REACH TOWER 1-65 | 270952 | Completed | 8b | Information Only | Inspection Regime | The majority of the 13th floor level flat/lift lobby area has been covered with square carpet tiles, at present this floor covering is in good condition and well fitted and does not I believe pose any type of hazard. But the floor covering could deteriorate, lift etc and become a trip hazard. | I would recommend that the floor covering on this floor level is monitored by the caretakers on their monthly inspections and if it becomes a trip hazard by lifting or being damaged then the laminate flooring should be repaired or removed. | Neighbourhood Management | Nicola Rees | 2017-09-20 | The ESA has been advised of this advice on the 07.10.16 at 1:1. | 2016-10-07 | Fully Completed |  |  |  | 2016-09-20 10:53 | 2016-10-12 12:08
CHELSEA REACH TOWER, BLANTYRE STREET, LONDON SW10 0EG - 2016.08.05 | 2016-09-20 15:20 | S217012740016 | CHELSEA REACH TOWER 1-65 | 270993 | Active | 13d | High | Mobility Scooters | At the time of this assessment there was a mobility scooter parked on the 13th floor level flat/lift lobby area. | Does the TMO know that there is a mobility scooter parked on this flat/lift lobby area? Can it please be confirmed that this mobility scooter is not being charged on this flat/lift lobby area. Queried with Nicola - 14th Sept | Neighbourhood Management | Nicola Rees | 2016-10-18
CHELSEA REACH TOWER, BLANTYRE STREET, LONDON SW10 0EG - 2016.08.05 | 2016-09-20 15:42 | S217012740016 | CHELSEA REACH TOWER 1-65 | 271005 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and checks on the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-10-18 | These are sent and being undertaken. | 2016-10-14 | Fully Completed | Nicola Rees | 2016-09-20 15:42 | 2016-10-11 15:43 | 2016-09-20 15:42 | 2016-10-17 17:32 | -21 | In target
CHESTERTON SQUARE, PEMBROKE ROAD, LONDON W8 6PH. - 2016.10.25 | 2016-12-20 12:06 | S217011780001 | CHESTERTON SQUARE 1-92 | 274049 | Active | 23e | High | Inspection Regime | Are the occupier's monthly tests and inspections of the fire extinguishers, doors etc in this building being undertaken as per the caretakers check list? | Can it please be confirmed that the occupier's monthly tests and inspections of the fire extinguishers etc in this building being undertaken as per the caretakers check list? | Neighbourhood Management | Nicola Rees | 2017-01-17 |  |  |  | Cyril Morris | 2016-12-20 12:06 | 2017-01-10 12:08 |  |  | 58 | 58 days overdue
CLYDESDALE HOUSE, 255 WESTBOURNE PARK ROAD, LONDON W11 1ED - 2016.08.18 | 2016-09-21 11:35 | S217010570001 | CLYDESDALE HOUSE | 271048 | Active | 8a | High | Inspection Regime | On the 2nd floor level staircase landing area outside flat 15 there are items of household furniture. | These items of furniture should be removed from the staircase landing area outside flat 15. The residents should be reminder that the common parts should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading of the staircase enclosure is kept as low as possible. | Neighbourhood Management | Louise Nezandonyi | 2016-10-19
CLYDESDALE HOUSE, 255 WESTBOURNE PARK ROAD, LONDON W11 1ED - 2016.08.18 | 2016-09-21 11:39 | S217010570001 | CLYDESDALE HOUSE | 271049 | Active | 8b | Medium | Inspection Regime | The front garden area of flat 6 is untidy, it has black bags of rubbish in it and a lot of old wood and other old household items. | The front garden area of flat 6 should be cleared up with all the rubbish and waste removed. | Neighbourhood Management | Louise Nezandonyi | 2016-12-07
CLYDESDALE HOUSE, 255 WESTBOURNE PARK ROAD, LONDON W11 1ED - 2016.08.18 | 2016-09-21 12:45 | S217010570001 | CLYDESDALE HOUSE | 271061 | Active | 23e | High | Inspection Regime | Are the monthly occupier tests and inspections being undertaken within this building, monthly inspections of the fire fighting equipment along with the other items on the caretakers checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-10-19
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 14:18 | S217010570001 | CLYDESDALE HOUSE | 102862 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire fighting equipment in the building being undertaken along with the other items on the caretakers checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Checks undertaken as per the current checklist. This process is to be reviewed before implementing an electronic system for recording checks. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 14:18 | 2013-09-10 14:21 | 2013-08-20 14:18 | 2013-10-14 11:41 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 13:19 | S217010570001 | CLYDESDALE HOUSE | 102835 | Completed | 8a | High | Communal Area Storage | On the 2nd floor level balcony outside flats 12 and 13 there are old broken chairs, tins of paint and two other items of furniture. n. | These items should be removed from this balcony area, the pots of plants near to these items can remain as long as the plants are kept against the wall of the building and are not causing an obstructio | Neighbourhood Management | Martin Barr |  | Items have been removed apart from plants, confirmed by inspection | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 13:19 | 2013-09-10 13:29 | 2013-08-20 13:19 | 2013-10-14 11:40 | -21 | In target
CLYDESDALE HOUSE-2013.06.14 | 2013-08-20 13:30 | S217010570001 | CLYDESDALE HOUSE | 102838 | Completed | 8b | High | Communal Area Storage | On the 2nd floor level staircase landing area outside flat 15 there are two items of household furniture. | These two items of furniture should be removed from the staircase landing area outside flat 15. The residents should be reminder that the common parts should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading of the staircase enclosure is kept as low as possible. | Neighbourhood Management | Martin Barr |  | There is one small wicker chair which does not extend further out that many of the pot plants kept outside flats. It has been there some time, is in use and does not attract any further items around it, therefore we have taken the decision to allow this item to remain. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 13:30 | 2013-09-10 13:34 | 2013-08-20 13:30 | 2013-10-14 14:39 | -21 | In target
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 10:03 | S217010050003 | COPPERFIELD HOUSE | 157994 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting systems in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 10:03 | 2014-09-09 10:04 | 2014-08-19 10:03 | 2014-09-01 16:23 | -21 | In target
COPPERFIELD HOUSE - 2014.08.05 | 2014-08-19 10:05 | S217010050003 | COPPERFIELD HOUSE | 157995 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 10:05 | 2014-10-18 10:06 | 2014-08-19 10:05 | 2014-09-01 16:23 | -60 | In target
CORBETT HOUSE - 2015.06.11 | 2015-06-15 11:18 | S217000750001 | CORBETT HOUSE | 201477 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | Confirmed / complete. | 2015-06-18 | Fully Completed | Wendy Stevenson | 2015-06-15 11:18 | 2015-07-06 11:19 | 2015-06-15 11:18 | 2015-06-19 17:21 | -21 | In target
CRAIGIE VILLAS, TADEMA ROAD, LONDON SW10 0PZ - 2015.12.15 | 2016-02-08 16:52 | S217005360017 | CRAIGIE VILLAS | 242043 | Active | 23b | High | Inspection Regime | Is the monthly occupiers test and inspection of the emergency lighting unit installed within this building being undertaken with records kept? | Monthly occupier testing and inspection of the emergency lighting unit in the ground floor level entrance hall area of this building should be undertaken, With the results of the testing etc recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-03-01 |  |  |  | Cyril Morris | 2016-02-08 16:52 | 2016-02-29 16:54 |  |  | 374 | 374 days overdue
CREMORNE CLUB ROOM-2013.08.03 | 2013-08-23 15:11 | U217012760245 | TMO CLUBROOM CREMORNE SHELTERED CLUBROOM | 103572 | Completed | 8 | Medium | Communal Area Storage | The boiler room is also used for storage, there are no items stored on the boiler or next to it but the storage in this room is untidy. | I would recommend that the storage in the boiler room is tidied up and any old and unwanted items are removed. | Neighbourhood Management | Hash Chamchoun | 2013-10-22 | Referred to Hash Chamchoun Confirmation that contents have been sorted and clearance has completed on 17th Sept. | 2013-09-17 | Fully Completed | Wendy Stevenson | 2013-08-23 15:11 | 2013-10-22 15:15 | 2013-08-23 15:11 | 2013-09-25 11:00 | -60 | In target | 2013-08-23 15:11 | 2013-09-24 11:09 | Hash Chamchoun
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 13:29 | S217003310001 | CURRAN HOUSE | 200500 | Completed | 12 | Low | Communal Area Storage | On the 4th floor level balcony there are a lot of plants in pots etc, these could restrict the width of this walkway/balcony, causing an obstruction and they could be a trip hazard. | I would recommend that the caretaker is asked to monitor this situation. If the plants start to cause an obstruction or become a trip hazard then some of them should be removed. | Neighbourhood Management | Kamran Hye |  | completed by Felix Akumany Items near flat 12- stickers were put on last week. I will chick it this week if items are still there, I will arrange for OCS to remove them. | 2015-06-26 | Fully Completed | Jimmy Lemos | 2015-06-08 13:29 | 2015-12-05 13:30 | 2015-06-08 13:29 | 2015-07-13 15:24 | -180 | In target
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 14:01 | S217003310001 | CURRAN HOUSE | 200507 | Completed | 14B | Information Only | Inspection Regime | There was no access to the ground floor garages under the 1st floor level studio's. | I would recommend that these garages are checked to see what they are used for and to see that the storage in them is not excessive as there is sleeping accommodation above them. Also that the roof/floor slab between the garages and the studios has no holes of gaps in it that would allow the passage of heat or smoke etc up to the residential areas from the garages. | Neighbourhood Management | Kamran Hye |  | completed by Felix Akumani | 2015-07-01 | Fully Completed |  |  |  | 2015-06-08 14:01 | 2015-07-29 16:35 |  |  | 2015-06-08 14:01 | 2015-08-04 16:35 | Janice Wray
CURRAN HOUSE AND STUDIOS - 2015.05.22 | 2015-06-08 14:07 | S217003310001 | CURRAN HOUSE | 200514 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | Fire Extinguishers - job sent to repairs department completed by Felix Akumani ESA | 2015-06-26 | Fully Completed | Jimmy Lemos | 2015-06-08 14:07 | 2015-06-29 14:09 | 2015-06-08 14:07 | 2015-07-13 15:26 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:39 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181403 | Completed |  | High |  | There is an office within this area which has a locked door and there appears to be no key to unlock this door. No access has been gained to this office in years I am told. | I would recommend that the key to this office is found or the lock changed so that an inventory of any contents of this office can be produced and any portable electrical appliance found etc can be tested. Hash - do you have the key for this? | Neighbourhood Management | Hash Chamchoun |  | This is no longer used by the Supported Housing Team. Locks changed by Community Centre Officer | 2015-06-26 | Fully Completed | Janice Wray | 2015-02-02 15:39 | 2015-02-23 15:41 | 2015-02-02 15:39 | 2015-06-29 12:39 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:45 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181409 | Completed | 13 | High |  | There is an emergency pull cord located in the toilet of this building, it is not known if this emergency pull cord is tested weekly in accordance with the manufacturers guidance. | Can it please be confirmed that the emergency pull cord located in the toilet, with an indicator light above the toilet door and a control panel on the wall is being tested weekly in accordance with the manufactures instructions and that records are kept? | Neighbourhood Management | Hash Chamchoun |  | Pullcord system has now been disconnected as this room is no longer used by the Supported Housing Team | 2015-06-26 | Fully Completed | Janice Wray | 2015-02-02 15:45 | 2015-02-23 15:52 | 2015-02-02 15:45 | 2015-06-29 12:51 | -21 | In target
DACRE HOUSE COMMUNITY ROOM - 2014.10.14 | 2015-02-02 15:54 | S217000310008 | DACRE HOUSE COMMUNITY CENTRE | 181414 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Wendy Stevenson |  | inspected 16/03/15 4 extinguishers last inspected 12/2014 | 2015-05-07 | Fully Completed | Janice Wray | 2015-02-02 15:54 | 2015-02-23 15:55 | 2015-02-02 15:54 | 2015-05-11 09:57 | -21 | In target
DACRE HOUSE, BEAUFORT STREET, LONDON SW3 5BH - 2016.02.11 | 2016-04-04 14:35 | S217000310003 | DACRE HOUSE | 252349 | Completed | 3 | Information Only | Miscellaneous | By the end wall of the estate near to the cleaners hut, there are old items of furniture, white goods, fridges etc and some other bulk items, these are awaiting collection to be disposed of. | These items are located away from this building but I would recommend that regular collection of these bulk items is undertaken so that items are not left here for long periods of time. It is better to have regular collections to minimise the amount of items and combustible waste located on site. | Neighbourhood Management | Nicola Rees | 2016-07-11 | This is completed as and when needed by ESA and there may be future developments to have it on a regular route via cleaning contractor. | 2016-04-11 | Fully Completed |  |  |  | 2016-04-04 14:35 | 2016-04-12 16:58
DARFIELD WAY FLATS 2 TO 27 - 2015.08.13 | 2015-09-02 14:56 | S217008566606 | DARFIELD WAY 2-9 | 214590 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in these buildings, with the completed sheets/records kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-02 14:56 | 2015-09-23 14:57 | 2015-09-02 14:56 | 2015-09-17 11:23 | -21 | In target
DARTREY TOWER - 2013.03.01 | 2013-08-20 15:26 | S217012740006 | DARTREY TOWER 1-49 | 102905 | Completed | 8a | Medium | Communal Area Storage | There are private household items being stored in the flat/lift lobby area riser cupboards on the 11th, 13th and 17th floor levels. Also contractors waste is being stored in the 6th floor level cupboards. | I would recommend that all the household items and waste/rubbish is removed from these riser cupboards. | Neighbourhood Management | Wendy Stevenson | 2013-10-17 | We issued this one in advance of the workflow and you provided the following info. Please confirm that all these orders are now completed 16th flr - PC desk dumped - cleaners REMOVED COMPLETED 16th flr - lhs EIC GB lock to be changed - order 201305183 COMPLETED 9th flr - EIC needs FB lock changed - 201305183 COMPLETED 5th flr - EIC - lock change needed - 201305183 COMPLETED Refuse is now removed from 11th and 13th and 17th floors. Order raised 18th Oct for refuse to be removed from 6th floor - COMNPLETED. | 2014-01-08 | Fully Completed | Wendy Stevenson | 2013-08-20 15:26 | 2013-10-19 15:36 | 2013-08-20 15:26 | 2014-01-10 09:57 | -60 | In target | 2013-08-20 15:26 | 2014-01-16 09:56 | Janice Wray
DARTREY TOWER - 2013.03.01 | 2013-08-20 15:37 | S217012740006 | DARTREY TOWER 1-49 | 102914 | Completed | 8b | Medium | Communal Area Storage | On the 5th floor level flat/lift lobby area there is a plastic garden type shed and some sets of step ladders. | Have the TMO given permission of a plastic storage shed to be located on this flat/lift lobby area? Along with sets of step ladders. If the occupant of flat 3 does not have permission to have this shed here it should be removed. | Neighbourhood Management | Olivia Hutchison | 2013-09-17 | Has permission been given to the occupant of flat 3 for this to be stored here? | 2013-10-14 | Fully Completed | Olivia Hutchison | 2013-08-20 15:37 | 2013-10-19 15:42 | 2013-08-20 15:37 | 2013-10-29 13:51 | -60 | In target
DARTREY TOWER, ON THE WORLDS END ESTATE, BLANTYRE STREET, LONDON SW10 0EB - 2016.07.28 | 2016-08-31 12:56 | S217012740006 | DARTREY TOWER 1-49 | 270331 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-09-27 | Monthly H+S checks are sent every month to the team for these to be completed. | 2016-10-10 | Fully Completed | Nicola Rees | 2016-08-31 12:56 | 2016-09-21 12:57 | 2016-08-31 12:56 | 2016-10-11 16:35 | -21 | In target
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:16 | S217008560001 | DIXON HOUSE | 244892 | Active | 1 | High | Miscellaneous | At the time of this assessment the lights were not working in the 2 bulk storage rooms of this building. | I would recommend that the lights in these two bulk storage rooms are checked and repairs undertaken so that the lights work. Raised with Raymond Hylton | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | Janice has siad nthat she will chase Raymond Hylton on this - I have also emailed Os the ESA to find out if the repair has been done. | 2016-03-09 | Partially Completed | Louise Nezandonyi | 2016-02-22 14:16 | 2016-03-14 14:18 | 2016-02-22 14:16 | 2016-03-10 11:01 | -21 | In target
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:31 | S217008560001 | DIXON HOUSE | 244897 | Completed | 12e | High | Miscellaneous | There are cold smoke seals fitted to the self closing fire doors off the flat/lift lobby areas to the refuse chute balcony and on to the lobby area before the staircase and on to the staircase. Some of these cold smoke seals are damaged or there are pieces missing. | As the TMO have fitted fire doors with cold smoke seals to these areas they must be maintained to the standard as when the doors were installed. All missing and damaged cold smoke seals should be replaced. Spoke to Owaldo and he has agreed to include in his inspections | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | Spoken to Janice Wray she will be speaking to Carl about this for further clarity and then will update us | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-22 14:31 | 2016-03-14 14:34 | 2016-02-22 14:31 | 2016-09-01 20:16 | -21 | In target | 2016-02-22 14:31 | 2016-09-07 20:15 | Janice Wray
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:44 | S217008560001 | DIXON HOUSE | 244907 | Completed | 14a | High | Miscellaneous | There are metal cover plates fixed over a cable duct on the flat/lift lobby areas which provide fire stopping for the duct. It appears that contractors have removed these metal cover plates on most floor levels and not secured them back again fully thus compromising the fire stopping of the walls surface. These metal plates are heavy sheets of metal and might also fall off the wall and cause a serious injury if they were to hit a person. | These metal cover plates should be re-fixed securely back to the wall so providing suitable fire stopping for the cable duct and also to stop these heavy metal plates from falling on somebody. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all the structural elements of the buildings remain fire rated. Oswaldo has agreed to undertake this work | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | Os has confirmed that he has checkeds the whole of the block on 15/03/2016 and has raised orders with our repairs team for the whole of the block | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-22 14:44 | 2016-03-14 14:50 | 2016-02-22 14:44 | 2016-03-17 16:21 | -21 | In target
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 14:56 | S217008560001 | DIXON HOUSE | 244920 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units, fire extinguishers and sprinkler system in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting and sprinkler systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | Yes this is being tested and I recvords are being kept on insight once the cartetaker has put put through the information using his total mobile. | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-22 14:56 | 2016-03-14 14:58 | 2016-02-22 14:56 | 2016-03-10 11:59 | -21 | In target
DIXON HOUSE, 1 DARFIELD WAY, LONDON W10 6TU - 2016.01.21 | 2016-02-22 15:00 | S217008560001 | DIXON HOUSE | 244923 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | I can confirm that the caretaker is undertaking the monthly occupier check as per the caretakers check list. We haver the sheets stored on insight | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-22 15:00 | 2016-03-14 15:01 | 2016-02-22 15:00 | 2016-03-10 11:33 | -21 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:20 | S217010050004 | DOMBEY HOUSE | 158093 | Completed | 8a | High | Communal Area Storage | There is bedroom furniture being stored in the lobby area by flat 13's door and by the rear exit door to the garden area, pine bed frames etc. | These items of furniture should be removed from the staircase enclosure immediately. The children's bikes could remain in this area if the furniture was removed. If the storage of combustible items becomes a problem in this staircase enclosure and by the rear exit door in particular then I would recommend that all items are removed including the bikes and this is kept a sterile area. | Neighbourhood Management | Martin Barr |  | Confirmed as being removed 28-08-14 | 2014-08-28 | Fully Completed | Martin Barr | 2014-08-19 15:20 | 2014-09-09 15:22 | 2014-08-19 15:20 | 2014-09-01 16:26 | -21 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:22 | S217010050004 | DOMBEY HOUSE | 158095 | Completed | 8b | High | Communal Area Storage | There is numerous push bikes being stored in the lobby area by flat 19's entrance door and by the rear exit door to the garden area. | These children's bikes could remain in this area if they are neatly stacked here and they must not obstruct the means of escape route from the building. If though these bikes obstruct the means of escape route or are not kept in a tidy manor then I would recommend that they are removed. | Neighbourhood Management | Martin Barr |  | All bikes confirmed removed 28-08-14 | 2014-08-28 | Fully Completed | Martin Barr | 2014-08-19 15:22 | 2014-09-09 15:24 | 2014-08-19 15:22 | 2014-09-01 16:27 | -21 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:24 | S217010050004 | DOMBEY HOUSE | 158096 | Completed | 8c | High | Communal Area Storage | There is a metal charcoal BBQ being stored in the area by the rear exit door by flats 19 and 20. | This metal charcoal BBQ should be removed immediately. | Neighbourhood Management | Martin Barr |  | Confirmed removed 28-08-14 | 2014-08-28 | Fully Completed | Martin Barr | 2014-08-19 15:24 | 2014-09-09 15:25 | 2014-08-19 15:24 | 2014-09-01 16:30 | -21 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:26 | S217010050004 | DOMBEY HOUSE | 158097 | Completed | 8d | Medium | Communal Area Storage | There is a wooden table being stored in the electrical cupboard by flats 19 and 20. | This wooden table should be removed from this electrical cupboard which should be kept empty. | Neighbourhood Management | Martin Barr |  | table was removed. cupboard empty of all items. | 2015-06-03 | Fully Completed | Martin Barr | 2014-08-19 15:26 | 2014-10-18 15:27 | 2014-08-19 15:26 | 2015-06-04 12:48 | -60 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:41 | S217010050004 | DOMBEY HOUSE | 158107 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting systems in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 15:41 | 2014-09-09 15:43 | 2014-08-19 15:41 | 2014-09-01 16:38 | -21 | In target
DOMBEY HOUSE - 2014.08.05 | 2014-08-19 15:43 | S217010050004 | DOMBEY HOUSE | 158108 | Completed | 23c | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 15:43 | 2014-10-18 15:44 | 2014-08-19 15:43 | 2014-09-01 16:39 | -60 | In target
DORA HOUSE - 2014.7.22 | 2014-08-01 16:40 | S217010050011 | DORA HOUSE | 155717 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-01 16:40 | 2014-09-30 16:42 | 2014-08-01 16:40 | 2014-09-01 16:19 | -60 | In target
DORRIT HOUSE - 2014.7.22 | 2014-08-01 16:44 | S217010050006 | DORRIT HOUSE | 155720 | Completed | 8 | High | Communal Area Storage | There are piles of cardboard boxes located by the ground floor level rear exit of the staircase of flats 7 to 12. | These cardboard boxes should be removed from the entrance hall/lobby area. I would recommend that the tenant who owns these cardboard boxes is reminded of the no storage of combustible items rule in the staircase enclosures. | Neighbourhood Management | Martin Barr |  | Items confirmed as removed 28-08-14 | 2014-08-28 | Fully Completed | Martin Barr | 2014-08-01 16:44 | 2014-08-22 16:46 | 2014-08-01 16:44 | 2014-09-01 16:20 | -21 | In target
DORRIT HOUSE - 2014.7.22 | 2014-08-01 16:49 | S217010050006 | DORRIT HOUSE | 155722 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-01 16:49 | 2014-09-30 16:50 | 2014-08-01 16:49 | 2014-09-01 16:21 | -60 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:25 | S217010470003 | EASTRY HOUSE | 196875 | Completed | 9a | High | Communal Area Storage | In the ground floor level electrical room/ cupboard there are opened bags of plaster, cement and large clear plastic bags of contractors waste. | All of these bags and any waste and rubbish should be removed from this ground floor level electrical room/cupboard. | Neighbourhood Management | Martin Barr |  | OCS have emptied this cupboard | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-13 15:25 | 2015-06-03 15:30 | 2015-05-13 15:25 | 2015-06-04 12:48 | -21 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:55 | S217010470003 | EASTRY HOUSE | 196891 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-13 15:55 | 2015-06-03 15:56 | 2015-05-13 15:55 | 2015-05-19 11:55 | -21 | In target
EASTRY HOUSE - 2015.05.06 | 2015-05-13 15:57 | S217010470003 | EASTRY HOUSE | 196893 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-13 15:57 | 2015-06-03 15:58 | 2015-05-13 15:57 | 2015-05-19 11:56 | -21 | In target
ELGIN MEWS, NUMBERS 1 TO 24 LONDON W11 1PU - 2017.01.24 | 2017-03-02 15:06 | S217008670001 | ELGIN MEWS (1-24) | 276033 | Active | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency escape lighting units in each part of this building being undertaken with records kept? Along with the other caretaker/Estates Services Assistant checks of the buildings structure. | Monthly occupier testing and inspections of the emergency escape lighting units in each part of this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Martin Barr | 2017-04-03
ELM PARK HOUSE CAR PARK | 2014-01-02 09:45 | S217002186603 | ELM PARK HOUSE PARKING | 122267 | Completed | 23A | High | Emergency Lighting | Monthly caretaker testing and inspections of the emergency lighting system, fire fighting equipment, the sprinkler system and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of the installed systems/equipment/fittings? With the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2014-01-23 | Inspections are carried out and any observations noted, however the porters are not able to test emergency lighting, fire fighting equipment and sprinkler systems in car parks. Is this being done by A n R on a contract? | 2014-01-07 | Fully Completed | Wendy Stevenson | 2014-01-02 09:45 | 2014-01-23 09:46 | 2014-01-02 09:45 | 2014-01-08 17:03 | -21 | In target
ELM PARK HOUSE CAR PARK | 2014-01-02 09:48 | S217002186603 | ELM PARK HOUSE PARKING | 122270 | Completed | 23c | Information Only | Miscellaneous | It is proposed that the two end exits are not designated emergency escape exits. | I would recommend that these two exits are maintained free to use and the steps from the right hand side one are kept free of fallen leaves and other vegetation. | Neighbourhood Management | Wendy Stevenson | 2014-07-01 | All fire exit signs in the car park will be removed by the porters. Vegetation has been removed already. | 2014-01-08 | Fully Completed |  |  |  | 2014-01-02 09:48 | 2014-01-09 17:41
ELM PARK HOUSE, FULHAM ROAD, LONDON SW10 9QD - 2016.04.05 | 2016-05-25 16:51 | S217002180002 | ELM PARK HOUSE | 262533 | Active | 13 | High | Mobility Scooters | There is a mobility scooter located on the [redacted] floor level flat/lift lobby area by flats [redacted] and [redacted} and another on the [redacted] floor level flat/lift lobby area outside flat [redacted]. These were not causing an obstruction as the flat/lift lobby areas are quite large and there were not being charged at the time of this assessment. It is not known if the TMO have a policy on mobility scooters being in the common parts of residential buildings. | Is there a TMO policy for mobility scooters being left in the common parts of TMO residential buildings, in this case on the flat/lift lobby areas of this building? It is not known how the owners of these mobility scooters are charging these vehicles batteries. I would recommend that the owners of these two mobility scooters are asked how and where their scooters are being charged? The charging of the batteries of mobility scooters should not be undertaken on/within the common parts of residential buildings. | Neighbourhood Management | Nicola Rees | 2016-06-15 | Greg has spoken to resident of [redacted] about not charging their scooter and has advised them not to do so in communal areas. Should we get these residents to sign an agreement? Thanks | 2016-09-28 | Partially Completed | Nicola Rees | 2016-05-25 16:51 | 2016-06-15 16:52 | 2016-05-25 16:51 | 2016-09-29 18:01 | -21 | In target
ELM PARK HOUSE, FULHAM ROAD, LONDON SW10 9QD - 2016.04.05 | 2016-05-25 16:54 | S217002180002 | ELM PARK HOUSE | 262535 | Active | 23a | High | Miscellaneous | In the roof top level water tank room there is an automatic smoke detector fitted on the ceiling. Who is weekly testing this smoke detector? Where is the control panel for this BS5839 Part 1 detector and who is undertaking the servicing etc of this device and any other ones in the external Vodafone equipment hut on the external roof? | Please can it be confirmed who is testing, servicing and the owner of the installed BS 5839 Part 1 fire alarm system installed at the roof level of this building? Where is this fire alarm systems control panel? Are weekly occupiers tests of this installed fire alarm system being undertaken? Who by and who is recording these tests. Is 6 monthly servicing and inspection of this installed fire alarm system being undertaken? | Neighbourhood Management | Nicola Rees | 2016-06-15 | Porters believe this is in connection to Vodafone equipment. Could we get some further guidance? | 2016-09-06 | Partially Completed | Nicola Rees | 2016-05-25 16:54 | 2016-06-15 16:56 | 2016-05-25 16:54 | 2016-09-07 16:30 | -21 | In target
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:29 | S217010050009 | ESTELLA HOUSE | 158191 | Completed | 8 | High | Communal Area Storage | By the rear exit door near to flats 1 and 2 there are parts for a motor bike, the frame, wheels etc. A | ll of the parts of the motor bike should be removed from this staircase enclosure. The push bike located here can remain. | Neighbourhood Management | Martin Barr |  | Motorbike parts confirmed removed 28-08-14 | 2014-08-28 | Fully Completed | Martin Barr | 2014-08-20 11:29 | 2014-09-10 11:31 | 2014-08-20 11:29 | 2014-09-01 16:47 | -21 | In target
ESTELLA HOUSE - 2014.08.14 | 2014-08-20 11:37 | S217010050009 | ESTELLA HOUSE | 158198 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-20 11:37 | 2014-10-19 11:38 | 2014-08-20 11:37 | 2014-09-01 16:56 | -60 | In target
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:08 | S217008270001 | CAMBORNE MEWS (1-12) | 181043 | Completed | 8a | High | Communal Area Storage | Outside flats 5 and 6 on the staircase landing there are piles of household items in carrier bags and black bags, access to flat 6 is restricted. | All of these items should be removed from this landing areas immediately. | Neighbourhood Management | Siobhan Rumble |  | Housing Officer to speak to tenant to remove or we will remove | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-30 12:08 | 2015-02-20 12:10 | 2015-01-30 12:08 | 2015-07-14 13:57 | -21 | In target | 2015-01-30 12:08 | 2015-03-18 15:46 | Siobhan Rumble
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:39 | S217008270002 | CAMBORNE MEWS (13-36) | 181047 | Completed | 8b | High | Communal Area Storage | Outside flat 30 on the staircase landing there is a tumble dryer, it is not known if this tumble dryer is being used in this area. | This tumble dryer should be removed from this staircase landing immediately, I would recommend that the occupant of the flat is asked if this is being used on the landing and if it is the consequences of using a tumble dryer in a means of escape route should be explained to the occupant. | Neighbourhood Management | Siobhan Rumble |  | Housing Officer to ask resident to remove or we will remove | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-30 12:39 | 2015-02-20 12:40 | 2015-01-30 12:39 | 2015-07-14 15:19 | -21 | In target | 2015-01-30 12:39 | 2015-03-18 15:42 | Siobhan Rumble
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:48 | S217008270002 | CAMBORNE MEWS (13-36) | 181049 | Completed | 8c | High | Communal Area Storage | There is a shelving system/rack piled up with combustible items outside flat 15 in the lobby area. | This shelving system/rack should be removed from this lobby area, and the resident reminded that items should not be stored in this lobby area/staircase enclosure. | Neighbourhood Management | Siobhan Rumble |  | Housing Officer to speak to tenant to remove or we will remove | 2015-07-31 | Fully Completed | Siobhan Rumble | 2015-01-30 12:48 | 2015-02-20 12:51 | 2015-01-30 12:48 | 2015-08-03 12:21 | -21 | In target | 2015-01-30 12:48 | 2015-03-18 15:47 | Siobhan Rumble
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:51 | S217008270002 | CAMBORNE MEWS (13-36) | 181051 | Completed | 8d | High | Communal Area Storage | On the staircase landing area outside flats 17 and 18 there is an old television and some cardboard boxes. | I would recommend that the owner of this old television and the boxes is reminded that combustible items should not be stored on the staircase landings. These items should be removed. | Neighbourhood Management | Siobhan Rumble |  | Done | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-01-30 12:51 | 2015-02-20 12:52 | 2015-01-30 12:51 | 2015-10-15 10:37 | -21 | In target | 2015-01-30 12:51 | 2015-03-18 15:41 | Siobhan Rumble
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 12:53 | S217008270002 | CAMBORNE MEWS (13-36) | 181053 | Completed | 8d | Medium | Communal Area Storage | Outside flat 27 in the lobby area., there is a large box of bottles of water, bags and a few other items. | I would recommend that the owner of these items is reminded that things should not be stored here or on the staircase landings. | Neighbourhood Management | Siobhan Rumble |  | Housing Officer to speak to tenant to remove or arrange removal | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-30 12:53 | 2015-03-31 12:53 | 2015-01-30 12:53 | 2015-07-14 13:56 | -60 | In target | 2015-01-30 12:53 | 2015-03-18 15:39 | Siobhan Rumble
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 13:03 | S217008270001 | CAMBORNE MEWS (1-12) | 181060 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in these two buildings being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in these two buildings should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | yes and paperwork available for inspection | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-30 13:03 | 2015-02-20 13:04 | 2015-01-30 13:03 | 2015-03-12 16:04 | -21 | In target | 2015-01-30 13:03 | 2015-03-18 16:03 | Janice Wray
FLATS 1 TO 36, CAMBORNE MEWS - 2015.1.23 | 2015-01-30 13:04 | S217008270001 | CAMBORNE MEWS (1-12) | 181062 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests as per the caretakers check list ,in these two buildings, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes and paperwork available on request | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-30 13:04 | 2015-02-20 13:05 | 2015-01-30 13:04 | 2015-03-10 15:42 | -21 | In target
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 14:28 | S217010550001 | WEST ROW 15-49 ODD | 243809 | Completed | 1 | High | Miscellaneous | During this assessment access could not be gained to the office off the 1st floor landing of the left hand staircase of this building by flat 77. It is not known if there are any portable electrical appliances in this office. | I would recommend that this office is checked to see if there are any portable electrical appliances. If there are, can it please be confirmed that these portable electrical appliances have in date Portable Appliance Testing (PAT) labels on them? If any electrical appliances do not have in date PAT labels on them, then these items should be PAT and any defects found rectified or new appliances purchased. | Neighbourhood Management | Louise Nezandonyi | 2016-03-15 | Last PAT was done last October and is due to be done again this October. If you need access to this room ikn future Sharon Baah has the key | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-02-16 14:28 | 2016-03-08 15:26 | 2016-02-16 14:28 | 2016-04-06 16:04 | -21 | In target
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 15:26 | S217010550001 | WEST ROW 15-49 ODD | 243852 | Active | 8 | Medium | Miscellaneous | During this assessment access could not be gained to the office off the 1st floor landing of the left hand staircase of this building by flat 77. | I would recommend that this office is checked to see that it does not contain quantities of combustible storage or old disused items. If any old items etc are found these should be removed. | Neighbourhood Management | Louise Nezandonyi | 2016-05-10 |  |  |  | Cyril Morris | 2016-02-16 15:26 | 2016-04-16 16:08 |  |  | 327 | 327 days overdue
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 16:16 | S217010550001 | WEST ROW 15-49 ODD | 243889 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-03-15 | Yes monthyly occupier tests and inspections of the installed emergency lighting untis in the building are being undertaken and receord are being kept. All records are kept on Insight. | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-02-16 16:16 | 2016-03-08 16:19 | 2016-02-16 16:16 | 2016-04-06 16:25 | -21 | In target
FLATS 15 TO 95, (ODD NUMBERS ONLY), WEST ROW, LONDON W10 5AX - 2016.01.07 | 2016-02-16 16:19 | S217010550001 | WEST ROW 15-49 ODD | 243891 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-03-15 | Yes the caretaker is undertaking monthly occupier checks of the building structure and records are kept on Insight. | 2016-04-05 | Fully Completed | Louise Nezandonyi | 2016-02-16 16:19 | 2016-03-08 16:21 | 2016-02-16 16:19 | 2016-04-06 16:29 | -21 | In target
FLATS 31 - 53 ADAIR ROAD - 2015.06.16 | 2015-06-26 14:42 | S217007860005 | ADAIR ROAD (31-53) | 203629 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-26 14:42 | 2015-07-17 14:43 | 2015-06-26 14:42 | 2015-09-21 08:49 | -21 | In target
FLATS 31 - 53 ADAIR ROAD - 2015.06.16 | 2015-06-26 14:44 | S217007860005 | ADAIR ROAD (31-53) | 203630 | Completed | 23c | High | Inspection Regime | Is the caretaker undertaking the occupiers tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-26 14:44 | 2015-07-17 14:45 | 2015-06-26 14:44 | 2015-09-21 08:48 | -21 | In target
FLORENCE HOUSE - 2014.08.14 | 2014-08-20 10:35 | S217010050012 | FLORENCE HOUSE | 158161 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-20 10:35 | 2014-10-19 10:36 | 2014-08-20 10:35 | 2014-09-01 16:45 | -60 | In target
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:06 | S217010470002 | FORELAND HOUSE | 196904 | Completed | 8 | Low | Communal Area Storage | During the risk assessment access could not be gained to the store room/area located off the staircase on the 2nd floor level. It is not known what is in this storage area, but it is suitably fire separated from the staircase. | I would recommend that key is obtained to this store room and its contents are checked. A regular check on the contents of this room should be undertaken to see that the storage or use is in accordance with any tenancy agreement if this is a private storage space. | Neighbourhood Management | Martin Barr |  | Clearance was arranged with OCS removing items. Cupboard is on H5 Gerda key | 2015-06-03 | Fully Completed | Martin Barr | 2015-05-13 16:06 | 2015-11-09 16:10 | 2015-05-13 16:06 | 2015-06-04 12:50 | -180 | In target
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:20 | S217010470002 | FORELAND HOUSE | 196912 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-13 16:20 | 2015-06-03 16:22 | 2015-05-13 16:20 | 2015-05-19 11:56 | -21 | In target
FORELAND HOUSE - 2015.05.06 | 2015-05-13 16:22 | S217010470002 | FORELAND HOUSE | 196915 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-05-13 16:22 | 2015-06-03 16:23 | 2015-05-13 16:22 | 2015-05-19 11:58 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.10.25 | 2016-11-29 11:57 | S217008740001 | FRINSTEAD HOUSE | 273347 | Active | 12d2 | High | Flat Door | Whilst undertaking the fire risk assessment it was noted that 2 of the 3 original apartment entrance doors are not fitted with self closing devices. This flat is number 64 64 - leasehold | Flat entrance doors off internal protected areas should be fitted with self closing devices, I would recommend that self closing devices are fitted to these flat entrance doors. | Neighbourhood Management | Samuel Anyanwu | 2016-12-29
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-23 16:40 | S217008740001 | FRINSTEAD HOUSE | 245325 | Completed | 3 | High | Inspection Regime | The fire fighter entry over ride device fitted to the entrance door of the temporary tunnel which gives access to this building did not function and release the locking device on the door and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | This fire fighter entry over ride device fitted to this entrance door should be repaired or replaced so that it releases the locking device fitted to the entrance door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. ESA to check & raise a repair if necessary | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | Os has confirmed that this was fixed on 15/03/2016 | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-23 16:40 | 2016-03-15 16:41 | 2016-02-23 16:40 | 2016-03-17 14:20 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 09:52 | S217008740001 | FRINSTEAD HOUSE | 245390 | Completed | 12e | High | Miscellaneous | There are cables hanging down from the pipes of the ceiling on some of the flat/lift lobby areas, these appear to be cables to satellite dishes fixed to the external walls of the building. Some of this cabling is held up with black tape. 16th floor level or tied up with string. | Does the TMO know about all these cables in these flat/lift lobby area? These flat/lift lobby areas are landlord areas and therefore under the control of the TMO. I would recommend that the cables on the flat/lift lobby areas are securely fixed to the walls or ceiling linings with the correct fastenings, metal ones not tape or plastic cable ties. The hanging cables could potentially obstruct the means of escape route in a fire situation. Could Os inspect please and request the relevant orders | Neighbourhood Management | Louise Nezandonyi | 2016-03-23 | Os has reported this to our repairs team on 15/03/2016 and the target date for this job to be completed by is 24/03/2016 | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-24 09:52 | 2016-03-16 09:53 | 2016-02-24 09:52 | 2016-03-17 14:22 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 09:54 | S217008740001 | FRINSTEAD HOUSE | 245391 | Completed | 12f | High | Inspection Regime | There are cold smoke seals fitted to the self closing fire doors off the flat/lift lobby areas to the refuse chute balcony and on to the lobby area before the staircase and on to the staircase. Some of these cold smoke seals are damaged or there are pieces missing. | As the TMO have fitted fire doors with cold smoke seals to these areas they must be maintained to the standard as when the doors were installed. All missing and damaged cold smoke seals should be replaced. Os has agreed to include these in his routine inspections and raise repairs as necessary with specific location details. | Neighbourhood Management | Louise Nezandonyi | 2016-03-23 | Janice Wray to get further clarity on this from Carl and get back to me. Suggest photos to clarify the standard the ESAs shouls assess against | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-24 09:54 | 2016-03-16 09:55 | 2016-02-24 09:54 | 2017-03-13 12:48 | -21 | In target | 2016-02-24 09:54 | 2017-03-17 12:47 | Janice Wray
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 10:02 | S217008740001 | FRINSTEAD HOUSE | 245403 | Completed | 14a | High | Inspection Regime | The metal cover plate fixed over a cable duct on the 2nd floor level flat/lift lobby area is not fixed to the wall correctly. This is a heavy metal plate. | This metal cover plate should be re-fixed securely back to the wall so providing suitable fire stopping for the cable duct and also stopping this heavy metal plate from falling on somebody. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all the structural elements of the buildings remain fire rated. Os to check & raise as repair if necessary | Neighbourhood Management | Louise Nezandonyi | 2016-03-23 | Os has raised this on 15/03/2016 and the target date for the job is 22/03/2016. | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-24 10:02 | 2016-03-16 10:04 | 2016-02-24 10:02 | 2016-03-17 14:53 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:49 | S217008740001 | FRINSTEAD HOUSE | 245451 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units and fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting and sprinkler systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-03-23 | Monthly checks are carried out at theis block and recorded on insight. The ESA Os Was unable to do the laste emergency lighting check due to the building works this has been recored oin insight as well. | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-24 11:49 | 2016-03-16 11:50 | 2016-02-24 11:49 | 2016-03-10 12:58 | -21 | In target
FRINSTEAD HOUSE, FRESTON ROAD, LONDON W10 6TZ - 2016.01.21 | 2016-02-24 11:57 | S217008740001 | FRINSTEAD HOUSE | 245464 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-03-23 | I can confirm that montly chefcks are being carried ot and recorded on insigfht with the completed sheets bieng storedasnd kept as proof | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-24 11:57 | 2016-03-16 11:59 | 2016-02-24 11:57 | 2016-03-10 13:00 | -21 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:44 | S217008850003 | GADSDEN HOUSE | 185097 | Completed | 8a | High | Inspection Regime | At the basement level there is a lot of rubbish on the floor both inside and outside of the storage cupboards, one side is worse than the other one. These storage cupboards are not being used at present. | I would recommend that all of the rubbish and waste is cleared up from both of these basement areas so that these areas are totally free of any waste or rubbish. | Neighbourhood Management | Martin Barr |  | Items outside sheds have been removed, this area is clear. | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:44 | 2015-03-17 11:46 | 2015-02-24 11:44 | 2015-06-04 10:51 | -21 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:46 | S217008850003 | GADSDEN HOUSE | 185099 | Completed | 8b | Medium | Communal Area Storage | On the open external balcony outside flat 9 there is a lot of decorating items, old tins of paint, dust sheets, paint brushes and rollers etc, plus some bags. | I would recommend that all of these items are removed from the balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | Resident has agreed to move. Most items already gone and remaining few will be moved shortly. | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:46 | 2015-04-25 11:47 | 2015-02-24 11:46 | 2015-06-04 10:51 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:48 | S217008850003 | GADSDEN HOUSE | 185102 | Completed | 8c | Medium | Communal Area Storage | On the open external balcony outside flat 12 there an old internal door and 2 black bags. | I would recommend that these items are removed from the balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | Items have been removed | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:48 | 2015-04-25 11:49 | 2015-02-24 11:48 | 2015-06-04 10:52 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:49 | S217008850003 | GADSDEN HOUSE | 185103 | Completed | 8d | Medium | Communal Area Storage | On the open external balcony outside of flat 15 there is a bedroom unit with items piled up on it. . | I would recommend that this bedroom unit is removed from this balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | Items have been removed | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:49 | 2015-04-25 11:50 | 2015-02-24 11:49 | 2015-06-04 10:53 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:51 | S217008850003 | GADSDEN HOUSE | 185105 | Completed | 8e | Medium | Communal Area Storage | On the open external balcony outside of flat 22 there is a dismantled bedroom unit and other items stored next to it. | I would recommend that these items are removed from this balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | These items have been removed from the balcony | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:51 | 2015-04-25 11:51 | 2015-02-24 11:51 | 2015-06-04 10:54 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 11:52 | S217008850003 | GADSDEN HOUSE | 185106 | Completed | 8f | Medium |  | On the open external balcony outside of flat 24 there are bags of clothes and cardboard boxes stacked up on top of each other. | I would recommend that all of these items are removed from this balcony area outside of this flat. | Neighbourhood Management | Martin Barr |  | Clothes and boxes have been removed from balcony | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-24 11:52 | 2015-04-25 11:53 | 2015-02-24 11:52 | 2015-06-04 10:54 | -60 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:11 | S217008850003 | GADSDEN HOUSE | 185130 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-24 12:11 | 2015-03-17 12:12 | 2015-02-24 12:11 | 2015-05-19 12:04 | -21 | In target
GADSDEN HOUSE - 2015.02.12 | 2015-02-24 12:13 | S217008850003 | GADSDEN HOUSE | 185134 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-24 12:13 | 2015-03-17 12:14 | 2015-02-24 12:13 | 2015-05-19 12:05 | -21 | In target
GALSWORTHY HOUSE - 2015.06.03 | 2015-06-11 14:35 | S217008660003 | GALSWORTHY HOUSE | 201127 | Completed | 8 | Medium | Miscellaneous | At the rear of the row of external storage shed there are old motor bike parts. | I would recommend that all these old motor bike parts are removed from this area. | Neighbourhood Management | Martin Barr |  | These items were removed some time ago | 2015-09-24 | Fully Completed | Martin Barr | 2015-06-11 14:35 | 2015-08-10 14:36 | 2015-06-11 14:35 | 2015-09-25 11:33 | -60 | In target
GALSWORTHY HOUSE - 2015.06.03 | 2015-06-11 14:37 | S217008660003 | GALSWORTHY HOUSE | 201128 | Completed | 12 | Medium | Flat Door | It was highlighted in a letter sent to the TMO on the 23rd July 2014 that the internal door frame and the lock area of flat 4's entrance doors was damaged. This flat entrance door is the same doors as was installed in July last year. | Can it please be confirmed if this flat entrance door was repaired? Martin could your chaps check out whether this work has been completed ? | Neighbourhood Management | Martin Barr | 2017-03-10 | ESA checked door frame & lock -- all secure & in good condiotn | 2017-03-10 | Fully Completed | Janice Wray | 2015-06-11 14:37 | 2015-08-10 14:38 | 2015-06-11 14:37 | 2017-03-13 12:33 | -60 | In target | 2015-06-11 14:37 | 2017-03-17 12:32 | Janice Wray
GALSWORTHY HOUSE - 2015.06.03 | 2015-06-11 14:39 | S217008660003 | GALSWORTHY HOUSE | 201129 | Completed | 23a | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 14:39 | 2015-07-02 14:40 | 2015-06-11 14:39 | 2015-09-21 09:38 | -21 | In target
GALSWORTHY HOUSE - 2015.06.03 | 2015-06-11 14:42 | S217008660003 | GALSWORTHY HOUSE | 201131 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 14:42 | 2015-07-02 14:44 | 2015-06-11 14:42 | 2015-09-21 08:58 | -21 | In target
GREAVES TOWER, BLANTYRE STREET, LONDON SW10 0EA - 2016.08..05 | 2016-09-20 17:00 | S217012740008 | GREAVES TOWER 4-62 | 271027 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and checks on the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-10-18 | There are some performance issues with this ESA around consistency in completing their checks. There is an action plan in place and regular meetings. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-09-20 17:00 | 2016-10-11 17:01 | 2016-09-20 17:00 | 2017-01-16 10:52 | -21 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:23 | S217012740008 | GREAVES TOWER 4-62 | 102332 | Completed | 8d | Medium | Communal Area Storage | On the 9th floor level flat/lift lobby area there is chair and table. | These items of furniture should be removed from the flat/lift lobby area and the owner of them reminded that items should not be stored on the flat/lift lobby areas. | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | Already removed. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:23 | 2013-10-15 16:24 | 2013-08-16 16:23 | 2013-10-17 14:03 | -60 | In target
GREAVES TOWER-2013.04.01 | 2013-08-16 16:25 | S217012740008 | GREAVES TOWER 4-62 | 102333 | Completed | 8e | Medium | Communal Area Storage | In the double cupboard on the 12th floor level flat/lift lobby area there are parts of a motor bike and other household items being stored. | These items should be removed from this cupboard and the cupboard secured locked shut. | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | Clearance ordered 16th Oct 2013. Update 23rd Oct 2013 - cupboard can't be accessed, needs lock change and then clearance to be ordered again. ESA to raise lock change 24th Oct 2013. Update 01.11.13 - still awaiting lock change to access bike parts. ESA to chase. Update 17.01.14 - repair order to change lock (201330451) was not acted upon, target date 4th Nov 2013. New order raised 17.01.14 but has been given a 20-day target date. | 2014-01-17 | Fully Completed | Wendy Stevenson | 2013-08-16 16:25 | 2013-10-15 16:26 | 2013-08-16 16:25 | 2014-03-18 17:05 | -60 | In target | 2013-08-16 16:25 | 2014-03-24 17:04 | Janice Wray
GREAVES TOWER-2013.04.01 | 2013-08-16 16:26 | S217012740008 | GREAVES TOWER 4-62 | 102334 | Completed | 8f | Medium | Communal Area Storage | In the right hand side riser cupboard on the ground floor level there are two sets of skis being stored. | I would recommend that these private items are removed from this riser cupboard. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | Bulk clearance arranged via cleaners today, awaiting order to be raised - COMPLETED. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:26 | 2013-10-15 16:27 | 2013-08-16 16:26 | 2014-01-10 10:01 | -60 | In target | 2013-08-16 16:26 | 2014-01-16 10:00 | Janice Wray
GREAVES TOWER-2013.04.01 | 2013-08-16 16:17 | S217012740008 | GREAVES TOWER 4-62 | 102326 | Completed | 8b | Medium | Communal Area Storage | There is contractors waste and combustible material stored in the roof level area where the dry rising main outlet is located. | would recommend that all the contractors waste and other material is removed from this roof level area. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc has been removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-10-23 | Order raised 16th Oct 2013 for removal. Update 23rd Oct 2013 - specialist clean required as area is inaccessible - roof. ESA to order 24th Oct 2013. Update01.11.13 - still awaiting clearance. ESA instructed to arrange this. Update 14.01.14 - photos seen, now cleared. | 2013-11-01 | Fully Completed | Wendy Stevenson | 2013-08-16 16:17 | 2013-10-15 16:20 | 2013-08-16 16:17 | 2014-01-15 11:59 | -60 | In target | 2013-08-16 16:17 | 2014-01-13 16:37 | Wendy Stevenson
GREAVES TOWER-2013.04.01 | 2013-08-16 16:21 | S217012740008 | GREAVES TOWER 4-62 | 102329 | Completed | 8c | Medium | Communal Area Storage | On the 5th floor level flat/lift lobby area there are 2 wardrobes and some other bedroom furniture. | These items of furniture should be removed from the flat/lift lobby area and the owner of them reminded that items should not be stored on the flat/lift lobby areas. | Neighbourhood Management | Wendy Stevenson | 2013-10-14 | Items have been removed. | 2013-10-15 | Fully Completed | Wendy Stevenson | 2013-08-16 16:21 | 2013-10-15 16:22 | 2013-08-16 16:21 | 2013-10-16 16:17 | -60 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:16 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172159 | Completed | 8 | High | Communal Area Storage | On the 19th and 20th floor levels push bikes have been chained to the dry rising main outlets. | The dry rising main outlets must not be obstructed at anytime, these push bikes should not be chained to these outlets and the owners of the push bikes must be told not to do this. | Neighbourhood Management | Siobhan Rumble |  | these have been removed | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 10:16 | 2014-12-22 10:18 | 2014-12-01 10:16 | 2015-03-10 14:54 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:51 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172187 | Completed | 16b | Medium | Signage | The floor number on staircase landing on the 16th floor level has been altered to look like an 18. Floor numbers aid the fire service if there is an incident in this building. | I would recommend that the 16th floor number is altered back to 16 from 18. Opposite the lifts and on each staircase landings of this building where there is a balcony. Seamus or OCS to sort | Neighbourhood Management | Siobhan Rumble |  | all done | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 10:51 | 2015-01-30 10:53 | 2014-12-01 10:51 | 2015-03-10 14:54 | -60 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:19 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172240 | Completed | 23b | High | Miscellaneous | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | these were done by RGE 6 monthly under contract. inspectors check the block lighting to check if all bulbs and emergency lighting are working and records are kept | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:19 | 2014-12-22 12:22 | 2014-12-01 12:19 | 2015-03-10 14:56 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:23 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172242 | Completed | 23c | High | Fire Alarm | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? Including testing the automatic smoke vents | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, including testing the smoke vents with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | being done by rydons | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:23 | 2014-12-22 12:24 | 2014-12-01 12:23 | 2015-03-10 14:57 | -21 | In target
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:25 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 172245 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes and these are available for inspection at any time | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-01 12:25 | 2014-12-22 12:27 | 2014-12-01 12:25 | 2015-03-10 14:59 | -21 | In target
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:09 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269278 | Completed | 1b | High | Inspection Regime | At the time of this assessment the lighting was not working in some roof level areas of this building. A check should be undertaken on all of the lighting circuits and light units at the roof level and any defect wiring or bulbs etc repaired or replaced so that the lighting is in full working order. | Nicky Could Paul Steadman check if the lighting in this area is now all operational and if not put it thro to repairs (as I'm not clear of the detail of what works or if it has now been repairs) Janice | Neighbourhood Management | Nicola Bartholomew | 2016-09-05 | Alex Bosman confirms that RMA have completed works on site - Certificate awaited | 2016-11-07 | Fully Completed | Janice Wray | 2016-08-08 16:09 | 2016-08-29 16:11 | 2016-08-08 16:09 | 2016-11-08 16:31 | -21 | In target
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:12 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269280 | Active | 2 | High | Inspection Regime | Behind the wire mesh gate off the staircase on the upper floor level to the roof there are used cigarette ends on the floor. | These used cigarette ends should be cleared up and persons remaindered that smoking is not allowed within this building. Nicky Could Paul please increase his inspections in this area and instigate whatever cleaning is required to ensure that this issue is kept under control Janice | Neighbourhood Management | Nicola Bartholomew | 2016-09-05 |  |  |  | Cyril Morris | 2016-08-08 16:12 | 2016-08-29 16:13 |  |  | 192 | 192 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:40 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269368 | Active | 12i | High | Responsive Item | Some of the staircase doors are not being closed fully by the self closing devices fitted to the doors. These doors should be picked up during the caretakers inspections of the doors. | Any staircase doors which are not being closed fully by the self closing devices should have the self closer adjusted or a new one fitted so that the doors close fully onto their stops. Could Paul Steadman please monitor and raise response repairs as necessary | Neighbourhood Management | Nicola Bartholomew | 2016-09-06 |  |  |  | Cyril Morris | 2016-08-09 12:40 | 2016-08-30 12:53 |  |  | 191 | 191 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 13:50 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269374 | Active | 12j | High | Responsive Item | The staircase door at the 16th floor level is damaged. | This door should be repaired or alternatively a new self closing certified 30 minute fire rated door fitted with intumescent strips and cold smoke seals could be installed. Could Paul please confirm if this has now been repaired & if not could he raise / chase the repair | Neighbourhood Management | Nicola Bartholomew | 2016-09-06 |  |  |  | Cyril Morris | 2016-08-09 13:50 | 2016-08-30 13:51 |  |  | 191 | 191 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:18 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269383 | Active | 16 | High | Signage | There are TMO standard fire action notices are displayed next to each of the fire alarm break glass call points in the basement boiler room and in the roof level areas of this building. | All other fire action notices which give different information should all be removed. Could Paul / Seamus please sort this? | Neighbourhood Management | Nicola Bartholomew | 2016-09-06 |  |  |  | Cyril Morris | 2016-08-09 14:18 | 2016-08-30 14:19 |  |  | 191 | 191 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:47 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269394 | Active | 17f | High | Miscellaneous | At the roof level there is a coil of fire alarm cable not connected at one end to anything. | What is this coil of fire alarm cable for? Could Paul arrange for his to be removed please? | Neighbourhood Management | Nicola Bartholomew | 2016-09-06 |  |  |  | Cyril Morris | 2016-08-09 14:47 | 2016-08-30 15:20 |  |  | 191 | 191 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:37 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269424 | Completed | 17h | High | Smoke Alarms | There are 2 smoke detectors fitted on the 7th floor level ceiling, the 2nd detector is a different style of smoke detector to the newly installed one. This device is on the ceiling near to the flat entrance door of flat 46. The contractor does not know anything about this 2nd device. | What is the reason for the 2nd smoke detector fitted on the 7th floor level ceiling near to flat 46's entrance door? Could Paul investigate this please? | Neighbourhood Management | Nicola Bartholomew | 2016-09-07 | Confirmation that second "detector" is actiually a CCTV camera | 2016-12-09 | Fully Completed | Janice Wray | 2016-08-10 09:37 | 2016-08-31 09:39 | 2016-08-10 09:37 | 2016-12-12 12:28 | -21 | In target
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:17 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269447 | Active | 23b | High | Fire Alarm | There are BS 5839 Part 1 fire detection systems fitted in this building, is weekly occupier testing of these systems being undertaken? | Weekly occupiers testing of the installed fire alarm systems must be undertaken and the results recorded as proof of testing. Weekly testing by Paul - training provided - please confirm | Neighbourhood Management | Nicola Bartholomew | 2016-09-07 |  |  |  | Cyril Morris | 2016-08-10 10:17 | 2016-08-31 10:19 |  |  | 190 | 190 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:48 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269520 | Completed | 23e | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Bartholomew | 2016-09-07 | Confirmed | 2016-12-09 | Fully Completed | Janice Wray | 2016-08-10 16:48 | 2016-08-31 16:49 | 2016-08-10 16:48 | 2016-12-12 12:32 | -21 | In target
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:51 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269522 | Active | 23g | High | Inspection Regime | Are the weekly occupier's tests of the buildings automatic smoke ventilation system being undertaken? | Weekly occupier inspections of the buildings smoke ventilation system should be undertaken, with the results recorded as proof of the inspections having been undertaken. Can you confirm that Paul is undertaking these please? | Neighbourhood Management | Nicola Bartholomew | 2016-09-07 |  |  |  | Cyril Morris | 2016-08-10 16:51 | 2016-08-31 16:52 |  |  | 190 | 190 days overdue
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:52 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | 269524 | Completed | 23h | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. Can you confirm that Paul is undertaking these please? | Neighbourhood Management | Nicola Bartholomew | 2016-09-07 | Confirmed | 2016-12-09 | Fully Completed | Janice Wray | 2016-08-10 16:52 | 2016-08-31 16:53 | 2016-08-10 16:52 | 2016-12-12 12:30 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:39 | S217012770015 | GRENFELL WALK 101-111 | 146393 | Completed | 8a | High | Communal Area Storage | There are numerous tubs and pots of shrubs and plants on the 1st floor level balcony of Grenfell Walk, this includes the staircase landing areas at each end of the building. Some of these tubs have small conifer trees in them. | I would recommend some of the tubs and pots of shrubs and plants on the 1st floor level of Grenfell Walk, this includes the staircase landing areas and the balcony outside the flat entrance doors are removed. Some of these tubs and pots can remain but they must not obstruct the dry rising water main outlet or the balcony. Please see item 19 below because the fire service must have a working area around the dry riser outlet valve. If the person responsible for placing the plants etc here on the 1st floor level balconies and staircases landings of Grenfell Walk does not agree with the removal of some of the shrubs and plants etc then I would recommend that all of the plants should be removed and the areas maintained completely clear at all items. | Neighbourhood Management | Janice Jones |  | Letter has been written to tenant stating he needs to remove the plants otherwise he will be re charged for all their removal. Home visit being undertaken by Siobhan Rumble on 04/09. Confrmation plants removed in Nov 2014 | 2013-11-29 | Fully Completed | Janice Jones | 2014-06-02 12:39 | 2014-06-23 12:41 | 2014-06-02 12:39 | 2015-03-12 16:15 | -21 | In target | 2014-06-02 12:39 | 2015-03-18 16:14 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:41 | S217012770015 | GRENFELL WALK 101-111 | 146394 | Completed | 8b | High | Communal Area Storage | There are some pots of plants on the 1st to 2nd floor level staircase of Grenfell Walk by flat 106. | All pots of plants should be removed from this staircase immediately, the staircase should be maintain free of all obstructions so that they can be used without the risk of tripping over pots of plants. | Neighbourhood Management | Janice Jones |  | This work has been completed - plants cleared | 2015-07-03 | Fully Completed | Janice Wray | 2014-06-02 12:41 | 2014-06-23 12:43 | 2014-06-02 12:41 | 2015-07-06 14:28 | -21 | In target
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:43 | S217012770010 | GRENFELL WALK | 146395 | Completed | 8c | High | Communal Area Storage | There are numerous tubs, pots and other gardening items stored under Grenfell Walk at the garden level. There is also some furniture. Some of these items are placed up against the vents of the underground garages. | I would recommend that this area at the garden level is tidied up and some of the tubs, pots and furniture etc is removed. This will reduce the fire loading of this area. | Neighbourhood Management | Janice Jones |  |  | 2014-10-27 | Fully Completed | Janice Wray | 2014-06-02 12:43 | 2014-06-23 12:44 | 2014-06-02 12:43 | 2015-05-11 09:51 | -21 | In target | 2014-06-02 12:43 | 2014-11-03 14:11 | Janice Jones
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:45 | S217012770010 | GRENFELL WALK | 146396 | Completed | 8d | Information Only | Communal Area Storage | For your infor-mation In contrast to the number of tubs and pots of shrubs and plants on the 1st floor level of Grenfell Walk the 2nd floor is not obstructed and the pots of plants located here do not need to be removed. | No action required | Neighbourhood Management | Janice Jones |  |  | 2014-10-27 | Fully Completed |  |  |  | 2014-06-02 12:45 | 2014-10-28 14:09 |  |  | 2014-06-02 12:45 | 2014-11-03 14:09 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 12:56 | S217012770015 | GRENFELL WALK 101-111 | 146399 | Completed | 19 | High | Hose Reels | The dry rising main outlet valve located on the 1st floor level of Grenfell Walk is partly obstructed by tubs of plants and shrubs. I believe that the fire service would find it hard the access this dry riser outlet. | Please also see item 8a as the balcony of this building at this floor level is also obstructed by plants and the fire service would find it hard to manoeuvre along this balcony with hose charged from the dry riser outlet. The shrubs and plants obscuring the dry rising main outlet should be removed so that the fire service have a clear working area around this dry riser outlet. Regular checks should be made so that this outlet remains usable at all times and that there is a clear area around the outlet. | Neighbourhood Management | Janice Jones |  |  | 2015-05-08 | Fully Completed | Janice Jones | 2014-06-02 12:56 | 2014-06-23 13:05 | 2014-06-02 12:56 | 2015-05-11 13:38 | -21 | In target | 2014-06-02 12:56 | 2015-05-15 13:37 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:06 | S217012770010 | GRENFELL WALK | 146403 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system of Upper Grenfell Walk and possibly Grenfell Walk being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in these buildings should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | Confirmation from Robert Regan that he is undertaking monthly testing of emergency lighting on Stage 3 at Lanc West. EL on this block not standard so Inspectors to be invited to follow-up training to ensure that they are clear about how to test at this block. | 2014-06-20 | Fully Completed | Siobhan Rumble | 2014-06-02 13:06 | 2014-06-23 13:08 | 2014-06-02 13:06 | 2014-06-23 12:01 | -21 | In target | 2014-06-02 13:06 | 2014-06-27 11:50 | Janice Wray
GRENFELL WALK AND UPPER GRENFELL WALK - 2014.5.20 | 2014-06-02 13:08 | S217012770010 | GRENFELL WALK | 146406 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing. | Neighbourhood Management | Siobhan Rumble |  | weekly inspections are carried out and all sheest completed. | 2014-06-20 | Fully Completed | Siobhan Rumble | 2014-06-02 13:08 | 2014-06-23 13:10 | 2014-06-02 13:08 | 2014-06-23 11:42 | -21 | In target | 2014-06-02 13:08 | 2014-06-27 11:41 | Janice Wray
GROVE HOUSE, CHELSEA MANOR STREET, LONDON SW3 5QB - 2106.04.04 | 2016-05-23 15:34 | S217000830002 | GROVE HOUSE | 261986 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency escape lighting units in this building should be undertaken, with the results recorded as proof of testing. | Neighbourhood Management | Nicola Rees | 2016-06-13 | This is being completed. | 2016-12-01 | Fully Completed | Nicola Rees | 2016-05-23 15:34 | 2016-06-13 15:35 | 2016-05-23 15:34 | 2016-12-02 16:15 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:09 | S217002400002 | GUNTER GROVE (36) | 197869 | Completed | 23b | High | Inspection Regime | 2Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Jimmy Lemos |  | has been check by ESA | 2015-05-22 | Fully Completed | Jimmy Lemos | 2015-05-19 16:09 | 2015-06-09 16:10 | 2015-05-19 16:09 | 2015-05-29 12:43 | -21 | In target
HARRIET HOUSE - 2015.05.11 | 2015-05-19 16:10 | S210008550002 | HARRIET HOUSE (1-20) | 197870 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Jimmy Lemos |  | completed by Kamran | 2015-05-28 | Fully Completed | Jimmy Lemos | 2015-05-19 16:10 | 2015-06-09 16:12 | 2015-05-19 16:10 | 2015-05-29 13:05 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 12:52 | S217008750001 | HAZLEWOOD TOWER | 133617 | Completed | 1a | High | Electrical Wire Check | There are no electrical portable appliance test labels on any of the portable electrical appliances in the rest area set up in the bulk storage room. These portable electrical items include a television, a deep fat fryer, a kettle and a portable electric heater amongst other things. | These portable electrical appliances should be tested by a suitably qualified person and portable appliance test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. Chris - Could you please investigate. Should they be using this area? Don't think it is on our Asset Register for PAT | Neighbourhood Management | Chris Baker |  | All electrical items have been removed. Cleaners have been instructed that they should not be using any eletrical items in this area, as it is not a designated rest area. | 2014-03-21 | Fully Completed | Chris Baker | 2014-03-07 12:52 | 2014-03-28 12:55 | 2014-03-07 12:52 | 2014-03-25 10:35 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 12:56 | S217008750001 | HAZLEWOOD TOWER | 133620 | Completed | 1b | High | Miscellaneous | There is an extension lead from an electrical socket in the electrical intake room into the bulk storage area, this extension lead is hung over doors stopping them closing and badly taped to the floor. | I would recommend that if an electrical supply is needed in the bulk storage area that purpose fitted electrical sockets are wall fitted in this area. The extension lead should be removed so that the doors can be closed fully. | Neighbourhood Management | Chris Baker |  | All extention leads have been removed, and cleaners advised that they should not be using eletrical appliances in this area. | 2014-03-20 | Fully Completed | Chris Baker | 2014-03-07 12:56 | 2014-03-28 12:57 | 2014-03-07 12:56 | 2014-03-25 10:37 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 12:58 | S217008750001 | HAZLEWOOD TOWER | 133621 | Completed | 1c | High | Miscellaneous | There are two multi plugs located at the end of the extension lead which runs from the electrical socket in the electrical intake room into the bulk storage area. | I would recommend that if an electrical supply is needed in the bulk storage area that purpose fitted electrical sockets are wall fitted in the area where they are required. The multi plugs can then be removed. | Neighbourhood Management | Chris Baker |  | All multi-plugs removed along with extention leads. Cleaners have no need for electrical items in this area. | 2014-03-20 | Fully Completed | Chris Baker | 2014-03-07 12:58 | 2014-03-28 13:00 | 2014-03-07 12:58 | 2014-03-25 10:39 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 13:01 | S217008750001 | HAZLEWOOD TOWER | 133622 | Completed | 6 | High | Miscellaneous | There is a cooking area set up in the ground floor level bulk storage area of this building. I do not believe that a bulk storage area is a suitable place to undertake cooking. | I would recommend that an inspection is undertaken of the cooking area in the bulk storage area of this building by an Environmental Health Officer. A report on the suitability of this area for cooking and as a rest area should be produced and any recommendations in the report acted upon. | Neighbourhood Management | Chris Baker |  | Cleaners have been advised that this area is not to be used for cooking. All cooking items have been removed and disposed of. | 2014-03-21 | Fully Completed | Chris Baker | 2014-03-07 13:01 | 2014-03-28 13:02 | 2014-03-07 13:01 | 2014-03-25 10:42 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 13:02 | S217008750001 | HAZLEWOOD TOWER | 133623 | Completed | 8a | High | Communal Area Storage | In nearly every cupboard on each flat /lift lobby area there is a cardboard box containing old/disused electrical meters. It appears that new electrical meters for the individual flats have been fitted and the old meters just dumped in the cupboards. | I would recommend that the cardboard boxes containing the old electrical meters are removed from the flat/lift lobby area cupboards. Martin - Could this be done as bulk clearance? | Neighbourhood Management | Martin Barr |  | Order no 201402864 raised to clear items. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 13:02 | 2014-03-28 13:03 | 2014-03-07 13:02 | 2014-04-22 11:06 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 13:04 | S217008750001 | HAZLEWOOD TOWER | 133624 | Completed | 8b | High | Communal Area Storage | In the internal central open area at the roof level there are empty cardboard boxes and piles of contractors waste. | I would recommend that the empty cardboard boxes and the waste are removed from the roof level area. | Neighbourhood Management | Martin Barr |  | Order no 201402864 raised to clear items. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 13:04 | 2014-03-28 13:15 | 2014-03-07 13:04 | 2014-04-22 11:06 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 13:15 | S217008750001 | HAZLEWOOD TOWER | 133627 | Completed | 11a | High | Miscellaneous | Whilst I was in this building I saw mice in the ground floor entrance lobby area and in the storage areas located off this ground floor lobby area. | I would recommend that a pest control company is tasked with eliminating all the mice and any other rodents from this building. | Neighbourhood Management | Chris Baker |  | The building has been referred to the pest control team at the council's Environmental Health department, and a treatment programme has been put in place to eliminate the mice from the ground floor areas. | 2014-03-17 | Fully Completed | Chris Baker | 2014-03-07 13:15 | 2014-03-28 14:05 | 2014-03-07 13:15 | 2014-03-25 10:44 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:05 | S217008750001 | HAZLEWOOD TOWER | 133643 | Active | 11b | High | Miscellaneous | At the roof level some of the plastic covering is missing from over the openings of one of the cold water tank rooms, the gaps that are now in this opening are allowing pigeons to enter the cold water tank room. | I would recommend that a pest control company is tasked with eliminating all the pigeons in the room and that the external openings are recovered over to stop pigeons entering the cold water tank room. | Neighbourhood Management | Chris Baker |  | Pigeon control specialists contracted to remove pigeons and cover openings, and monitor as necessary to ensure pigeons are unable to return. | 2014-03-26 | Fully Completed | Chris Baker | 2014-03-07 14:05 | 2014-03-28 14:08 | 2014-03-07 14:05 | 2014-03-31 17:00 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:09 | S217008750001 | HAZLEWOOD TOWER | 133645 | Completed | 12a | High | Responsive Item | Some of the doors of the cupboard located off each of the flat/lift lobby areas can not be locked shut. Items have been inserted in the locks or the locks damaged. | I would recommend that the doors where locks are damaged etc are repaired so that the cupboards con be secured locked shut. Martin - Could the ESA survey & identify which need attention & then refer to Repairs please | Neighbourhood Management | Martin Barr |  | All cupboards apart from the 3rd floor are closing and locking without problem. An order has been requested to fix the door on the 3rd floor. It is not the lock that is faulty, there is a piece of wood missing from the frame where bolts line up so it doesn't hold. | 2014-04-22 | Fully Completed | Martin Barr | 2014-03-07 14:09 | 2014-03-28 14:11 | 2014-03-07 14:09 | 2014-04-23 14:47 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2014-03-07 14:28 | S217008750001 | HAZLEWOOD TOWER | 133663 | Completed | 23 | High | Fire Extinguisher | Are the monthly occupier tests and inspections of the fire extinguishers, dry riser, the lifts and emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment, lifts emergency lighting etc and the other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Training on lighting testing due 23rd April. Checks will take place after this and once list of locations provided by A&R team. Block checks are completed and records kept. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 14:28 | 2014-03-28 14:29 | 2014-03-07 14:28 | 2014-04-22 09:01 | -21 | In target
HAZLEWOOD TOWER - 2014.2.20 | 2016-01-27 14:33 | S217008750001 | HAZLEWOOD TOWER | 239828 | Completed | 8 | Medium | Inspection Regime | In the small store room area where the CCTV equipment is located off the ground floor level entrance hall area there is some old electrical equipment and old light fittings in cardboard boxes. | These items should be removed from this area and disposed of. | Neighbourhood Management | Louise Nezandonyi | 2016-04-28 | Ronnie the ESA has checked this area and there are no old electrical equpment and old light fittings in cardboard boxes. | 2016-02-16 | Fully Completed | Louise Nezandonyi | 2016-01-27 14:33 | 2016-03-27 14:36 | 2016-01-27 14:33 | 2016-02-16 10:58 | -60 | In target
HAZLEWOOD TOWER, GOLBORNE GARDENS, LONDON W10 5DT - 2016.10.03 | 2016-11-14 14:16 | S217008750001 | HAZLEWOOD TOWER | 272874 | Active | 23b | High | Inspection Regime | Are the occupier's monthly tests and inspections in this building being undertaken as per the caretakers check list? | Can it please be confirmed that the occupier's monthly tests and inspections in this building being undertaken as per the caretakers check list? | Neighbourhood Management | Louise Nezandonyi | 2016-12-19 |  |  |  | Cyril Morris | 2016-11-14 14:16 | 2016-12-05 14:18 |  |  | 94 | 94 days overdue
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:12 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153375 | Completed | 23b | High | Inspection Regime | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Can it be confirmed that the weekly occupiers testing of the installed fire alarm system is being undertaken? If it is being tested are records of any testing being kept as proof of testing, if testing is not being undertaken then weekly testing should start and records of this testing kept as proof of testing. | Neighbourhood Management | Martin Barr |  | ESAs have been advised not to test fire alarm systems | 2014-08-28 | Fully Completed | Martin Barr | 2014-07-17 16:12 | 2014-08-07 16:13 | 2014-07-17 16:12 | 2014-09-01 16:17 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:15 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153380 | Completed | 23d | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-07-17 16:15 | 2014-08-07 16:16 | 2014-07-17 16:15 | 2014-09-01 16:18 | -21 | In target
HENRY DICKENS COURT COMMUNITY CENTRE - 2014.6.24 | 2014-07-17 16:17 | S217010057702 | HENRY DICKENS COMMUNITY ROOM | 153381 | Completed | 23e | High | Fire Extinguisher | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-07-17 16:17 | 2014-08-07 16:18 | 2014-07-17 16:17 | 2014-09-01 16:18 | -21 | In target
HEREFORD HOUSE, 370-372 FULHAM ROAD, LONDON SW10 9UY - 2016.05.10 | 2016-05-26 12:31 | S217002180006 | HEREFORD HOUSE | 262654 | Completed | 12b | High | Inspection Regime | The self closing device fitted to the landing lobby door outside flats 34A and B did not close this fire door fully. Also a piece of carpet has been laid on the floor in this lobby area and this carpet is obstructing the door from shutting fully. | The piece of carpet in this lobby area should be removed or the door adjusted so that it rides over the top of the carpet. Also I would recommend that the self closing device fitted to this fire door is adjusted, repaired or replaced so that it shuts the fire door fully onto its stops. Nicola Could the ESA please investigate whether carpet can say and door by adjusted to accommodate. Please advise | Neighbourhood Management | Nicola Rees | 2016-06-16 | Email sent to John 02.06.16. Email chasing on the 06.09.16. Email sent to Jimmy 01.12.16. I have had confirmation that the carpet has been removed. | 2017-01-16 | Fully Completed | Nicola Rees | 2016-05-26 12:31 | 2016-06-16 12:38 | 2016-05-26 12:31 | 2017-01-17 16:34 | -21 | In target
HEREFORD HOUSE, 370-372 FULHAM ROAD, LONDON SW10 9UY - 2016.05.10 | 2016-05-26 14:11 | S217002180006 | HEREFORD HOUSE | 262699 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting systems/units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-06-16 | Yes these are being completed. | 2016-06-02 | Fully Completed | Nicola Rees | 2016-05-26 14:11 | 2016-06-16 14:12 | 2016-05-26 14:11 | 2016-06-03 11:20 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:54 | S217008850001 | HOLMEFIELD HOUSE | 130788 | Completed | 1d | Information Only | Miscellaneous | In the room/area called 116A there are old computers etc that have a PAT date of last being tested as 2009 or 2010, this room is now not used. | I would recommend that all of the electrical items in this room are portable appliance tested or if they are not needed them removed from this room and disposed of. Glenn - do you know anything about these? | Neighbourhood Management | Glenn McAllister |  | Storeroom now cleared | 2014-04-22 | Fully Completed |  |  |  | 2014-02-19 16:54 | 2014-04-23 15:41 |  |  | 2014-02-19 16:54 | 2014-04-29 15:38 | Janice Wray
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:56 | S217008850001 | HOLMEFIELD HOUSE | 130791 | Completed | 2 | Medium | Signage | Some of the "No Smoking" signs displayed in this building are defaced or damaged. | I would recommend that new "No Smoking" signs are provided where the old ones are either defaced or damaged. | Neighbourhood Management | Martin Barr |  | Signs are in place. ESA has some spares and will replace these if removed again. | 2014-06-05 | Fully Completed | Martin Barr | 2014-02-19 16:56 | 2014-04-20 16:57 | 2014-02-19 16:56 | 2014-06-06 09:39 | -60 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:57 | S217008850001 | HOLMEFIELD HOUSE | 130794 | Completed | 8a | High | Communal Area Storage | There is storage of combustible materials/waste, old tins of paint, household furniture and household items in the area at the rear of the electrical room near to flat 604, called room K29/G/26. Electrical rooms should be controlled areas. | I would recommend that all the items are removed from this room and that the electrical rooms are kept free of any storage. | Neighbourhood Management | Martin Barr |  | The locations on this issue do not match up. Cupboard labelled K29/G/26 was checked and is clear. | 2014-06-05 | Fully Completed | Martin Barr | 2014-02-19 16:57 | 2014-03-12 16:59 | 2014-02-19 16:57 | 2014-06-06 09:41 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 16:59 | S217008850001 | HOLMEFIELD HOUSE | 130796 | Completed | 8b | High | Miscellaneous | There is an excessive amount of combustible storage and household items on the balcony/walkway area outside flat 518, this is a common part of the building and not an area demised to the occupant of flat 518. | I would recommend that all the items in the walkway area outside flat 518 are removed. Alternatively this walkway area could be demised to the occupant of this flat and a gate erected at the end of this walkway as it joins the landing area. | Neighbourhood Management | Glenn McAllister |  | Visited tenant on the Wednesday 26th February 2014 advised him to clear bulk content from commual area. Will send letter advising him to move all items by 12th February 2014 | 2014-02-26 | Fully Completed | Glenn McAllister | 2014-02-19 16:59 | 2014-03-12 17:01 | 2014-02-19 16:59 | 2014-04-03 15:57 | -21 | In target | 2014-02-19 16:59 | 2014-03-11 12:12 | Glenn McAllister
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 17:01 | S217008850001 | HOLMEFIELD HOUSE | 130799 | Completed | 8c | High | Communal Area Storage | On the walkway/balcony area outside flat 530 there is an old washing machine, flat 216 an old freezer, flat 416 a wardrobe, TV and bedside table flat 325 upper balcony old bedroom units | I would recommend that these items are removed from outside these flats. | Neighbourhood Management | Glenn McAllister |  | Most of the bulk items have now been cleared. apart from items outside flat 530. will send letter to tenant advising him to move items by 12th March 2014 | 2014-02-26 | Fully Completed | Glenn McAllister | 2014-02-19 17:01 | 2014-03-12 17:02 | 2014-02-19 17:01 | 2014-04-03 15:57 | -21 | In target | 2014-02-19 17:01 | 2014-03-11 12:14 | Glenn McAllister
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-19 17:03 | S217008850001 | HOLMEFIELD HOUSE | 130802 | Completed | 8d | High | Miscellaneous | In the garden area opposite flat 416 there is an old mattress, soft chairs and a small table. | This is an external area but I would recommend that these items are removed from this area. | Neighbourhood Management | Martin Barr |  | This area is checked regularly and these items were removed some time ago. | 2014-06-05 | Fully Completed | Martin Barr | 2014-02-19 17:03 | 2014-03-12 17:04 | 2014-02-19 17:03 | 2014-06-06 09:44 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:04 | S217008850001 | HOLMEFIELD HOUSE | 130813 | Completed | 8e | Low | Communal Area Storage | No access could be gained to the residents storage areas of the building as these are private storage areas. | I would recommend that the ESA's carry out checks of these areas to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that these area are kept tidy with no excessive amounts of combustible items etc. | Neighbourhood Management | Martin Barr |  | These are resident private storage areas. The TMO does not hold keys for any private storage areas across our stock. | 2014-06-05 | Fully Completed | Martin Barr | 2014-02-20 09:04 | 2014-08-19 09:06 | 2014-02-20 09:04 | 2014-06-06 09:44 | -180 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 09:30 | S217008850001 | HOLMEFIELD HOUSE | 130843 | Completed | 18b | High | Inspection Regime | It is not known if any fire extinguishers or hose reels etc are located in the lower ground floor level car parking area of this building. | I would recommend that a check is undertaken to see if any fire extinguishers or hose reels etc are located in the lower ground floor level car parking area. If any are the last servicing/test dates should be checked to see if the items of equipment are in service date. If it is found that any equipment is out of test/service date it should be serviced immediately or removed. | Neighbourhood Management | Martin Barr |  | We have not found any extinguishers or hose reels. The area is being passed over to Nick Rendle's project team to look into commercial use of the space. | 2014-06-05 | Fully Completed | Martin Barr | 2014-02-20 09:30 | 2014-03-13 09:32 | 2014-02-20 09:30 | 2014-06-06 09:46 | -21 | In target
HOLMEFIELD HOUSE 2014.01.14 | 2014-02-20 10:56 | S217008850001 | HOLMEFIELD HOUSE | 130870 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire extinguishers and building being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Training on lighting testing due 23rd April. Checks will take place after this and once list of locations provided by A&R team. Block checks are completed and records kept. | 2014-04-17 | Fully Completed | Martin Barr | 2014-02-20 10:56 | 2014-03-13 10:57 | 2014-02-20 10:56 | 2014-04-22 09:03 | -21 | In target
HORTENSIA HOUSE, FLATS 1 - 8 - 2015.06.15 | 2015-06-26 14:55 | S217002700003 | HORTENSIA HOUSE (1-8) | 203633 | Completed | 13 | High | Miscellaneous | There is a metal ramp in the ground floor level entrance hall area of this building, it is not known if this ramp was installed to aid a disabled person who needs a mobility scooter. No scooters etc were parked in the entrance area at the time of this assessment. | I would recommend that this entrance hall area is checked on a regular basis to make certain that a mobility scooter is not being charged in this entrance hall area. It is acceptable for a mobility scooter to be parked here, in this entrance hall area but no charging must not take place here. | Neighbourhood Management | Wendy Stevenson |  | Olusola (ESA) confirms that he checks regularly for mobility scooters and is aware that they must not be charged in communal areas - to date he has not encountered this. | 2015-09-30 | Fully Completed | Janice Wray | 2015-06-26 14:55 | 2015-07-17 14:56 | 2015-06-26 14:55 | 2015-10-01 12:08 | -21 | In target
HORTENSIA HOUSE, FLATS 49 - 56 - 2015.06.15 | 2015-06-26 15:07 | S217002700005 | HORTENSIA HOUSE (49-56) | 203641 | Completed | 13 | High | Miscellaneous | There were two mobility scooters parked in the entrance area of this building at the time of this assessment. | I would recommend that this entrance hall area is checked on a regular basis to make certain that mobility scooters are not being charged in this entrance hall area. It is acceptable for a mobility scooter to be parked here, in this entrance hall area but no charging must not take place here. | Neighbourhood Management | Wendy Stevenson |  | Olusola (ESA) confirms that he checks regularly for mobility scooters and is aware that they must not be charged in communal areas - to date he has not encountered this. | 2015-09-30 | Fully Completed | Janice Wray | 2015-06-26 15:07 | 2015-07-17 15:09 | 2015-06-26 15:07 | 2015-10-01 12:09 | -21 | In target
HORTENSIA HOUSE, FLATS 9 - 48 - 2015.06.15 | 2015-06-26 15:00 | S217002700004 | HORTENSIA HOUSE (9-48) | 203635 | Completed | 13 | High | Miscellaneous | There is a ramp in the ground floor level entrance hall area of the staircase of flats 9 to 16, it is not known if this ramp was installed to aid a disabled person who needs a mobility scooter. No scooters etc were parked in the entrance area at the time of this assessment. | I would recommend that this entrance hall area is checked on a regular basis to make certain that a mobility scooter is not being charged in this entrance hall area. It is acceptable for a mobility scooter to be parked here, in this entrance hall area but no charging must not take place here. | Neighbourhood Management | Wendy Stevenson |  | Olusola (ESA) confirms that he checks regularly for mobility scooters and is aware that they must not be charged in communal areas - to date he has not encountered this. | 2015-09-30 | Fully Completed | Janice Wray | 2015-06-26 15:00 | 2015-07-17 15:02 | 2015-06-26 15:00 | 2015-10-01 12:11 | -21 | In target
HUNTER HOUSE - 2015.05.13 | 2015-05-27 09:35 | S217003720001 | HUNTER HOUSE | 198831 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Kamran Hye |  | completed by Kamran. | 2015-05-28 | Fully Completed | Jimmy Lemos | 2015-05-27 09:35 | 2015-06-17 09:36 | 2015-05-27 09:35 | 2015-05-29 13:06 | -21 | In target
HUNTER HOUSE - 2015.05.13 | 2015-05-27 09:37 | S217003720001 | HUNTER HOUSE | 198833 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | completed by ESA | 2015-05-28 | Fully Completed | Jimmy Lemos | 2015-05-27 09:37 | 2015-06-17 09:38 | 2015-05-27 09:37 | 2015-05-29 13:07 | -21 | In target
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:53 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171854 | Completed | 8a | High | Communal Area Storage | 8a High Residents are storing items outside their flats entrance doors. 1. There is a large table outside flat 315. 2. There is a wardrobe and other furniture outside flat 435. | I would recommend that the residents are asked to remove the items outside their flats. The residents should be reminder that the walkways should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading is kept as low as possible. (The LFB insist that the 3 finger blocks must be "zero tolerance" in relation to storage within the communal areas.) | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | Paul Steadman confirms items have been removed - 10th July 2015 | 2015-07-10 | Fully Completed | Janice Wray | 2014-11-28 10:53 | 2014-12-19 10:54 | 2014-11-28 10:53 | 2015-07-13 12:54 | -21 | In target | 2014-11-28 10:53 | 2015-07-17 12:53 | Janice Wray
HURSTWAY WALK - 2014.11.13 | 2014-11-28 10:55 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171855 | Completed | 8b | Low | Inspection Regime | The lower ground floor garages and storage areas of the building are private residential storage areas. | I would recommend that the caretakers carry out checks of these areas to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that these area are kept tidy with no excessive amounts of combustible items etc. | Neighbourhood Management | Siobhan Rumble | 2014-12-10 | caretakers do not have access to these garages. we carried out an audit in May 2012 and will carry out another this year. | 2012-05-11 | Fully Completed | Siobhan Rumble | 2014-11-28 10:55 | 2015-05-27 10:56 | 2014-11-28 10:55 | 2015-03-10 14:48 | -180 | In target | 2014-11-28 10:55 | 2014-12-22 16:52 | Siobhan Rumble
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:24 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171871 | Completed | 19a | High | Miscellaneous | The manual over ride control panel for the automatic opening vents, located by the entrance door of the 500 section, Latimer Road, has been painted over, this appears to have happened during the redecoration of this area. | I would recommend that this manual over ride control panel for the automatic open vents in this area is clean of all paint and that this manual override is tested to see that it works correctly. Could we get OCS to clean please? | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | OCS instructed to clean this - Siobhan Rumble | 2015-01-23 | Fully Completed | Siobhan Rumble | 2014-11-28 11:24 | 2014-12-19 11:25 | 2014-11-28 11:24 | 2015-01-26 14:00 | -21 | In target | 2014-11-28 11:24 | 2015-01-30 13:59 | Janice Wray
HURSTWAY WALK - 2014.11.13 | 2014-11-28 11:45 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171895 | Completed | 23b | High | Fire Alarm | Are the weekly occupier's tests of the fire alarm system in this building being undertaken. | Can it be confirmed that the caretaker(s) are undertaking the weekly occupiers testing of the fire alarm system in this building, there were no records of any testing or a fire logbook available at the time of this assessment. | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | System not fully operational at present - new control panels being installed - one for each walkway - so cannot be teaed curerntly | 2015-05-08 | Fully Completed | Siobhan Rumble | 2014-11-28 11:45 | 2014-12-19 11:51 | 2014-11-28 11:45 | 2015-05-11 13:42 | -21 | In target | 2014-11-28 11:45 | 2015-05-15 13:40 | Janice Wray
HURSTWAY WALK - 2014.11.13 | 2014-11-28 12:04 | S217012770013 | HURSTWAY WALK 301-39 & 401-39 | 171911 | Completed | 23d | High | Emergency Lighting | Are the monthly occupier testing and inspections of the emergency escape lighting system, the fire extinguishers and the buildings structural inspections being undertaken? | Can it be confirmed that the caretakers are undertaking the occupiers monthly testing and inspections of the installed systems, as per the caretakers check list in these buildings? With the results completed records kept as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble | 2015-01-12 | Tests & inspections are now being recorded | 2015-01-23 | Fully Completed | Siobhan Rumble | 2014-11-28 12:04 | 2014-12-19 12:05 | 2014-11-28 12:04 | 2015-01-26 13:58 | -21 | In target | 2014-11-28 12:04 | 2015-01-30 13:57 | Janice Wray
INGELOW HOUSE - 2015.06.15 | 2015-06-30 11:14 | S217002640001 | INGELOW HOUSE | 204018 | Completed | 8 | High | Communal Area Storage | By the base of the stairs down to the lower ground floor level from the entrance hall area of flats 1 to 4, there is a pile of bedding, part of a bed and some other combustible items being stored here. | I would recommend that these items are removed from the walkway area. Wendy | Neighbourhood Management | Wendy Stevenson | 2015-06-21 | REMOVED COMPLETED | 2015-08-13 | Fully Completed | Janice Wray | 2015-06-30 11:14 | 2015-07-21 11:16 | 2015-06-30 11:14 | 2016-03-15 16:54 | -21 | In target
INGELOW HOUSE - 2015.06.15 | 2015-06-30 16:31 | S217002640001 | INGELOW HOUSE | 204147 | Completed | 23e | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc | Neighbourhood Management | Wendy Stevenson |  | John Whall confirms inspections undertaken | 2015-10-09 | Fully Completed | Janice Wray | 2015-06-30 16:31 | 2015-07-21 16:32 | 2015-06-30 16:31 | 2015-10-12 13:12 | -21 | In target
JEAN DARLING HOUSE, MILMAN STREET, LONDON SW10 0BX - 2016.11.21 | 2016-12-20 11:26 | S217012760006 | JEAN DARLING HOUSE | 274037 | Completed | 23b | High | Inspection Regime | It is not known if the monthly occupiers testing of the emergency lighting units installed on the means of escape routes of this building are being undertaken. | Can it please be confirmed that the ESA's /caretakers are undertaking the occupiers checks and tests of this building as per the caretakers check list with the results recorded as proof of testing? | Neighbourhood Management | Nicola Rees | 2017-01-17 | This is being completed. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-12-20 11:26 | 2017-01-10 11:30 | 2016-12-20 11:26 | 2017-01-16 11:33 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:18 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181511 | Completed | 2 | Information Only | Signage | There is presently not a "No smoking" sign displayed in this building. A No Smoking sign was left with the resident's association member who wanted to fit the sign in a frame before hanging it on the wall. | I would recommend that the caretaker is asked to confirm that the sign is displayed. | Neighbourhood Management | Wendy Stevenson |  | sign is displayed 16/03/15 | 2015-05-07 | Fully Completed |  |  |  | 2015-02-03 10:18 | 2015-05-11 09:59
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:20 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181514 | Completed | 8 | Medium | Miscellaneous | The vegetation and flowers etc outside the rear exit door in the garden are overgrown and the rear exit door cannot be opened easily. | I would recommend that the vegetation and flowers etc in the garden area directly outside the rear exit door of this building are cut back so that the door can be opened without being obstructed. | Neighbourhood Management | John Gaffney |  | Landscape Team have investigated and advise there is no rear exit door from this area | 2015-11-18 | Fully Completed | Janice Wray | 2015-02-03 10:20 | 2015-04-04 10:21 | 2015-02-03 10:20 | 2015-11-19 09:53 | -60 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:21 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181516 | Completed | 13a | High | Inspection Regime | There is an emergency pull cord located in the toilet of this building, it is not known if this emergency pull cord is tested weekly in accordance with the manufacturers guidance. | Can it please be confirmed that the emergency pull cord located in the toilet, with an indicator light above the toilet door and a control panel on the wall is being tested weekly in accordance with the manufactures instructions and that records are kept? | Neighbourhood Management | Wendy Stevenson |  | in working order 16/03/15 | 2015-03-16 | Fully Completed | Janice Wray | 2015-02-03 10:21 | 2015-02-24 10:22 | 2015-02-03 10:21 | 2015-05-11 12:44 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:23 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181519 | Completed | 13b | Low | Miscellaneous | There is a control box, "Diplomat" located on the wall on the left hand side of the entrance door. There are 2 red lights showing on this control box, zones 1 and 2, the occupant seems to think this is a panic alarm device? | Can it please be confirmed what this "Diplomat" control box is wired up to? If this is a panic alarm is it in working order? Or what is this control box for? If this is a panic alarm is it tested, serviced and maintained in accordance with any manufacturers instructions? Wendy - do you know anything about this? | Neighbourhood Management | Wendy Stevenson |  | still investigating - not a panic alarm | 2015-07-28 | Fully Completed | Janice Wray | 2015-02-03 10:23 | 2015-08-02 10:24 | 2015-02-03 10:23 | 2015-07-29 19:53 | -180 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:29 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181526 | Completed | 23c | High | Inspection Regime | Are the weekly occupier's tests of the Building's fire alarm and warning system being undertaken? This is a domestic fire alarm system but the guidance is still for weekly tests to be undertaken. | Can it be confirmed that the weekly occupiers testing of the installed fire alarm system is being undertaken? If it is being tested are records of any testing being kept as proof of testing, if testing is not being undertaken then weekly testing should start and records of this testing kept as proof of testing. | Neighbourhood Management | Wendy Stevenson |  |  | 2015-05-08 | Fully Completed | Janice Wray | 2015-02-03 10:29 | 2015-02-24 10:30 | 2015-02-03 10:29 | 2015-05-11 13:47 | -21 | In target
JOHN KEYS RESOURCE CENTRE - 2014 .10.14 | 2015-02-03 10:31 | S217004267710 | JOHN KEYS RESOURCE CENTRE | 181527 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Wendy Stevenson |  |  | 2015-05-08 | Fully Completed | Janice Wray | 2015-02-03 10:31 | 2015-02-24 10:31 | 2015-02-03 10:31 | 2015-05-11 12:56 | -21 | In target
KELFIELD COURT - 2015.06.03 | 2015-06-11 15:23 | S217009010001 | KELFIELD COURT | 201156 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 15:23 | 2015-07-02 15:24 | 2015-06-11 15:23 | 2015-09-21 08:56 | -21 | In target
KELFIELD COURT - 2015.06.03 | 2015-06-11 15:24 | S217009010001 | KELFIELD COURT | 201157 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-11 15:24 | 2015-07-02 15:25 | 2015-06-11 15:24 | 2015-09-21 08:55 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 13:43 | B217009120001 | KENSAL HOUSE | 102844 | Completed | 12c | High | Miscellaneous | There are a lot of pots of plants on the staircase landing outside flats 16 and 17 and on the stairs and the half landing below this landing. These plants are reducing the width of the staircase and could cause a trip hazard. | Some of these pots of plants should be removed from the landings and off the steps of the staircase so they are not a trip hazard or reduce the width of the means of escape route. A few pots of plants etc are I believe acceptable against the wall on the top floor landing but the staircase should be kept clear at all times. | Neighbourhood Management | Glenn McAllister | 2013-09-10 | Could the residents be asked to remove the plant pots from the stairs. (It is fine for a few pots to be positioned on the top floor landing against the wall where they will not cause an obstruction.) | 2013-08-21 | Fully Completed | Glenn McAllister | 2013-08-20 13:43 | 2013-09-10 14:03 | 2013-08-20 13:43 | 2013-08-22 14:39 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 15:03 | B217009120001 | KENSAL HOUSE | 102890 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire fighting equipment in the building being undertaken along with the other items on the caretakers checklist, with records kept? As all the fire extinguishers are over 2 years out of test date these monthly inspections appear not to be happening. | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr | 2013-09-10 | Please confirm these regular inspections are taking place and are documented. Please confirm this would involve regular visual inspection of fire extinguishers. Checks are carried out by a contractor, RGE, who are paid for the service. ESAs will check visually where they see equipment and log on the current checklist, but they will not necessarily check every location on a block inspection. When I visited Kensal House the extinguisher I found in an intake cupboard had been recently checked. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 15:03 | 2013-09-10 15:09 | 2013-08-20 15:03 | 2013-10-14 11:43 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 15:10 | B217009120001 | KENSAL HOUSE | 102895 | Completed | 23e | High | Fire Alarm | Are the weekly occupier's tests of the installed fire alarm systems in these buildings being undertaken? If they are how are these being undertaken as there are no break glass call points or other testing points visible. | Can it be confirmed that the caretaker(s) are undertaking the weekly occupiers testing of the fire alarm systems with records being kept as proof of testing having been undertaken? | Neighbourhood Management | Martin Barr | 2013-09-10 | Please discuss with H&S. Weekly testing of alarm is necessary but this could only be done if staff are trained and competemt to do testing and resdents are informed in advance. Assessor has now investigated and confirmed that these detectors cn be removed from the building - works initiated. | 2014-08-15 | Fully Completed | Martin Barr | 2013-08-20 15:10 | 2013-09-10 15:13 | 2013-08-20 15:10 | 2014-08-18 14:57 | -21 | In target | 2013-08-20 15:10 | 2014-08-22 14:55 | Janice Wray
KENSAL HOUSE - 2013.06.01 | 2013-08-20 14:25 | B217009120001 | KENSAL HOUSE | 102869 | Completed | 22 | Medium | Miscellaneous | The lower ground floor areas of these buildings are occupied by other occupiers and under their control. | I would recommend that the occupiers of the lower ground floor level areas are asked for their fire risk assessments and the significant findings from them. Once these have been obtained then any actions on the significant findings sheet that may be applicable to the TMO parts of the buildings should be action-ed. | Neighbourhood Management | Glenn McAllister | 2013-09-10 | Could you please advise of names & contact details of who uses these areas so thatwe can write and request copie of their FRA.OCS AND THEATRE GROUP ADDRESS IS BASEMENT AREA KENSAL HOUSE. LADBROKE GROVE. LONDON W10 5BQ | 2013-08-21 | Fully Completed | Glenn McAllister | 2013-08-20 14:25 | 2013-10-19 14:50 | 2013-08-20 14:25 | 2013-09-10 13:33 | -60 | In target | 2013-08-20 14:25 | 2013-09-12 13:17 | Glenn McAllister
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:36 | B217009120001 | KENSAL HOUSE | 102800 | Completed | 8a | High | Communal Area Storage | On the staircase landing outside flats 4 and 5 there is an old washing machine, on the landing outside flats 20 and 21 there is an old slot in electrical cooker and on the landing outside flats 67 and 68 an old large television. | These three household appliances should be removed from these staircase landing areas as they are restricting the means of escape routes. I would recommend that the residents are reminded of the TMO policy for the collection of bulk items and the caretaker reminded about the reporting procedure for items in the common parts of the building. | Neighbourhood Management | Martin Barr | 2013-09-10 | All of the items have been removed. ESAs (caretakers) are aware of reporting bulk items. Where it is identified which resident has left it we deal with the individuals, otherwise OCS are asked to clear the bulk items. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 11:36 | 2013-09-10 11:38 | 2013-08-20 11:36 | 2013-10-14 09:42 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:43 | B217009120001 | KENSAL HOUSE | 102802 | Completed | 8b | High | Communal Area Storage | Outside flat 1 in the entrance lobby area there are numerous black bags of clothes and household items. | These bags should be removed from this entrance lobby area. The occupier of flat 1 should be reminder that the entrance lobby area should be maintained free of all items of storage so there is no fuel source for a fire and the fire loading of the staircase enclosure is kept as low as possible. | Neighbourhood Management | Martin Barr | 2013-09-10 | I have knocked on the door of flat 1 during a previous inspection and asked them to store items inside, which they did at the time. There were some smaller items back on a follow up check on 10th October. This has been referred to Glenn McAlister, Neighbourhood Officer, to deal with. Cleared | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 11:43 | 2013-09-10 11:45 | 2013-08-20 11:43 | 2017-03-13 12:35 | -21 | In target | 2013-08-20 11:43 | 2017-03-17 12:35 | Janice Wray
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:45 | B217009120001 | KENSAL HOUSE | 102803 | Completed | 8c | High | Communal Area Storage | At the lower ground floor level behind the entrance/exit door by flat 38 there are folding tables and chairs being stored. | These items should be removed from the staircase. | Neighbourhood Management | Martin Barr | 2013-09-10 | Items have all been removed. This has been checked for completion. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 11:45 | 2013-09-10 11:47 | 2013-08-20 11:45 | 2013-10-14 10:35 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:47 | B217009120001 | KENSAL HOUSE | 102804 | Completed | 8d | High | Communal Area Storage | In the rear externally accessed room behind the staircase for flats 28 to 37 there is a lot of contractors waste, old light fittings etc. | All the waste etc should be removed from this area. | Neighbourhood Management | Martin Barr | 2013-09-10 | An order has been raised for cleaning contractors to remove the waste items. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 11:47 | 2013-09-10 11:49 | 2013-08-20 11:47 | 2013-10-14 10:41 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:49 | B217009120001 | KENSAL HOUSE | 102806 | Completed | 8e | High | Communal Area Storage | A push bike tyre pump is located on the fire alarm system sounder by flats 67 and 68, this pump is wedged behind the sounder cable and could damage the cable. | This push bike tyre pump should be removed immediately and the owner of it told not to store it in this location again as it could damage the fire alarm sounder or its cable. | Neighbourhood Management | Martin Barr | 2013-09-10 | This item has been removed, confirmed by inspection. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 11:49 | 2013-09-10 11:51 | 2013-08-20 11:49 | 2013-10-14 10:42 | -21 | In target
KENSAL HOUSE - 2013.06.01 | 2013-08-20 11:51 | B217009120001 | KENSAL HOUSE | 102808 | Completed | 8f | Medium | Storage | The external balcony of I believe flat 21 in over loaded with stored items of furniture and cardboard boxes. | I would recommend that the occupant of this flat is asked to tidy up this balcony and remove some of the items stored on it. | Neighbourhood Management | Glenn McAllister | 2013-09-17 | The LFB do raise issues of excessive storage of combustible items on private balconies with us. Whilst this is not in the communal area it does increase the fire loading of the building and the overall potential fire risk so grateful if you could encourage tenant to reduce this. LETTERS TO ALL RESIDENTS, 5.9.2013 Some storage removed & situation being monitored - ONGOING | 2013-08-21 | Fully Completed | Glenn McAllister | 2013-08-20 11:51 | 2013-10-19 11:56 | 2013-08-20 11:51 | 2017-03-13 12:41 | -60 | In target | 2013-08-20 11:51 | 2017-03-17 12:40 | Janice Wray
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:38 | S217007970011 | KENSAL COMMUNITY OFFICE | 181619 | Completed | 17a | High | Fire Alarm | The installed fire detection/alarm system covers both of these areas of the building, with the fire alarm control panel being located in the OCS area. | Can it please be confirmed what is the procedure if the fire alarm system activates when the community area is in use and the control panel in the OCS area cannot be accessed because the office is closed? Do the residents association or the caretakers have accessed to the OCS office area? It may be that the fire alarm panel has to be relocated so that it can be accessed at all times. | Neighbourhood Management | Sarah Lynch |  | Confirmation that the ESA has a key to the OCS office | 2015-11-17 | Fully Completed | Janice Wray | 2015-02-03 12:38 | 2015-02-24 12:39 | 2015-02-03 12:38 | 2015-11-18 21:58 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:43 | S217007970011 | KENSAL COMMUNITY OFFICE | 181622 | Completed | 21 | Information Only | Miscellaneous | It is not known if the OCS manager and his staff have received any fire safety training and know how to use the fire extinguishers etc in their area. | I would recommend that the OCS manager is asked if all of his staff in this area have receive suitable fire training? | Neighbourhood Management | Sarah Lynch |  | OCS Manager Steve Warwick is aqualified fire ground training instructor and has shown the office staff how to use the extinguishers. | 2015-11-17 | Fully Completed |  |  |  | 2015-02-03 12:43 | 2015-11-18 22:01
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:44 | S217007970011 | KENSAL COMMUNITY OFFICE | 181624 | Completed | 23a | High | Inspection Regime | Are the weekly occupier's tests of the premises fire alarm and warning system being undertaken? | Can it be confirmed who is undertaking the weekly occupiers testing of the installed fire alarm system of these areas? If it is being tested are records of any testing being kept as proof of testing, if testing is not being undertaken then weekly testing should start and records of this testing kept as proof of testing in the fire logbook located next to the fire alarm panel. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-02-03 12:44 | 2015-02-24 12:46 | 2015-02-03 12:44 | 2015-09-21 09:43 | -21 | In target
KENSAL HOUSE COMMUNITY AREA AND OCS OFFICE- 2014.06.24 | 2015-02-03 12:49 | S217007970011 | KENSAL COMMUNITY OFFICE | 181628 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and the fire extinguishers in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system and the extinguishers in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-03 12:49 | 2015-02-24 12:50 | 2015-02-03 12:49 | 2015-05-19 12:06 | -21 | In target
KENSAL HOUSE, LADBROKE GROVE, LONDON W10 5BQ - 2016.08.29 | 2016-10-03 15:12 | B217009120001 | KENSAL HOUSE | 271476 | Completed | 12c | High | Inspection Regime | The nosing on some of the steps of the staircases in these buildings are damaged or are missing. There are too many areas to mention individually, the damaged or missing nosing could result in a trip and fall down the stairs. | I would recommend that a check of all the steps of the staircases is undertaken and any damaged or missing nosing is repaired or replaced. Could ESA please survey & raise with Repairs | Neighbourhood Management | Louise Nezandonyi | 2016-10-31 | Comprehensive inspection undertaken by ESA on 4th Nov & photos and schedule of defects given to John Griffin in Repairs. He will discuss with his manager how best to progress ESA to monitor completion | 2016-11-07 | Fully Completed | Janice Wray | 2016-10-03 15:12 | 2016-10-24 15:14 | 2016-10-03 15:12 | 2016-11-08 17:04 | -21 | In target
KENSAL HOUSE, LADBROKE GROVE, LONDON W10 5BQ - 2016.08.29 | 2016-10-03 15:14 | S217009120014 | KENSAL HOUSE 8-48 | 271477 | Active | 12d | Information Only | Inspection Regime | There are pots of plants on the staircase landing outside flats 16 and 17 and on the staircase half landing below this flat landing area. There were no pots of plants on the staircase at the time of this assessment. The plants are against the walls and not overly reducing the width of the staircase and they are not presently a trip hazard. | The amount of plants on these landing areas should be monitored and if any pots of plants are placed on the steps of the staircase then these should be removed immediately. | Neighbourhood Management | Louise Nezandonyi | 2017-10-02
KENSAL HOUSE, LADBROKE GROVE, LONDON W10 5BQ - 2016.08.29 | 2016-10-03 15:32 | B217009120001 | KENSAL HOUSE | 271484 | Active | 23d | High | Inspection Regime | It is not known if any caretaker testing and inspections of the fire fighting equipment, emergency lighting and the buildings structural items are being undertaken? | Can it be confirmed that the caretaker(s) are undertaking the tasks as per the caretakers check list in these buildings, with the completed sheets kept as a records and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-10-31 |  |  |  | Cyril Morris | 2016-10-03 15:32 | 2016-10-24 15:34 |  |  | 136 | 136 days overdue
KENSINGTON MANSIONS - 2015.04.09 | 2015-04-27 14:36 | S217006800001 | KENSINGTON MANSIONS | 194308 | Completed | 1 | Medium | Miscellaneous | I am told that there is a vacuum cleaner kept in the ground floor level under staircase cupboard of this building. This is used by the cleaner to vacuum the carpeted entrance hall area and the staircase. | Please can it be confirmed that this electrically powered vacuum cleaner is in date for Portable electrical Appliance Testing (PAT). If it is not I would recommend that a PAT is undertaken immediately and any defects found rectified. | Neighbourhood Management | Stephen Walters |  | All OCS electrical equipment is Pat tested yearly and a log book is kept in the OCS Office at Kensal House, Pat testing is due again in November 15. | 2015-11-17 | Fully Completed | Janice Wray | 2015-04-27 14:36 | 2015-06-26 14:39 | 2015-04-27 14:36 | 2015-11-18 22:05 | -60 | In target
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 11:45 | S217002180001 | KEPPEL HOUSE | 200433 | Completed | 8 | Low | Communal Area Storage | There were some items stored under the secondary staircase by flat 12, there was a folded up wheelchair and a set of step ladders and a metal ladder. | I would recommend that the caretaker is asked to check this area regularly and if the amount of storage under this staircase becomes excessive or combustible items are stored here then all storage is removed. | Neighbourhood Management | Kamran Hye |  | Felix (ESA) confirms he is monitoring storage in this area | 2015-09-30 | Fully Completed | Jimmy Lemos | 2015-06-08 11:45 | 2015-12-05 11:46 | 2015-06-08 11:45 | 2015-10-01 11:55 | -180 | In target | 2015-06-08 11:45 | 2015-10-07 11:53 | Janice Wray
[Redacted] - 2015.05.22 | 2015-06-08 11:46 | S217002180001 | KEPPEL HOUSE | 200434 | Active | 12 | High | Flat Door | New flat entrance doors have been fitted to flats 7 and 8, these doors have clear glazing in the vision panels which is not marked as fire rated glass and they do not have self closing devices fitted to them. | It should be confirmed that these 2 new flat entrance doors are 30 minute fire rated doors (FD30), if they are not then new FD30 doors should be fitted. But self closing devices must be fitted to these doors. | Neighbourhood Management | Nazrul Islam | 2015-06-18 | Mr [redacted] Direct Line: [Redacted] [Redacted] e-mail: nislam@kctmo.org.uk [Redacted] Date: 18th June 2015 Our Reference Your Reference Please Contact TMO/LHS/NI/ [Redacted] Nazrul Islam Re: Front Door - FRA Review Dear [redacted], I write to inform you that as part of our ongoing commitment to ensure the safety and compliance of our residents, our Fire Safety Consultant has undertaken a further, more detailed, review. It is reported a new flat entrance doors have been fitted to flats [redacted] this doors have clear glazing in the vision panels which is not marked as fire rated glass and they do not have self closing devices fitted to them. As a result of this review, it has come to light that your front entrance door may not be a FD30 compliant door. I must therefore request the following: " Confirmation as to whether your door is FD30 rated, if you are unable to clarify, we can arrange for our consultant to visit the property with you to assess the door. " FD30 rated doors need to have a self closing device to comply with the requirements of the Building Regulations, can you please confirm if this in place " If your door is not compliant then you will have to replace the door with a compliant one and provide us with confirmation of the new doors compliance I have attached a guide which may be of use but should you have any further questions then please contact Janice Wray on [Redacted]. Regards Nazrul Islam Home Ownership Officer | 2015-06-18 | Partially Completed | Nazrul Islam | 2015-06-08 11:46 | 2015-06-29 11:48 | 2015-06-08 11:46 | 2015-06-23 13:56 | -21 | In target | 2015-06-08 11:46 | 2015-06-26 14:55 | Nazrul Islam
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 12:36 | S217002180001 | KEPPEL HOUSE | 200469 | Completed | 19 | High | Inspection Regime | There is a fire fighters switch located on the wall by the main staircase entrance door of this building, I think that this fire fighter's switch is for the retail units brand/shop advertising signs. | I would recommend that the retail unit is asked to confirm that this fire fighters switch is for their brand/shop advertising signs. If it is it should be signed accordingly, a red and yellow sign. Jimmy - Can you confirm? | Neighbourhood Management | Jimmy Lemos |  | completed by Felix Akumany | 2015-06-26 | Fully Completed | Jimmy Lemos | 2015-06-08 12:36 | 2015-06-29 12:38 | 2015-06-08 12:36 | 2015-07-13 15:21 | -21 | In target
KEPPEL HOUSE - 2015.05.22 | 2015-06-08 12:40 | S217002180001 | KEPPEL HOUSE | 200478 | Completed | 23b | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and the fire fighting equipment. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Kamran Hye |  | completed by ESA Felix Akumany | 2015-06-26 | Fully Completed | Jimmy Lemos | 2015-06-08 12:40 | 2015-06-29 12:42 | 2015-06-08 12:40 | 2015-07-13 15:22 | -21 | In target
KING CHARLES HOUSE, WANDON ROAD, LONDON SW6 2JH - 2016.04.04 | 2016-05-25 11:02 | S217008550001 | KING CHARLES HOUSE | 262376 | Active | 1b | Medium | Inspection Regime | Next to each flat entrance door there is a cabinet/box inserted in the wall which contains electrical wiring etc. A lot of the cabinets/boxes have their lock damaged and are not secured shut. | I would recommend that all these cabinets/ boxes are checked and any that do not lock have new locks fitted to them, this is to stop unauthorised persons tampering with the flats electrics. Nicola Could the ESA pick these up on his regular inspections and request orders accordingly please | Neighbourhood Management | Nicola Rees | 2016-08-24 | Email sent to Rahman 28.09.16. This is near completion and there are two floors to be done br RD (update 13.01.17) |  | Partially Completed | Cyril Morris | 2016-05-25 11:02 | 2016-07-24 11:06 |  |  | 228 | 228 days overdue
KING CHARLES HOUSE, WANDON ROAD, LONDON SW6 2JH - 2016.04.04 | 2016-05-25 11:57 | S217008550001 | KING CHARLES HOUSE | 262403 | Completed | 12d | High | Inspection Regime | There are cold smoke seals fitted to the self closing fire doors of the flat/lift lobby areas to the staircase enclosure. Some of these cold smoke seals are damaged and the doors now do not close fully or the cold smoke seal is stopping the door from closing fully. | All of the flat/lift lobby area to the staircase enclosure fire doors should be checked and the doors adjusted etc or the cold smoke seals refitted so that all of these doors close fully on to the door stops. Any damaged or missing pieces of cold smoke seal must be replaced. The caretaker should regularly check these fire doors and these inspections should be recorded as proof of the inspections having been undertaken. Nicola Could these be picked up by ESA on his inspection and fed through to repairs with specific location details please | Neighbourhood Management | Nicola Rees | 2016-06-15 | Email sent to Rahman 28.09.16. This has been reported under reference 201624611. Two doors sent to a specialist as spring mechanism issues but thes rest completed. | 2016-10-14 | Fully Completed | Nicola Rees | 2016-05-25 11:57 | 2016-06-15 12:00 | 2016-05-25 11:57 | 2016-10-17 17:34 | -21 | In target
KING CHARLES HOUSE, WANDON ROAD, LONDON SW6 2JH - 2016.04.04 | 2016-05-25 12:07 | S217008550001 | KING CHARLES HOUSE | 262407 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system/units in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-06-15
KING CHARLES HOUSE, WANDON ROAD, LONDON SW6 2JH - 2016.04.04 | 2016-05-25 12:27 | S217008550001 | KING CHARLES HOUSE | 262413 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure and items, as some fire extinguishers are years out of service date it appears that no caretakers inspections are being undertaken. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Nicola Rees | 2016-06-15 | We have put in better place monitoring of the fire extinguishers in order to make sure that this situation is not ongoing. | 2016-12-01 | Fully Completed | Nicola Rees | 2016-05-25 12:27 | 2016-06-15 12:29 | 2016-05-25 12:27 | 2016-12-02 16:16 | -21 | In target
KINGSNORTH HOUSE, SILCHESTER ROAD, LONDON W10 6SH - 2016.06.08 | 2016-06-28 16:59 | S217009980002 | KINGSNORTH HOUSE | 266281 | Active | 23b | High | Emergency Lighting | There are emergency lighting units installed on each of the staircase landings, the means of escape routes of this building, it is not known if the monthly occupiers testing of these lights is being undertaken. | Can it please be confirmed that the caretaker is undertaking the occupiers checks and tests of this building as per the caretakers check list with the results recorded as proof of testing? | Neighbourhood Management | Louise Nezandonyi | 2016-07-19
LACLAND HOUSE, MILMAN STREET, LONDON SW10 0BP - 2016.01.28 | 2016-02-19 16:03 | S217012760002 | LACLAND HOUSE | 244682 | Completed | 8 | Medium | Communal Area Storage | There is storage on the landings of the secondary staircases at the rear of the flats. | All storage should be removed from the landings of these two secondary staircases. | Neighbourhood Management | Nicola Rees | 2016-05-23 | This is no longer there. Verified by ESA on 14.04.16 | 2016-04-14 | Fully Completed | Nicola Rees | 2016-02-19 16:03 | 2016-04-19 16:04 | 2016-02-19 16:03 | 2016-04-18 17:33 | -60 | In target
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 11:09 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164643 | Completed | 1b | Medium | Miscellaneous | One of the two fridges in the kitchen has a portable electrical appliance "Failed" label on it. This fridge is not in use presently. | Can it please be confirmed what is happening to this fridge, is it being repaired or removed from this area and disposed of? | Neighbourhood Management | Siobhan Rumble |  | i have instructed the estate supers to have this disposed of | 2014-11-04 | Fully Completed | Siobhan Rumble | 2014-10-09 11:09 | 2014-12-08 11:10 | 2014-10-09 11:09 | 2014-11-05 14:00 | -60 | In target | 2014-10-09 11:09 | 2014-11-11 13:59 | Janice Wray
LANCASTER WEST COMMUNITY ROOMS ( FORMERLY CARETAKERS OFFICE) | 2014-10-09 12:26 | S217012770014 | LANCASTER WEST COMMUNITY ROOMS | 164670 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Siobhan Rumble | 2014-12-24 | yes fire extinguishers are being checked | 2015-06-05 | Fully Completed | Siobhan Rumble | 2014-10-09 12:26 | 2014-10-30 12:27 | 2014-10-09 12:26 | 2015-06-22 15:00 | -21 | In target | 2014-10-09 12:26 | 2015-06-26 14:58 | Janice Wray
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 11:28 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164256 | Completed | 23a | High | Inspection Regime | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Can it be confirmed that the occupiers of this premises are undertaking the weekly occupiers testing of the installed fire alarm system? If it is being tested are records of any testing being kept as proof of testing, if testing is not being undertaken then weekly testing should start and records of this testing kept as proof of testing. | Neighbourhood Management | Siobhan Rumble | 2014-12-10 | RBKC Compliance Officer advised as follows on 12th Dec - "I have spoken to Amey and they have confirmed they will be carrying out weekly fire alarm checks at baseline Studios. The Amey Facilities Manager for the site is Ray Tuthill e-mail ray.tuthill@amey.co.uk" | 2014-12-15 | Fully Completed | Siobhan Rumble | 2014-10-07 11:28 | 2014-10-28 11:30 | 2014-10-07 11:28 | 2014-12-16 16:53 | -21 | In target | 2014-10-07 11:28 | 2014-12-22 16:52 | Janice Wray
LANCASTER WEST OFFICE ( FORMERLY EMB ROOMS ) | 2014-10-07 12:06 | S217012777701 | TMO CLUBROOM EMB CLUBROOM | 164266 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the office manager or a designated person is undertaking the monthly occupier tests of fire extinguishers and the buildings structure and recording these inspections?. | Neighbourhood Management | Siobhan Rumble |  | The estate officers carry out weekly testing of the fire alarm and the panic alarm for the office, also the fire extinguishers | 2014-10-10 | Fully Completed | Siobhan Rumble | 2014-10-07 12:06 | 2014-10-28 12:08 | 2014-10-07 12:06 | 2014-10-13 12:32 | -21 | In target
LEDBURY HOUSE | 2015-03-26 16:19 | S217012270005 | LEDBURY HOUSE | 190075 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting units installed in specific areas of this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting units should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-03-26 16:19 | 2015-04-16 16:20 | 2015-03-26 16:19 | 2015-05-19 12:07 | -21 | In target
LONGLANDS COURT FLATS 1 TO 48,WESTBOURNE GROVE, LONDON W11 2QE - 2016.03.14 | 2016-04-20 10:50 | S217010567701 | LONGLANDS COURT (1-48) | 255431 | Active | 2 | High | Inspection Regime | At the roof level there is some discarded used smoking material in two of the lift and water tank rooms. | All of the used smoking material should be removed from these roof areas. | Neighbourhood Management | Louise Nezandonyi | 2016-05-25
LONGLANDS COURT FLATS 1 TO 48,WESTBOURNE GROVE, LONDON W11 2QE - 2016.03.14 | 2016-04-20 10:52 | S217010567701 | LONGLANDS COURT (1-48) | 255432 | Active | 8a | High | Inspection Regime | At the roof level there is contractors waste in two of the lift and water tank rooms. | All of this contractors waste should be removed from these roof areas. | Neighbourhood Management | Louise Nezandonyi | 2016-05-25
LONGLANDS COURT FLATS 1 TO 48,WESTBOURNE GROVE, LONDON W11 2QE - 2016.03.14 | 2016-04-20 10:54 | S217010567701 | LONGLANDS COURT (1-48) | 255434 | Active | 8b | High | Communal Area Storage | Outside the flat entrance door of flat [redacted] there is a mobility scooter being parked and also a number of other items. I understand that the TMO are allowing this resident to park their mobility scooter here, it is charged outside of the building. But the other items should be removed from this entrance hall area. | Remove all other storage from the entrance hall area outside of this flat entrance door. | Neighbourhood Management | Louise Nezandonyi | 2016-05-25
LONGLANDS COURT FLATS 1 TO 48,WESTBOURNE GROVE, LONDON W11 2QE - 2016.03.14 | 2016-04-20 11:39 | S217010567701 | LONGLANDS COURT (1-48) | 255484 | Active | 14c | High | Inspection Regime | At the roof level the metal sub division door cannot be shut because there is a portable ladder laid along the corridor obstructing this door from be closed. | The ladder should be removed and the metal sub division door kept in the closed position unless in use. Louise - As Ken is on light duties can we get someone else to assist with this relocation of ladder? | Neighbourhood Management | Louise Nezandonyi | 2016-05-25
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:14 | S217012770017 | CLARENDON WALK 1-24 | 219179 | Completed | 8a | High | Communal Area Storage | There are open areas on Clarendon Walk which are fenced off and are being used as storage areas, other ones are empty spaces. The areas located between flats 41 and 44 and flat 40 and 43 have a lot of cardboard boxes in them and other items. | I would recommend that the persons who have storage in these areas are asked can they tidy up the boxes and remove and old and damaged items. I believe that if the boxes are stored tidily them some storage in these areas is acceptable. Siobhan | Neighbourhood Management | Siobhan Rumble |  |  | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-09-30 12:14 | 2015-10-21 12:15 | 2015-09-30 12:14 | 2015-10-15 10:30 | -21 | In target
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:16 | S217012770017 | CLARENDON WALK 1-24 | 219182 | Completed | 8b | Medium | Communal Area Storage | On Clarendon Walk they are fenced off areas outside flats 1, 14 and 42 which are private areas, there is some storage in these private areas. | I would recommend that the occupants of these flats are asked that can they tidy up these areas and remove and old boxes etc. I believe that if any storage is tidy then this is acceptable, for instance flat 1 uses this area as a gym area. At the time of this assessment there were a lot of black bags piled up on the weights bench. | Neighbourhood Management | Siobhan Rumble |  | done | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-09-30 12:16 | 2015-11-29 12:18 | 2015-09-30 12:16 | 2015-10-15 10:51 | -60 | In target
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:20 | S217012770017 | CLARENDON WALK 1-24 | 219186 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | yes and recorded on the mobile devices | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-09-30 12:20 | 2015-10-21 12:22 | 2015-09-30 12:20 | 2015-10-15 10:52 | -21 | In target
LOWER, UPPER AND CLARENDON WALK - 2015.07.08 | 2015-09-30 12:24 | S217012770017 | CLARENDON WALK 1-24 | 219189 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes done | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-09-30 12:24 | 2015-10-21 12:28 | 2015-09-30 12:24 | 2015-10-15 10:52 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:33 | S217012770019 | CLARENDON WALK 33-56 | 212625 | Completed | 8a | High | Communal Area Storage | There are open areas on Clarendon Walk which are fenced off and are being used as storage areas, other ones are empty spaces. The areas located between flats 41 and 44 and flat 40 and 43 have a lot of cardboard boxes in them and other items. | I would recommend that the persons who have storage in these areas are asked can they tidy up the boxes and remove and old and damaged items. I believe that if the boxes are stored tidily them some storage in these areas is acceptable. | Neighbourhood Management | Siobhan Rumble |  | done | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-08-19 10:33 | 2015-09-09 10:34 | 2015-08-19 10:33 | 2015-10-15 10:37 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:35 | S217012770017 | CLARENDON WALK 1-24 | 212626 | Completed | 8b | Medium | Communal Area Storage | On Clarendon Walk they are fenced off areas outside flats 1, 14 and 42 which are private areas, there is some storage in these private areas. | I would recommend that the occupants of these flats are asked that can they tidy up these areas and remove and old boxes etc. I believe that if any storage is tidy then this is acceptable, for instance flat 1 uses this area as a gym area. At the time of this assessment there were a lot of black bags piled up on the weights bench. | Neighbourhood Management | Siobhan Rumble |  |  | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-08-19 10:35 | 2015-10-18 10:37 | 2015-08-19 10:35 | 2015-10-15 10:31 | -60 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:43 | S217012770017 | CLARENDON WALK 1-24 | 212630 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | these are completed on the mobile working phones | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-08-19 10:43 | 2015-09-09 10:45 | 2015-08-19 10:43 | 2015-10-15 10:32 | -21 | In target
LOWER, UPPER AND CLARENDON WALK, - 2015.07.08 | 2015-08-19 10:48 | S217012770017 | CLARENDON WALK 1-24 | 212633 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes and are done via hand helds | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-08-19 10:48 | 2015-09-09 10:49 | 2015-08-19 10:48 | 2015-10-15 10:38 | -21 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 14:49 | S217010570003 | LOWERWOOD COURT | 133673 | Completed | 8c | Low | Communal Area Storage | There are old plant pots etc in the electrical cupboard on the 5th floor level. | I would recommend that all the items are removed from this electrical cupboard. | Neighbourhood Management | Martin Barr |  | All itmes have been removed from the cupboard. ESA removed them and sent photos as confirmation. | 2014-04-22 | Fully Completed | Martin Barr | 2014-03-07 14:49 | 2014-09-03 14:50 | 2014-03-07 14:49 | 2014-04-23 14:44 | -180 | In target
LOWERWOOD COURT - 2014.02.06 | 2014-03-07 15:05 | S217010570003 | LOWERWOOD COURT | 133688 | Completed | 23 | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire extinguishers, dry riser, external staircase, lifts and emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment, lifts etc and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Training on lighting testing due 23rd April. Checks will take place after this and once list of locations provided by A&R team. Block checks are completed and records kept. | 2014-04-17 | Fully Completed | Martin Barr | 2014-03-07 15:05 | 2014-03-28 15:06 | 2014-03-07 15:05 | 2014-04-22 09:04 | -21 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:03 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205665 | Completed | 8 | Low | Storage | During the risk assessment access could not be gained to the three 1st floor level staircase landing store rooms , one off each of the staircases. The caretaker does not appear to have keys for these areas. It is not known what is in these store rooms, but they are suitably fire separated from the staircase landings. | Can it please be confirmed that these are private residents storage areas, if they are, no action is needed on this issue. If they are not I would recommend that keys are obtained to the locks of these doors to check what is in these areas. | Neighbourhood Management | Martin Barr |  | 1 room is used privately by a resident for storage. One is currently empty and the other contains the PAC fob reader equipment. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-09 09:03 | 2016-01-05 09:06 | 2015-07-09 09:03 | 2015-10-16 11:20 | -180 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 09:58 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205691 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting systems in this building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting systems in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 09:58 | 2015-07-30 10:00 | 2015-07-09 09:58 | 2015-09-18 17:59 | -21 | In target
MANCHESTER DRIVE - 2015.06.29 | 2015-07-09 10:00 | Z217009380001 | MANCHESTER DRIVE (1-82) | 205695 | Completed | 23d | High | Inspection Regime | Is the caretaker undertaking the occupier's tests, checks and inspections of this building as per the caretakers check list? | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 10:00 | 2015-07-30 10:01 | 2015-07-09 10:00 | 2015-09-18 17:59 | -21 | In target
MANNING HOUSE - 2015.06.03 | 2015-06-12 08:31 | S217008490001 | MANNING HOUSE | 201211 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-12 08:31 | 2015-07-03 08:32 | 2015-06-12 08:31 | 2015-09-21 08:51 | -21 | In target
MANNING HOUSE - 2015.06.03 | 2015-06-12 08:33 | S217008490001 | MANNING HOUSE | 201212 | Completed | 23c | High | Inspection Regime | Is the caretaker undertaking the occupiers tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-12 08:33 | 2015-07-03 08:34 | 2015-06-12 08:33 | 2015-09-21 08:50 | -21 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 15:14 | S217008560002 | MARKLAND HOUSE | 244930 | Active | 8a | High | Hose Reels | The ground floor level water pump room is being used to store green metal shelving and racking. | I would recommend that all storage is removed from this water pump room as this area is not big enough to be used as a storage area. | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | Os the ESA has spoken to Steve the manager of Energie who hsa said the items in here belong to him. Os has agreed to give him a week to remove the items otherwise they will be stickered and removed by the TMO. | 2016-03-14 | Partially Completed | Louise Nezandonyi | 2016-02-22 15:14 | 2016-03-14 15:16 | 2016-02-22 15:14 | 2016-03-15 09:23 | -21 | In target | 2016-02-22 15:14 | 2016-03-21 11:33 | Janice Wray
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 15:18 | S217008560002 | MARKLAND HOUSE | 244934 | Completed | 8b | Medium | Communal Area Storage | At the head of the steps up to the roof area, at the roof level there is a pile of empty sandwiches packs, drinks bottles and food wrappers. | This rubbish should be removed from this area. | Neighbourhood Management | Louise Nezandonyi | 2016-05-16 | Os has removed these items and I have seen proof of this, he believesthe items may have been left by the lift contractors and I have agreed to speak with Maria Ares about this. | 2016-03-14 | Fully Completed | Louise Nezandonyi | 2016-02-22 15:18 | 2016-04-22 16:41 | 2016-02-22 15:18 | 2016-03-15 10:01 | -60 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 16:51 | S217008560002 | MARKLAND HOUSE | 244989 | Completed | 12f | High | Miscellaneous | There are cold smoke seals fitted to the self closing fire doors off the flat/lift lobby areas to the refuse chute balcony and on to the lobby area before the staircase and on to the staircase. Some of these cold smoke seals are damaged or there are pieces missing. | As the TMO have fitted fire doors with cold smoke seals to these areas they must be maintained to the standard as when the doors were installed. All missing and damaged cold smoke seals should be replaced. Oswaldo has agreed to include in his inspections | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | Os has agreed to include thse in his inspections and he will report the missing ones and the damaged ones. Once he has done this he will let me know all the ones he has reported. Ongoing & inhand | 2016-03-14 | Fully Completed | Louise Nezandonyi | 2016-02-22 16:51 | 2016-03-14 16:53 | 2016-02-22 16:51 | 2016-03-15 11:35 | -21 | In target | 2016-02-22 16:51 | 2016-03-21 11:34 | Janice Wray
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-22 16:55 | S217008560002 | MARKLAND HOUSE | 244992 | Completed | 114a | High | Inspection Regime | The metal cover plate on the 7th floor level is only fixed to the wall by 2 screws, 8 screw holes are empty. Somebody has removed this metal cover plate and not secured it back again fully. This is a heave piece of sheet metal and might also fall off the wall and cause a serious injury if it were to hit a person. | This metal cover plate should be re-fixed securely back to the wall. Oswaldo agreed to investigate & raise repair if required | Neighbourhood Management | Louise Nezandonyi | 2016-03-21 | On 15/03/2016 Os has confrimed that on this day he has checked all floors in the whole block and reported this cover plates and others to the repoairs team. | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-22 16:55 | 2016-03-14 16:56 | 2016-02-22 16:55 | 2016-03-17 14:15 | -21 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 08:43 | S217008560002 | MARKLAND HOUSE | 245018 | Completed | 14c | High | Miscellaneous | A piece of fire rated glazing in the staircase screen next to the staircase door on the 1st floor level has been replaced. This piece of glazing has been fitted very badly, with the work not in accordance with the fitting of fire rated glazing in a metal frame. | I would recommend that a new piece of Georgian wired fire rated glass is refitted into this fire rated screen. This piece of glazing should be puttied in correctly. Could Oswaldo please investigate | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | This has been checked and could not be found if the fire risk assessor could show which glazing he means? | 2016-03-16 | Fully Completed | Louise Nezandonyi | 2016-02-23 08:43 | 2016-03-15 08:45 | 2016-02-23 08:43 | 2016-03-17 14:17 | -21 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 09:01 | S217008560002 | MARKLAND HOUSE | 245026 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units, fire extinguishers and sprinkler system in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting and sprinkler systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | The monthly occupier testing and inspections are undertaken and the results are recorded as proof on insight once the ESA has put the information through his total mobile device. | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-23 09:01 | 2016-03-15 09:02 | 2016-02-23 09:01 | 2016-03-10 12:27 | -21 | In target
MARKLAND HOUSE, 28 DARFIELD WAY, LONDON W10 6UA - 2016.01.21 | 2016-02-23 09:59 | S217008560002 | MARKLAND HOUSE | 245063 | Completed | 23f | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-03-22 | I can confirm that the caretaker is undertaking the monthly occupier checks and completed sheets are kept as proof of testing. | 2016-03-09 | Fully Completed | Louise Nezandonyi | 2016-02-23 09:59 | 2016-03-15 10:00 | 2016-02-23 09:59 | 2016-03-10 12:36 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:10 | S217010050008 | MARLEY HOUSE | 143634 | Completed | 8 | High | Communal Area Storage | There are two large Butane gas cylinders, as used on gas powered BBQs in the central area of the residents storage area. These are high fire risk items and a fire hazard, I believe that the storage of gas cylinders is not allowed under the tenancy agreement. | I would recommend that these gas cylinder are removed from this storage area immediately. | Neighbourhood Management | Chris Baker | 2014-06-04 | Items confirmed as removed. | 2014-06-03 | Fully Completed | Chris Baker | 2014-05-14 10:10 | 2014-06-04 10:12 | 2014-05-14 10:10 | 2014-06-05 16:12 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:35 | S217010050008 | MARLEY HOUSE | 143649 | Completed | 17 | High | Fire Alarm |  | This area is not manned on a permanent basis there are only employees in this area of the building for part of the day. There are no employees in this area on a permanent basis. I would therefore recommend that the fire alarm system in this area of the building is connected to a monitoring station/service so in the event of an activation of the fire alarm system the fire service or an on duty caretaker is informed. Could this be linked to CAS? Janice/Kevin to visit site to see if its is possible to link exisiting fire system to CAS - hc. | Neighbourhood Management | Hash Chamchoun | 2014-06-30 | Janice/Kevin to visit site to establish is exisiting Fire System can be linked to CAS. Fire alarm not linked. Risk not concsidered significant at present | 2014-09-05 | Fully Completed | Hash Chamchoun | 2014-05-14 10:35 | 2014-06-04 10:36 | 2014-05-14 10:35 | 2014-09-10 10:38 | -21 | In target | 2014-05-14 10:35 | 2014-06-17 15:35 | Janice Wray
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:37 | S217010050008 | MARLEY HOUSE | 143651 | Completed | 19 | High | Miscellaneous | The dry rising main inlet valve for this building is obscured and covered over by shrubs etc and the fire service would find it hard the access this dry riser inlet. | I would recommend that all of the shrubs and plants obscuring the dry rising main inlet valve are cut away and that regular checks are made so that this inlet valve remains visible at all times. Landscape - Dominic / Chris | Neighbourhood Management | Dominic Davies |  |  | 2014-10-24 | Fully Completed | Dominic Davies | 2014-05-14 10:37 | 2014-06-04 10:39 | 2014-05-14 10:37 | 2014-10-27 12:48 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:41 | S217010050008 | MARLEY HOUSE | 143656 | Completed | 23c | High | Inspection Regime | Are the weekly occupier's tests of the fire alarm and warning system installed in the cleaners/caretakers area being undertaken? | Weekly occupier tests and inspections of the fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Martin Barr |  | We've been advised that ESAs are not to test the fire alarms at present. |  | Fully Completed | Martin Barr | 2014-05-14 10:41 | 2014-06-04 10:42 | 2014-05-14 10:41 | 2014-09-01 12:32 | -21 | In target
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:43 | S217010050008 | MARLEY HOUSE | 143657 | Completed | 23d | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-09-05 | Fully Completed | Martin Barr | 2014-05-14 10:43 | 2014-06-04 10:44 | 2014-05-14 10:43 | 2014-09-10 10:36 | -21 | In target | 2014-05-14 10:43 | 2014-09-16 10:35 | Janice Wray
MARLEY HOUSE - 2014.4.22 | 2014-05-14 10:49 | S217010050008 | MARLEY HOUSE | 143660 | Completed | 23f | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-09-05 | Fully Completed | Martin Barr | 2014-05-14 10:49 | 2014-06-04 10:52 | 2014-05-14 10:49 | 2014-09-10 10:34 | -21 | In target | 2014-05-14 10:49 | 2014-09-16 10:32 | Janice Wray
MATTHEW CLOSE, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 10:17 | S217009400001 | MATTHEW CLOSE (1-28) | 225097 | Completed | 3 | Medium | Miscellaneous | The fire fighter entry over ride devices fitted to the staircase entrance doors of flats 2 and 4, also to flats 14 and 16 did not function and release the locking device fitted to the staircase doors. These over ride devices allow the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride devices fitted to the two staircase entrance doors should be repaired or replaced so that they releases the locking device fitted to the doors. | Neighbourhood Management | Louise Nezandonyi |  | The ESA has reported this to our repairs team and the job refernce number is 201542820, for the two fire fighter entry over ride devices fitted to the two staircase entrance doors. | 2015-11-27 | Fully Completed | Louise Nezandonyi | 2015-11-02 10:17 | 2016-01-01 10:19 | 2015-11-02 10:17 | 2015-11-30 16:10 | -60 | In target
MATTHEW CLOSE, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 10:19 | S217009400001 | MATTHEW CLOSE (1-28) | 225098 | Completed | 8 | High | Communal Area Storage | Residents are storing combustible items outside their flats entrance doors, on the staircase landings. Outside flats 6 and 8 all of the household items and furniture should be removed. | I would recommend that the residents are asked to remove the combustible items outside their flat entrance doors on the staircase landings. The residents should be reminder that the staircase enclosures should be maintained free of all items. | Neighbourhood Management | Louise Nezandonyi | 2016-02-08 | The ESA has confirmed that all items have been removed | 2016-02-08 | Fully Completed | Louise Nezandonyi | 2015-11-02 10:19 | 2015-11-23 10:20 | 2015-11-02 10:19 | 2016-02-09 13:55 | -21 | In target | 2015-11-02 10:19 | 2015-12-06 15:26 | Louise Nezandonyi
MORLAND HOUSE- 2015.06.22 | 2015-06-29 12:05 | S217009210003 | MORLAND HOUSE | 203804 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Siobhan Rumble |  | yes always done | 2015-07-13 | Fully Completed | Siobhan Rumble | 2015-06-29 12:05 | 2015-07-20 12:07 | 2015-06-29 12:05 | 2015-07-14 16:16 | -21 | In target
MORLAND HOUSE- 2015.06.22 | 2015-06-29 12:08 | S217009210003 | MORLAND HOUSE | 203805 | Completed | 23d | High | Inspection Regime | Is the caretaker undertaking the occupier's tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes | 2015-07-13 | Fully Completed | Siobhan Rumble | 2015-06-29 12:08 | 2015-07-20 12:10 | 2015-06-29 12:08 | 2015-07-14 16:17 | -21 | In target
MULBERRY CLOSE, BEAUFORT STREET, LONDON SW3 5AB - 2016.05.03 | 2016-05-23 16:42 | S217000310006 | MULBERRY CLOSE | 262051 | Completed | 12e | High | Miscellaneous | There is a cabin hook attached to each of the fire rated corridor sub division doors at each floor level of this building, so that the door can be held in the open position. | These cabin hooks should be removed immediately from each of these doors, so that the doors cannot be left in the open position. These corridor sub division doors should be in the closed position unless somebody is passing through the door. Nicola - can Jimmy remove these? | Neighbourhood Management | Nicola Rees | 2016-06-13 | This has been removed 31.05.16 | 2016-05-31 | Fully Completed | Nicola Rees | 2016-05-23 16:42 | 2016-06-13 16:43 | 2016-05-23 16:42 | 2016-06-03 11:02 | -21 | In target
MULBERRY CLOSE, BEAUFORT STREET, LONDON SW3 5AB - 2016.05.03 | 2016-05-23 16:59 | S217000310006 | MULBERRY CLOSE | 262065 | Completed | 18b | Medium | Fire Extinguisher | There was portable fire fighting equipment provided in the common parts of this building, this has now been removed but all of the supporting brackets for the fire extinguishers and the signs are still in place. | The supporting brackets for the fire extinguishers which have been removed and the signs which were displayed above the fire extinguishers should all be removed. Nicola - would Jimmy be able to undertake this work please? | Neighbourhood Management | Nicola Rees | 2016-08-26 | This has been completed 31.05.16 | 2016-05-31 | Fully Completed | Nicola Rees | 2016-05-23 16:59 | 2016-07-22 17:00 | 2016-05-23 16:59 | 2016-06-03 11:03 | -60 | In target
MULBERRY CLOSE, BEAUFORT STREET, LONDON SW3 5AB - 2016.05.03 | 2016-05-23 17:04 | S217000310006 | MULBERRY CLOSE | 262070 | Completed | 23b | High | Inspection Regime | It appears that caretaker inspections are not being undertaken in this building as the fire extinguishers are out of service/test date and the lift motor room extinguisher has "Condemned" written on it. . | Can it please be confirmed that the caretakers inspections and checks of this building are being undertaken in accordance with the caretakers check list? If they are not then caretakers inspections and checks should be undertaken, with the visits recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-06-13 | The monthly inspections are being carried out as are the weekly inspections at this block. | 2016-05-31 | Fully Completed | Nicola Rees | 2016-05-23 17:04 | 2016-06-13 17:05 | 2016-05-23 17:04 | 2016-06-03 11:05 | -21 | In target
NICKLEBY HOUSE - 2014.7.22 | 2014-08-04 13:07 | S217010050001 | NICKLEBY HOUSE | 155840 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Yes, checks of the emergency lighting are undertaken where we are aware of them. A&R still to provide lists of sites and locations. Records of checks will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-04 13:07 | 2014-08-25 13:08 | 2014-08-04 13:07 | 2014-09-01 16:21 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 15:41 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151230 | Completed | 1a | High | Electrical Wire Check | There is no electrical portable appliance testing (PAT) label on the vacuum cleaner stored in the office and 1 of the microwave ovens, these are Nursery items. All of the other electrical items in this building which belong to the building have in date labels on them | I would recommend that the Nursery are asked to confirm that all of their portable electrical items are PAT. The vacuum cleaner and the microwave should be PAT immediately by a suitably qualified person and a test label attached to each item and any others if they pass the test. Siobhan Rumble to bring to attention of Nursery & ask them to address asap | Neighbourhood Management | Siobhan Rumble |  | the PAT teste was carried out yesterday 14th August 2014 and included all you have listed. | 2014-08-14 | Fully Completed | Siobhan Rumble | 2014-07-01 15:41 | 2014-07-22 15:44 | 2014-07-01 15:41 | 2014-08-18 12:17 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 15:52 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151236 | Completed | 21 | High | Miscellaneous | Grenfell Nursery are currently using this building, have the nursery staff been shown how to undertake the occupiers tests inspections and are fire drills etc being undertaken by the nursery? . | Can it please be confirmed that the Grenfell Nursery are undertaking all of the occupier tests, inspections and fire drills etc as required (specifically testing the fire alarm on a weekly basis & keeping a record & carrying out 6-monthly fire drills) Could you seek confirmation from the Nursery that they are doing these fire alarm tests & fire drills | Neighbourhood Management | Siobhan Rumble | 2014-12-10 | The nursery are closed until the end of summer, when they return i will speak to them and confirm that these are taking place The nursery has now left these premises and relocated back to their permanent location at Grenfell Tower. This resource centre is now under control of Sharon Baah, Community Centre Officer, who will undertake weekly fire alarm testing and maintain a record of these. | 2016-06-07 | Fully Completed | Siobhan Rumble | 2014-07-01 15:52 | 2014-07-22 15:53 | 2014-07-01 15:52 | 2016-06-13 08:13 | -21 | In target | 2014-07-01 15:52 | 2015-06-24 19:27 | Janice Wray
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:13 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151245 | Completed | 23b | High | Fire Alarm | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Can it be confirmed that the weekly occupiers testing of the installed fire alarm system is being undertaken? If it is being tested are records of any testing being kept as proof of testing, if testing is not being undertaken then weekly testing should start and records of this testing kept as proof of testing. Siobhan Rumble Could you seek confirmation from the Nursery that they are doing these fire alarm tests & fire drills | Neighbourhood Management | Siobhan Rumble | 2014-12-15 | as you will be aware we have just moved to new offices, i or any of my colleagues have not been shown if we have a fire alarm or where it is. i would appreciate someone coming to show us then we can carry out weekly checks as we did at Grenfell Tower | 2014-08-14 | Fully Completed | Siobhan Rumble | 2014-07-01 16:13 | 2014-07-22 16:16 | 2014-07-01 16:13 | 2014-12-16 14:46 | -21 | In target | 2014-07-01 16:13 | 2014-08-22 13:30 | Siobhan Rumble
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:17 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151249 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. Siobhan - As per our discussion - could Rob confirm he is doing the monthly tests on these lights please - Janice | Neighbourhood Management | Siobhan Rumble |  | This is done weekly with a fish key and recorded on the weekly inspection sheets | 2014-08-14 | Fully Completed | Siobhan Rumble | 2014-07-01 16:17 | 2014-07-22 16:19 | 2014-07-01 16:17 | 2014-08-15 11:51 | -21 | In target
NORTH KENSINGTON RESOURCE CENTRE - 2014.6.2 | 2014-07-01 16:21 | U217012770720 | TMO CLUBROOM NTH KEN TEN RESOURCE CENTRE | 151251 | Completed | 23f | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. Siobhan - Will Rob / Paul be doing monthly visual inspections of this area ? - Janice | Neighbourhood Management | Siobhan Rumble |  | RGE used to do the testing of the fire extinguishers and labelling them, i am guessing the new electrical contractor now does this? our estate supers will do a visual check of the labels quarterly. if there is a policy on this could we please have a copy? | 2014-08-13 | Fully Completed | Siobhan Rumble | 2014-07-01 16:21 | 2014-07-22 16:22 | 2014-07-01 16:21 | 2014-08-15 11:56 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:27 | S217008370001 | NOTTINGWOOD HOUSE | 108463 | Completed | No Item Number | Information Only | Miscellaneous | Some residents of this building have erected gates at the entrance of the open balcony to their flat, the open balcony areas cannot be accessed and are now under the control of the resident. | Can it be confirmed that the TMO are happy that some residents have restricted access to the open balcony areas outside their flat entrance door and that these areas are no demised to the flat occupant and that the resident has control over this balcony area? | Neighbourhood Management | Steve Rowe | 2014-03-03 | Steve this is for our information only. He is suggesting that we establish whether we have given these people permission to erect these gates but doen't appear to be raising any specific concerns | 2013-11-08 | Fully Completed |  |  |  | 2013-10-01 13:27 | 2013-11-11 16:57
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:38 | S217008370001 | NOTTINGWOOD HOUSE | 108468 | Completed | No Item Number | Information Only | Storage | In the basement area under staircase 5 these is a gym area and what appears to be a push bike repair area. . | Can it be confirmed that the TMO are aware that this basement area is being used as a fitness area come gym with weights and other fitness equipment. Also there are a lot of push bikes and what appears to be tools and equipment to repair/mend push bikes. There is minimal ventilation in this basement area and restricted access. | Neighbourhood Management | Chris Baker | 2013-10-15 | Gym equipment has been removed and disposed of. Bikes and other items have been taken out, and operatives advised not to use this area in future. | 2013-10-02 | Fully Completed |  |  |  | 2013-10-01 13:38 | 2013-10-03 14:02
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:42 | S217008370001 | NOTTINGWOOD HOUSE | 108469 | Completed | 1b | High | Wiring Inspection | In the basement area there are portable electrical appliances which do not have any portable appliance testing labels attached to them. | All the portable electrical appliances in the basement area should be portable appliance tested immediately by a suitably qualified person and new test labels attached to each item if it passes the test. I would recommend that an asset register of all the items is started and maintained and test records are kept. | Neighbourhood Management | Chris Baker | 2013-10-22 | All eletrical appliances have been removed. Staff advised that any electrical applicances will need PAT testing before being used, and that the contractor will need to keep suitable records of such items. | 2013-10-01 | Fully Completed | Chris Baker | 2013-10-01 13:42 | 2013-10-22 13:44 | 2013-10-01 13:42 | 2013-10-03 14:03 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:44 | S217008370001 | NOTTINGWOOD HOUSE | 108470 | Completed | 1c | High | Wiring Inspection | In the basement area an electrical cooker has been wired in using what appears to be a normal extension lead and trailing leads and multi plugs are also being used in this area. | I would recommend that an electrician is asked to check all the electrical wiring etc in this area as soon as possible and any non compliant wiring is replaced etc. | Neighbourhood Management | Chris Baker | 2013-10-22 | Electric Cooker has been removed and disposed of. Multi plugs have all been removed. | 2013-10-01 | Fully Completed | Chris Baker | 2013-10-01 13:44 | 2013-10-22 13:48 | 2013-10-01 13:44 | 2013-10-03 14:03 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:49 | S217008370001 | NOTTINGWOOD HOUSE | 108473 | Completed | 2 | Medium | Signage | The "No Smoking" signs in the entrance lobby areas of staircases 1 and 7 were damaged or defaced. | I would recommend that new "No Smoking" signs are displayed in these 2 staircase entrance lobby areas. | Neighbourhood Management | Martin Barr | 2013-11-04 | Damaged and missing signs have been replaced. |  | Fully Completed | Martin Barr | 2013-10-01 13:49 | 2013-11-30 13:50 | 2013-10-01 13:49 | 2013-11-12 10:16 | -60 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 13:51 | S217008370001 | NOTTINGWOOD HOUSE | 108474 | Completed | 6 | High | Miscellaneous | The cooking area in the basement does not appear to comply with the environmental health requirements, there are no work surfaces, and sinks and running water etc also appear to be lacking. | I would recommend that the cooking area in the basement is checked out to see that it conforms to the requirements needed for health and safety and environmental health, including cleanliness and ventilation. | Neighbourhood Management | Chris Baker | 2013-10-22 | Cooking equipment has been removed. | 2013-10-01 | Fully Completed | Chris Baker | 2013-10-01 13:51 | 2013-10-22 16:03 | 2013-10-01 13:51 | 2013-10-03 14:02 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 16:03 | S217008370001 | NOTTINGWOOD HOUSE | 108557 | Completed | 8a | High | Communal Area Storage | It appears that residents are using the staircase and landing areas from the 4th floor level up to the roof level of staircases 3, 4 and 5 as private storage areas. | I would recommend that these staircase areas are completely cleared of all private storage and the gates secured to stop unauthorised access to these areas which access the open roof. | Neighbourhood Management | Martin Barr | 2013-10-22 | Order 201511257 was raised for DMC to fit new gerda locks to gets preventing access | 2015-10-30 | Fully Completed | Martin Barr | 2013-10-01 16:03 | 2013-10-22 16:05 | 2013-10-01 16:03 | 2015-11-02 10:26 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-01 16:05 | S217008370001 | NOTTINGWOOD HOUSE | 108558 | Completed | 8b | High | Communal Area Storage | On the open external roof area above flat 30 there are 2 chairs and some empty bottles etc, it appears that residents are accessing the open external roof area. The metal TV cable box on the roof is damaged. | I would recommend that these chairs are removed from the roof and that the gate which allows access to the roof is secured to stop unauthorised access to the open external roof. | Neighbourhood Management | Martin Barr | 2013-10-22 | Items on the roof have been removed. The gate has been secured. The TV equipment belongs to Virgin media and we will not repair it. | 2015-06-03 | Fully Completed | Martin Barr | 2013-10-01 16:05 | 2013-10-22 16:23 | 2013-10-01 16:05 | 2015-06-04 13:50 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-03 14:57 | S217008370001 | NOTTINGWOOD HOUSE | 108947 | Completed | 8c | High | Storage | On the external balcony outside flats numbers 24, 79 and 84, there are charcoal fuelled BBQs, it is not known if the occupant's use these BBQs on the balcony's, but this is a high fire risk item and a fire hazard. I believe that cooking on a BBQ on a flat balcony is not allowed under the tenancy agreement. | I would recommend that the charcoal BBQs are removed from the balcony areas outside these flats immediately. | Neighbourhood Management | Steve Rowe | 2013-10-25 | A - Request for caretaker to take a photo of the area (by Steve Row c 08.11.13?) B - Letter sent to Flats 24, 79, 84 and ESA asked to return. (action taken by Tim Huntley 29.04.14) | 2014-04-29 | Fully Completed | Mandy Warrier | 2013-10-03 14:57 | 2013-10-24 15:54 | 2013-10-03 14:57 | 2014-04-30 11:17 | -21 | In target | 2013-10-03 14:57 | 2014-03-28 12:44 | Tim Huntley
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-03 15:55 | S217008370001 | NOTTINGWOOD HOUSE | 108962 | Completed | 8d | High | Communal Area Storage | In the bin room of staircase 3 there is a very large oil drum which is used as a charcoal BBQs, it is not known who this belongs too or where it is used. | I would recommend that this oil drum is removed from this bin room. | Neighbourhood Management | Martin Barr |  | Oil drum has been removed. |  | Fully Completed | Martin Barr | 2013-10-03 15:55 | 2013-10-24 15:56 | 2013-10-03 15:55 | 2013-11-12 10:17 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-03 15:57 | S217008370001 | NOTTINGWOOD HOUSE | 108964 | Completed | 8e | High | Communal Area Storage | Outside flat 18 on the external balcony the occupant has used some old wood as shelves, these are tied to the metal bars over the windows with string. | I would recommend that these shelves are removed along with all the items on them. | Neighbourhood Management | Martin Barr | 2013-10-25 | Resident has removed items as requested | 2015-06-03 | Fully Completed | Martin Barr | 2013-10-03 15:57 | 2013-10-24 15:58 | 2013-10-03 15:57 | 2015-06-04 13:52 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-03 15:59 | S217008370001 | NOTTINGWOOD HOUSE | 108965 | Completed | 8f | High |  | There was waste and household items next to the refuse chute openings on the 4th floor level of staircase 1, 3rd floor level of staircase 2, on the 2nd floor level of staircase 4 and tins of old paint and timber off cuts on the 3rd floor level of staircase 7. | These items by the refuse chutes should be removed and I would recommend that residents are reminded that items should not be left on these balcony areas by the refuse chute openings. | Neighbourhood Management | Martin Barr | 2013-10-25 | Each landing on these staircases has been cleared, none of the items were present on inspection 11/11/2013 |  | Fully Completed | Martin Barr | 2013-10-03 15:59 | 2013-10-24 16:00 | 2013-10-03 15:59 | 2013-11-12 10:18 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-03 16:00 | S217008370001 | NOTTINGWOOD HOUSE | 108966 | Completed | 8g | High |  | In the entrance lobby area of staircase 9 there is an old bed, a wardrobe and a bedside table. | These items should be removed from the lobby area. | Neighbourhood Management | Martin Barr | 2013-10-25 | Items have all been removed from 9th floor staircase lobby. |  | Fully Completed | Martin Barr | 2013-10-03 16:00 | 2013-10-24 16:01 | 2013-10-03 16:00 | 2013-11-12 10:18 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-07 14:03 | S217008370001 | NOTTINGWOOD HOUSE | 109365 | Completed | 8h | High | Communal Area Storage | The basement area could do with a good tidy up and all the old damaged items stored there removed. This includes all the old bikes and the cardboard boxes etc. | I would recommend that the basement area is tided up and all unwanted old and damaged items are removed from this area. If one part is to be used as a cleaners store and rest area the amount of materials should be kept to a minimum as should any chairs and other items. This is because there is no fire separation in this basement area and there is only the one entrance/exit route. The rear exit is sealed off by chains securing the gate at the ground floor level. If this area is to be used as a full rest room type area then the basement level must be comply with all the requirements of the Building Regulations and Environmental Health standards. | Neighbourhood Management | Chris Baker | 2013-10-28 | Superfluous items removed. Area cleaned, and cleaners store tidied. Items from caged storage area disposed of. | 2013-10-02 | Fully Completed | Chris Baker | 2013-10-07 14:03 | 2013-10-28 14:05 | 2013-10-07 14:03 | 2013-10-08 14:16 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-07 14:06 | S217008370001 | NOTTINGWOOD HOUSE | 109366 | Completed | 8i | High | Communal Area Storage | In the children's play area there are two old fridge freezers, young children could be trapped in these. There are also other disused household appliances in this area, a washing machine and a microwave. | I would recommend that the old fridge freezers are removed immediately from this central children's play area along with any other old discarded household appliances. | Neighbourhood Management | Martin Barr | 2013-10-28 | These items have been removed from the children's play area. |  | Fully Completed | Martin Barr | 2013-10-07 14:06 | 2013-10-28 14:13 | 2013-10-07 14:06 | 2013-11-12 10:19 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 15:51 | S217008370001 | NOTTINGWOOD HOUSE | 109623 | Completed | 8j | Medium | Communal Area Storage | Just inside the gates to the central area there are old beds, mattresses, bedroom furniture and a settee. These combustible items could provide fuel for a fire. | I would recommend that all the old discarded furniture and beds etc is removed from this area, so that these items are not used as a fuel source for a fire. | Neighbourhood Management | Martin Barr | 2013-11-12 | These items have been removed. Bulk refuse picked up from the estate gets placed here before arranging collection from one location, so there will be items here sporadically prior to collection. |  | Fully Completed | Martin Barr | 2013-10-08 15:51 | 2013-12-07 15:54 | 2013-10-08 15:51 | 2013-11-12 10:20 | -60 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 15:55 | S217008370001 | NOTTINGWOOD HOUSE | 109628 | Completed | 8k | Information Only | Communal Area Storage | There are sheets of shuttering plywood being stored on the roof level area at the top of staircase 7. | Does this shuttering belong to the TMO or has it been left by contractors? It is in a secure area so can remain here if required. | Neighbourhood Management | Martin Barr |  | Cannot establish if they were left by a contractor or not. They can remain in situ as the area is secure so will leave them for now. |  | Fully Completed |  |  |  | 2013-10-08 15:55 | 2013-11-12 12:50
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 15:57 | S217008370001 | NOTTINGWOOD HOUSE | 109631 | Completed | 12e | High | Communal Area Storage | There are some pots of plants on the steps of staircase 3, these could cause a trip hazard and they are reducing the width of the staircase. | All the pots of plants on the steps of the staircase should be removed immediately so they are not a trip hazard or reduce the width of the means of escape route. | Neighbourhood Management | Martin Barr | 2013-10-29 | Most pots have been removed and remaining plants are not an obstruction | 2015-06-03 | Fully Completed | Martin Barr | 2013-10-08 15:57 | 2013-10-29 15:59 | 2013-10-08 15:57 | 2015-06-04 13:52 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 16:00 | S217008370001 | NOTTINGWOOD HOUSE | 109638 | Completed | 12f | Medium | Communal Area Storage | There are a lot of pots of plants on the balconies by flats 71 and 91 also piles of old plastic plant pots outside flat 71. | I would recommend that some of these pots of plants are removed from these balcony areas, they are reduce the width of the balcony considerably. A few pots of plants etc are I believe acceptable against the wall but not too many. | Neighbourhood Management | Martin Barr |  | There were no plant pots on either balcony that would cause an obstruction. Flat 91 had no plants at all, and those on the balcony of flat 71 were beyond the front door and not on an exit route. No other doors are beyond the plants. |  | Fully Completed | Martin Barr | 2013-10-08 16:00 | 2013-12-07 16:04 | 2013-10-08 16:00 | 2014-01-03 15:50 | -60 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 16:19 | S217008370001 | NOTTINGWOOD HOUSE | 109653 | Completed | 23b | High | Inspection Regime | It appears that the monthly occupier's inspections as per the caretaker's checklist are not being undertaken in this building with records kept? This is because all of the fire extinguishers are years passed there servicing date. | Monthly occupier's inspections as per the caretaker's checklist should be undertaken, with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Martin Barr | 2013-10-29 | ESAs complete paper records which are kept and can be checked if required. Project underway to replace these with handheld devices to record checks electronically. We may need to reconsider fire extinguisher checks being on the checklists. We have a contractor paid to carry out these tests and yet the ESAs are picked up on failures to check them. We do not have a list of sites where extuinguishers need to be checked and in Nottingwood House the only place I could find them was in the small intake cupboards. |  | Fully Completed | Martin Barr | 2013-10-08 16:19 | 2013-10-29 16:20 | 2013-10-08 16:19 | 2013-11-12 13:11 | -21 | In target
NOTTINGWOOD HOUSE - 2013.09.01 | 2013-10-08 16:23 | S217008370001 | NOTTINGWOOD HOUSE | 109656 | Completed | 12a | High | Miscellaneous | The gates that have been erected on the open balconies by flats 28 and 37 are badly damaged or are damaging the brickwork. | I would recommend that both of these gates are repaired or removed completely so that the brickwork is not damaged further or the damaged gate becomes a hazard. | Neighbourhood Management | Steve Rowe | 2013-11-14 | A) Request for caretaker to take a photo of the area 20/11/13 - gates checked tenant responsiblity - Letter to tenant to remove [Steve Rowe action dated 08.11.13] B) ESA asked to review situation at 28 & 37 and follow up letters to be sent. Flat 28 is leaseholder so that letter to come from HOO. Tim Huntley 29.04.14. | 2013-11-08 | Fully Completed | Mandy Warrier | 2013-10-08 16:23 | 2013-10-29 16:24 | 2013-10-08 16:23 | 2014-04-30 11:54 | -21 | In target | 2013-10-08 16:23 | 2014-03-28 12:47 | Tim Huntley
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:38 | S217010030001 | OCTAVIA HOUSE | 205858 | Completed | 8a | High | Storage | The cleaners are storing their cleaning materials etc on the steps going down to the basement area next to flat 24. | I would recommend that the cleaners stop storing their cleaning materials etc on the steps going down to the basement area next to flat 24. All items should be in the basement area with the basement door shut. | Neighbourhood Management | Martin Barr |  | Cleaners have been instructed to remove items from steps and reduce amount of materials stored | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-09 14:38 | 2015-07-30 14:40 | 2015-07-09 14:38 | 2015-10-16 11:23 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:40 | S217010030001 | OCTAVIA HOUSE | 205862 | Completed | 8b | High | Communal Area Storage | There is a tumble dryer in the ground floor level entrance hall area by flat 14. | The tumble dryer should be removed from this ground floor level entrance hall area. | Neighbourhood Management | Martin Barr |  | Item was removed | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-09 14:40 | 2015-07-30 14:41 | 2015-07-09 14:40 | 2015-10-16 11:24 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:42 | S217010030001 | OCTAVIA HOUSE | 205864 | Completed | 8c | Information Only | Communal Area Storage | At the roof level above flats 21 and 22 there are a lot of decoration materials being stored. | Are the TMO aware of this storage? When will this storage be removed? | Neighbourhood Management | Martin Barr |  | These have been left by the cyclical works contractors after FWA ceased trading. A&R are aware of this and are getting a new contractor to finish works off. | 2015-10-01 | Fully Completed |  |  |  | 2015-07-09 14:42 | 2015-10-16 11:28
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:50 | S217010030001 | OCTAVIA HOUSE | 205870 | Completed | 12e | High | Miscellaneous | Both of the doors from the basement areas are not shut, these fire doors should be kept shut at all times so that the basement area is separated from the rest of the building. | If the cleaners cannot keep these doors shut, then I would recommend that self closing devises are fitted to these doors so that they are closed automatically. | Neighbourhood Management | Martin Barr |  | These doors have been closed and cleaners instructed to remain closed. | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-09 14:50 | 2015-07-30 14:52 | 2015-07-09 14:50 | 2015-10-16 11:30 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 14:58 | S217010030001 | OCTAVIA HOUSE | 205876 | Completed | 12f | High | Communal Area Storage | There are some pots of plants on the staircase landing of flats 29 to 31, these pots of plants are in front of the refuse chute opening. | I would recommend that the pots of plants are removed from this area. | Neighbourhood Management | Martin Barr |  | Called [redacted] resident of [redacted] she has agreed to speak to her neighbours adn have the plants moved out of the way so that they are no longer blocking the refuse area and the staircase landing. | 2015-12-10 | Fully Completed | Louise Nezandonyi | 2015-07-09 14:58 | 2015-07-30 14:59 | 2015-07-09 14:58 | 2015-12-11 17:03 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 15:01 | S217010030001 | OCTAVIA HOUSE | 205881 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 15:01 | 2015-07-30 15:02 | 2015-07-09 15:01 | 2015-09-18 17:57 | -21 | In target
OCTAVIA HOUSE - 2015.05.27 | 2015-07-09 15:03 | S217010030001 | OCTAVIA HOUSE | 205885 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 15:03 | 2015-07-30 15:03 | 2015-07-09 15:03 | 2015-09-18 17:56 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:42 | S217010030001 | OCTAVIA HOUSE | 102873 | Completed | 2 | Medium | Miscellaneous | There were a lot of discarded cigarette ends on the third floor level staircase landing floor by the refuse chute opening of flats 19 and 20. | I would recommend that the person responsible for these discarded cigarette ends is identified and reminded of the no smoking policy and also the dangers of putting smoking material down the refuse chute, if this is what is happening. | Neighbourhood Management | Martin Barr |  | We haven't been able to identify the person responsible but on subsequent checks no signs of cigarette ends. The ESA will continue to monitor on his visits to the block. | 2014-04-04 | Fully Completed | Martin Barr | 2013-08-20 14:42 | 2013-10-19 14:43 | 2013-08-20 14:42 | 2014-04-07 13:18 | -60 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:47 | S217010030001 | OCTAVIA HOUSE | 102879 | Completed | 8a | High | Communal Area Storage | On the 3rd floor level staircase landing of flats 53 and 54 there is a gas slot in domestic cooker. | This cooker should be removed from this staircase landing. | Neighbourhood Management | Martin Barr |  | Order raised for removal of cooker | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-20 14:47 | 2013-09-10 14:48 | 2013-08-20 14:47 | 2013-11-08 14:44 | -21 | In target
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:49 | S217010030001 | OCTAVIA HOUSE | 102880 | Completed | 48 | High | Communal Area Storage | The external balcony area of flat 48 is piled high with cardboard boxes and furniture etc. | This balcony area should be tidied up and a lot of the items stored on this balcony area should be removed to lower the fire loading and also so that the balcony is not obstructed. | Neighbourhood Management | Glenn McAllister | 2013-12-05 | Checked the area in early October. This has now been referred to the Neighbourhood Officer, Glenn McAllister to contact the resident and ensure that the area is kept in a tidier condition. All combastbile items have been removed | 2013-11-07 | Fully Completed | Martin Barr | 2013-08-20 14:49 | 2013-09-10 14:50 | 2013-08-20 14:49 | 2014-01-03 10:19 | -21 | In target | 2013-08-20 14:49 | 2014-01-09 10:18 | Janice Wray
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:50 | S217010030001 | OCTAVIA HOUSE | 102881 | Completed | 8c | High | Communal Area Storage | Both of the two basement areas could do with a good tidy up and all the old damaged items stored there removed. | I would recommend that the two basement areas are tided up and all unwanted old and damaged items are removed from these areas. If one part is to be used as a cleaners store and rest area the amount of materials should be kept to a minimum as should and chairs and other items. This is because there is no fire separation of this basement area from the remainder of the staircase enclosure. If this area is to be used as a full rest room type area then the basement level must be fully fire separated from the remainder of the building. | Neighbourhood Management | Martin Barr |  | Items have been removed. Cleaners store is still in use but amount of items stored has been reduced. | 2014-11-05 | Fully Completed | Martin Barr | 2013-08-20 14:50 | 2013-09-10 14:51 | 2013-08-20 14:50 | 2014-11-06 16:26 | -21 | In target | 2013-08-20 14:50 | 2014-11-12 16:26 | Janice Wray
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:55 | S217010030001 | OCTAVIA HOUSE | 102884 | Completed | 9 | High | Inspection Regime | There is some building work being undertaken at the roof level above flat 68 to the brickwork of the parapet wall, this work is not completed but there is a lot of rubble, old brick work etc on the open roof along with contractors waste. It is assumed that all the building materials and contractors waste etc will all be removed from the roof area along with all the scaffolding. | I would recommend that somebody checks this roof area before the contractors leave site to see that all waste, rubbish and equipment, scaffolding is removed from site. | Neighbourhood Management | Martin Barr |  | Items from the roof were cleared. | 2014-11-05 | Fully Completed | Martin Barr | 2013-08-20 14:55 | 2013-09-10 14:56 | 2013-08-20 14:55 | 2014-11-06 16:30 | -21 | In target | 2013-08-20 14:55 | 2014-11-12 16:29 | Janice Wray
OCTAVIA HOUSE-2013.06.27 | 2013-08-20 14:57 | S217010030001 | OCTAVIA HOUSE | 102887 | Completed | 12a | High | Miscellaneous | At the fourth floor level of each staircase there is a wire gate fitted with a gerda lock which controls access to the open external roof area of the building. All of these gerda locks were locked shut and could not be unlocked apart from one and the gates are also secured shut with padlocks and chains. | Do the TMO know about this securing arrangement for these gates? If so no action is needed as long as the caretakers have all the keys needed to unlock all the locks fitted. If the TMO do not know about this issue then each gerda lock should be repaired or replaced and the reason for the padlocks and chains investigated. | Neighbourhood Management | Martin Barr |  | Martin, are you aware of any arrangements re the padlocks and chains plus the Gerda locks being locked shut? If not do you need to get repairs to release them? The padlocks and Gerda locks are standard and all ESAs can access these locks. I have been on the roof myself and gained access with FB keys and commonly used Gerda keys. | 2013-10-11 | Fully Completed | Martin Barr | 2013-08-20 14:57 | 2013-09-10 15:00 | 2013-08-20 14:57 | 2013-10-14 14:40 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:52 | S217010050005 | PICKWICK HOUSE | 158112 | Completed | 8a | High | Communal Area Storage | There is a sports bag containing household items in the electrical cupboard by flats 19 and 20. | I would recommend that this bag and its contents are removed from this electrical cupboard. | Neighbourhood Management | Martin Barr |  | bag was removed, cupboard left clear | 2015-06-03 | Fully Completed | Martin Barr | 2014-08-19 15:52 | 2014-09-09 15:53 | 2014-08-19 15:52 | 2015-06-04 12:51 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:53 | S217010050005 | PICKWICK HOUSE | 158115 | Completed | 8b | High | Communal Area Storage | There is furniture being stored by the rear exit door to the gardens by flats 1 and 2. . | This furniture should be removed from this area and the residents reminded that items of furniture should be stored in the staircase enclosure. | Neighbourhood Management | Martin Barr |  | Confirmed as removed 28-08-14 | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 15:53 | 2014-09-09 15:54 | 2014-08-19 15:53 | 2014-09-01 16:42 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:54 | S217010050005 | PICKWICK HOUSE | 158117 | Completed | 8c | High | Communal Area Storage | There is a settee and other soft furniture being stored in the alcove outside flats 11 and 12, the note on this settee etc says " being removed 2nd July" . | This settee and other furniture should be removed immediately from this area and the residents reminded that items of furniture should be stored in the staircase enclosure. | Neighbourhood Management | Martin Barr |  | Items have all been removed | 2015-06-03 | Fully Completed | Martin Barr | 2014-08-19 15:54 | 2014-09-09 15:56 | 2014-08-19 15:54 | 2015-06-04 12:53 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 15:56 | S217010050005 | PICKWICK HOUSE | 158120 | Completed | 8d | High | Communal Area Storage | There are pieces of kitchen work surface and other pieces of kitchen units in the alcove outside flats 17 and 18. | These items should be removed immediately. | Neighbourhood Management | Martin Barr |  | Confirmed removed 28-08-14 | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 15:56 | 2014-09-09 15:57 | 2014-08-19 15:56 | 2014-09-01 16:44 | -21 | In target
PICKWICH HOUSE - 2014.08.14 | 2014-08-19 16:00 | S217010050005 | PICKWICK HOUSE | 158123 | Completed | 23 | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | Caretakers complete checks of the building. Records of these will be electronic in the coming months. | 2014-08-29 | Fully Completed | Martin Barr | 2014-08-19 16:00 | 2014-10-18 16:01 | 2014-08-19 16:00 | 2014-09-01 16:45 | -60 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 11:43 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181301 | Completed | 8 | Low | Inspection Regime | The store is untidy and could do with a tidy up. | I would recommend that the store room is tidied up and any old, damaged or unwanted items are deposed of. | Neighbourhood Management | Martin Barr |  | Store area has been cleared out. | 2015-06-03 | Fully Completed | Martin Barr | 2015-02-02 11:43 | 2015-08-01 11:44 | 2015-02-02 11:43 | 2015-06-04 12:53 | -180 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 12:14 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181313 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-02 12:14 | 2015-02-23 12:16 | 2015-02-02 12:14 | 2015-05-19 12:07 | -21 | In target
PORTOBELLO COURT COMMUNITY CENTRE - 2014.08.14 | 2015-02-02 12:18 | U217012270159 | PORTOBELLO COURT CLUBROOM | 181315 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-02 12:18 | 2015-02-23 12:19 | 2015-02-02 12:18 | 2015-05-19 12:08 | -21 | In target
PURCELL HOUSE- 2015.01.28 | 2015-02-03 11:15 | S217012760009 | PURCELL HOUSE | 181540 | Completed | 8 | Low | Inspection Regime | During the risk assessment access could not be gained to the half landing store rooms off each staircase landing of this building as the caretaker does not have keys for these 4 areas. It is not known what is in these 4 store rooms, but they are suitably fire separated from the staircase landings. | I would recommend that keys are obtained to the locks of these store room doors as these are presently not private storage areas but common parts of the building, under the control of the TMO. Once keys have been obtained for these storerooms a regular check on their contents should be undertaken to see that the storage or use is in accordance with the tenancy agreements. I would recommend that access to these storage rooms is then controlled/restricted to known persons only. | Neighbourhood Management | Wendy Stevenson |  | Completed 19/3/15 - 4 storage cb keys with Kebra Smith | 2015-03-20 | Fully Completed | Janice Wray | 2015-02-03 11:15 | 2015-08-02 11:16 | 2015-02-03 11:15 | 2015-05-11 12:49 | -180 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 17:49 | S217010420002 | RAYMEDE TOWER | 148300 | Completed | 2 | High | Signage | On the 10th floor level the landing area of the staircase is littered with discarded used cigarette ends and smoking material. | I would recommend that the residents of this floor level are reminded that there is no smoking allowed in the internal areas of this building. A "No Smoking" could be displayed here. | Neighbourhood Management | Martin Barr |  | Issue has been referred to neighbourhood officer and police as kids appear to be smoking in area at night time. no smoking sign was put up. | 2015-06-03 | Fully Completed | Martin Barr | 2014-06-11 17:49 | 2014-07-02 17:50 | 2014-06-11 17:49 | 2015-06-04 13:09 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:02 | S217010420002 | RAYMEDE TOWER | 148310 | Completed | 16b | Medium | Signage | There is no signs displayed in the ground floor level entrance lobby area of this building informing the emergency services which flats are located on which floor levels. This sign would aid would aid the fire service or any other emergency service person if there is an incident in this building. | I would recommend that a sign is displayed in the ground floor level entrance lobby area of this building showing which flat numbers are located on which floor level. This sign should be permanently fixed to the wall and in a large font. | Neighbourhood Management | Martin Barr |  | Signs have been ordered & landscape & environment team are arranging them. | 2015-10-01 | Fully Completed | Martin Barr | 2014-06-11 18:02 | 2014-08-10 18:04 | 2014-06-11 18:02 | 2015-11-02 10:37 | -60 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:05 | S217010420002 | RAYMEDE TOWER | 148313 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2014-06-11 18:05 | 2014-07-02 18:06 | 2014-06-11 18:05 | 2015-05-19 12:11 | -21 | In target
RAYMEDE TOWER - 2014.5.28 | 2014-06-11 18:06 | S217010420002 | RAYMEDE TOWER | 148315 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2014-06-11 18:06 | 2014-07-02 18:07 | 2014-06-11 18:06 | 2015-05-19 12:11 | -21 | In target
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 14:36 | S217012760003 | RILEY HOUSE | 244638 | Completed | 3 | High | Miscellaneous | The fire fighter entry over ride device fitted to the entrance door of the staircase to flats 17 to 32 did not function and release the locking device and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. | The fire fighter entry over ride device fitted to this staircase entrance door should be repaired or replaced so that it releases the locking device fitted to the door. Could ESA check is this has now been repaired & if not raise order | Neighbourhood Management | Nicola Rees | 2016-03-21 | This repair was completed on the 18.03.16. | 2016-03-18 | Fully Completed | Nicola Rees | 2016-02-19 14:36 | 2016-03-11 14:38 | 2016-02-19 14:36 | 2016-04-12 16:47 | -21 | In target
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 14:39 | S217012760003 | RILEY HOUSE | 244640 | Completed | 8a | Medium | Miscellaneous | In the ground floor electrical cupboard by flats 1 and 2 there is some old pieces of flooring etc. This appears to be from the part of the floor which is missing outside flat 1. | All the waste flooring should be removed from this electrical cupboard. The electrical cupboards should not be used as storage areas by contractors. Could ESA arrange removal of these items if they are no longer required or relocation if they are | Neighbourhood Management | Nicola Rees | 2016-05-02 | Items removed - confirmed by ESA 20.04.16 | 2016-04-11 | Fully Completed | Nicola Rees | 2016-02-19 14:39 | 2016-04-19 14:41 | 2016-02-19 14:39 | 2016-04-21 12:05 | -60 | In target
RILEY HOUSE, MILMAN STREET, LONDON SW10 0BS - 2016.01.28 | 2016-02-19 14:49 | S217012760003 | RILEY HOUSE | 244652 | Completed | 8b | Medium | Miscellaneous | 8There are some bags of builders waste on the staircase landings in the secondary staircase flats 17 to 32. | I would recommend that these bags of waste and rubbish are removed from these staircase landings. | Neighbourhood Management | Nicola Rees | 2016-05-23 | This was not there when checked on the 14.04.16 | 2016-04-14 | Fully Completed | Nicola Rees | 2016-02-19 14:49 | 2016-04-19 14:50 | 2016-02-19 14:49 | 2016-04-15 15:50 | -60 | In target
SALTERS ROAD, FLATS 1 TO 28 - 2015.10.13 | 2015-11-02 11:09 | S217009940001 | SALTERS ROAD (1-28) | 225132 | Completed | 8 | High | Communal Area Storage | Residents are storing combustible items outside their flats entrance doors on the 2nd floor level staircase landings. Outside flats 2 and 4 all the household items should be removed, the children's toys could remain. Outside flats 6 and 8 the decorating items should be removed, including the boxes of laminate flooring and step ladders. Also the items of the staircase half landing. The small table is acceptable. Outside flats 10 and 12 the household items should be removed. Outside flats 14 and 16 on the landing there is a wardrobe on wheels used as a storage cupboard, this wardrobe should be removed The small unit and shoe rack outside flats 18/20 and 22/24 are acceptable and no action is needed. There was no access to the staircase of flats 26 and 28, any items on these staircase landings should be removed. | I would recommend that the residents are asked to remove the combustible items outside their flat entrance doors on the staircase landings. The residents should be reminder that the staircase enclosures should be maintained free of all items of combustible storage so that there is no fuel source for a fire and the fire loading of the staircase is kept as low as possible. | Neighbourhood Management | Louise Nezandonyi | 2016-01-12 | The ERSA has confirmed that everything has now been removed | 2016-01-11 | Fully Completed | Louise Nezandonyi | 2015-11-02 11:09 | 2015-11-23 11:10 | 2015-11-02 11:09 | 2016-01-12 11:52 | -21 | In target | 2015-11-02 11:09 | 2015-12-06 15:27 | Louise Nezandonyi
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:38 | S217007860006 | SOUTHAM HOUSE | 201215 | Completed | 8 | Low | Inspection Regime | During the risk assessment access could not be gained any of the lower ground floor levels areas of this building. It is not known what is in the garages or the storage cupboards/rooms, but these areas are suitably fire separated from the staircases. | I would recommend that a check on the contents of these areas is undertaken, to see that the storage or use of these areas/garages etc is in accordance with the tenancy agreements. | Neighbourhood Management | Martin Barr | 2016-02-01 | Spoken to Ronnie he has confirmed that at trhe lower ground floor levels of these blocks Marvel the contractors are using the storage cupoboards to store their material. He said that he can not get into the are in the first block 1-9 and in the other one it is all maintained well and everything is in the cupboards. No one else uses the storage spaces. | 2016-02-01 | Fully Completed | Louise Nezandonyi | 2015-06-12 08:38 | 2015-12-09 08:39 | 2015-06-12 08:38 | 2016-02-02 11:55 | -180 | In target
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:40 | S217007860006 | SOUTHAM HOUSE | 201217 | Completed | 12 | High | Miscellaneous | At the lower ground floor level at the base of the staircase of flats 1 to 9 a person cannot open the door. | I would recommend that suitable release devices, complying with the requirements of the Building regulations is fitted to this door and possibly also to the exit door at the corridor. Alternatively signage could be placed at the ground floor level stating "Leave the building by this door as there is no exit at the lower ground floor level" or words to this effect. Martin, please advise which option we should progress - if it would be preferable to retain existing arrangement please advise H&S who can arrange signage | Neighbourhood Management | Martin Barr |  | This is a fob key door, so a person with a fob key would be able to open the door. If that is non compliant with the building regs then we would either need to change the exit mechanism or put the signage as suggested. | 2015-10-30 | Fully Completed | Martin Barr | 2015-06-12 08:40 | 2015-07-03 08:41 | 2015-06-12 08:40 | 2015-11-02 10:41 | -21 | In target
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:43 | S217007860006 | SOUTHAM HOUSE | 201219 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-12 08:43 | 2015-07-03 08:44 | 2015-06-12 08:43 | 2015-09-21 08:50 | -21 | In target
SOUTHAM HOUSE - 2015.06.03 | 2015-06-12 08:44 | S217007860006 | SOUTHAM HOUSE | 201220 | Completed | 23c | High | Inspection Regime | Is the caretaker undertaking the occupiers tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-06-12 08:44 | 2015-07-03 08:45 | 2015-06-12 08:44 | 2015-09-21 08:50 | -21 | In target
ST COLUMBS HOUSE, BLAGROVE ROAD, LONDON W10 5TJ - 2016.07.21 | 2016-09-12 15:55 | S217008130001 | ST COLUMBS HOUSE | 270741 | Active | 8 | High | Inspection Regime | Outside flats 7 and 8 and in the small cupboard/room by flat's 5 entrance door there were some items of household furniture, etc. | These items should be removed from these areas. | Neighbourhood Management | Louise Nezandonyi | 2016-10-10 |  |  |  | Cyril Morris | 2016-09-12 15:55 | 2016-10-03 16:45 |  |  | 157 | 157 days overdue
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:49 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215782 | Completed | 2a | High | Inspection Regime | There are quite a few cigarette burn marks on the staircase carpet of the staircase enclosure of flats 1A to 7B. | I would recommend that an investigation is undertaken to see who is smoking in this staircase enclosure and leaving cigarette burn marks on the staircase carpet. Smoking in internal communal areas is not allowed. | Neighbourhood Management | Martin Barr |  | We have not identified those responsible, but issue was referred to Neighbourhood Officer and no smoking signs were displayed. | 2015-09-25 | Fully Completed | Martin Barr | 2015-09-09 16:49 | 2015-09-30 16:50 | 2015-09-09 16:49 | 2015-09-28 15:50 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:51 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215783 | Completed | 2b | Medium | Signage | There are not any "No Smoking" signs displayed in the entrance lobby areas of the parts of this building which have duplex flats within them.. | "No Smoking" sign's should be displayed in each of these three entrance lobby areas of this buildings. | Neighbourhood Management | Martin Barr |  | Signs have been put up | 2015-09-25 | Fully Completed | Martin Barr | 2015-09-09 16:51 | 2015-11-08 16:52 | 2015-09-09 16:51 | 2015-09-28 15:53 | -60 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:52 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215785 | Completed | 3 | Medium | Inspection Regime | Some of the doors of the brick built bin cupboards are missing or are damaged. | I would recommend that the wooden doors of these bin cupboards are repaired or that new doors are fitted. | Neighbourhood Management | Martin Barr |  | These have been reported to repairs team, along with some damage to brickwork on the bin stores, job numbers below Block 1-7 201529725 15-21 201529726 29-35 201529731 34A>B 201529734 39A>B 201529737 | 2015-09-25 | Fully Completed | Martin Barr | 2015-09-09 16:52 | 2015-11-08 16:54 | 2015-09-09 16:52 | 2015-09-28 16:00 | -60 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:54 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215788 | Completed | 4 | Medium | Inspection Regime | Some of the doors of the wall mounted gas meter boxes for these dwellings gas meters are missing or are damaged. | I would recommend that new doors are fitted to any gas meter boxes where they are missing or damaged. | Neighbourhood Management | Martin Barr |  | These have been reported by the ESA to repairs | 2015-10-15 | Fully Completed | Martin Barr | 2015-09-09 16:54 | 2015-11-08 16:55 | 2015-09-09 16:54 | 2015-10-16 10:24 | -60 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:56 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215789 | Completed | 8a & 8B | High | Communal Area Storage | On the staircase landing on the floor level and the lobby area of flats 19A and B there is household furniture being stored. | All items of storage should be removed from this staircase landing & lobby area.. | Neighbourhood Management | Martin Barr |  | This has all been removed now | 2015-12-24 | Fully Completed | Louise Nezandonyi | 2015-09-09 16:56 | 2015-09-30 16:57 | 2015-09-09 16:56 | 2015-12-29 12:34 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:58 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215791 | Completed | 8c | High | Communal Area Storage | At the base of the staircase on the floor level of flats 1A and B there is household furniture being stored. | All items of storage should be removed from this area. | Neighbourhood Management | Martin Barr |  | This has been removed | 2015-12-24 | Fully Completed | Louise Nezandonyi | 2015-09-09 16:58 | 2015-09-30 16:59 | 2015-09-09 16:58 | 2015-12-29 12:52 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 16:59 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215794 | Completed | 8d | High | Communal Area Storage | On the staircase landing on the floor level of flats 49A and B there is a washing machine and household furniture being stored. | All items of storage should be removed from this staircase landing. | Neighbourhood Management | Martin Barr | 2016-01-29 | OCS confirmed on 07/01/2016 that items have been removed by them | 2016-01-07 | Fully Completed | Louise Nezandonyi | 2015-09-09 16:59 | 2015-09-30 17:01 | 2015-09-09 16:59 | 2016-01-13 15:42 | -21 | In target | 2015-09-09 16:59 | 2015-12-18 12:04 | Louise Nezandonyi
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:01 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215795 | Completed | 12a | High | Inspection Regime | The staircase to lobby fire door on the floor level of flats 19A and B is held open by a cabin hook and there is a notice on this door from the occupants of these 2 flats stating that this door must remain in the open position. This is a self closing fire rated door. | The occupants of these 2 flats should be informed that the staircase to lobby door is a self closing fire rated door which should be shut unless a person is using the door. The cabin hook should be removed from this door. | Neighbourhood Management | Martin Barr | 2016-01-18 | Job ref 201551663 was completed on the 18th Jan. The cabin hook has been removed | 2016-01-18 | Fully Completed | Louise Nezandonyi | 2015-09-09 17:01 | 2015-09-30 17:03 | 2015-09-09 17:01 | 2016-02-09 13:39 | -21 | In target
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:12 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215805 | Completed | 12g | Medium | Communal Area Storage | In the lobby area of the staircase up to flats 11A and B a poorly fitted shelf has been erected and there is storage on this shelf. | This presently fitted shelf should be removed as it is badly fitted/constructed and all combustible items should be removed from this area. | Neighbourhood Management | Martin Barr | 2016-01-29 | The shelpf has now been removed by our contractors | 2016-02-15 | Fully Completed | Louise Nezandonyi | 2015-09-09 17:12 | 2015-11-08 17:14 | 2015-09-09 17:12 | 2016-02-16 10:48 | -60 | In target | 2015-09-09 17:12 | 2016-02-21 20:47 | Louise Nezandonyi
ST ERVANS ROAD, FLATS 1 TO 49 - 2015.08.27 | 2015-09-09 17:15 | S217010097701 | ST ERVANS ROAD ODD (1-49) | 215807 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-09 17:15 | 2015-09-30 17:17 | 2015-09-09 17:15 | 2015-09-17 10:50 | -21 | In target
ST MARKS GROVE FLATS 1-12 - 2015.06.15 | 2015-06-29 10:40 | S217010180013 | ST MARKS GROVE 1-12 | 203752 | Active | 1 | High | Miscellaneous | The area outside of this buildings electrical room/cupboard has recently been tarmac-ed, this tarmac is too high and the electrical room/cupboard door now does not open more than half way without damaging the door. If there was a fire in this electrical area not being able to fully open the door will cause problems. | I would recommend that the tarmac-ed area outside of this electrical room/cupboard door is lowered so that the door can be open fully. Alternatively part of the bottom of the door could be removed. | Neighbourhood Management | John Gaffney
ST MARKS GROVE FLATS 1-12 - 2015.06.15 | 2015-06-29 10:46 | S217010180013 | ST MARKS GROVE 1-12 | 203755 | Completed | 12 | Information Only | Inspection Regime | The metal cabinet secured to the wall of the staircase half landing below this ceiling hatch which might contain a portable ladder to access the external roof could not be opened using an FB key. | I would recommend that the caretaker is asked to check this ladder cabinet to see why an FB key would not open the lock fitted to the cabinet. If the lock fitted is not an FB one I would recommend that an FB lock is fitted. | Neighbourhood Management | Wendy Stevenson | 2016-01-14 | Email sent to John on 18.11.15 to confirm whether the fb lock has been installed. John confirmed that this was locked with a broken FB key and has said that this is operational. | 2016-01-14 | Fully Completed |  |  |  | 2015-06-29 10:46 | 2016-01-15 12:24
ST MARKS GROVE FLATS 1-12 - 2015.06.15 | 2015-06-29 10:50 | S217010180013 | ST MARKS GROVE 1-12 | 203758 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Wendy Stevenson | 2015-12-01 | I have ran a report and can see for the last three months this has been completed and its been done on a monthly basis. | 2015-12-01 | Fully Completed | Nicola Rees | 2015-06-29 10:50 | 2015-07-20 10:51 | 2015-06-29 10:50 | 2015-12-02 16:20 | -21 | In target
ST MARKS GROVE FLATS 1-12 - 2015.06.15 | 2015-06-29 10:51 | S217010180013 | ST MARKS GROVE 1-12 | 203759 | Completed | 23c | High | Inspection Regime | Is the caretaker undertaking the occupier's tests, checks and inspections of this building as per the caretakers check list. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | John Whall confirms inspections undertaken | 2015-10-09 | Fully Completed | Janice Wray | 2015-06-29 10:51 | 2015-07-20 10:52 | 2015-06-29 10:51 | 2015-10-12 13:15 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:10 | S217010180014 | ST MARKS GROVE 13-48 | 203733 | Completed | 12f | Information Only | Inspection Regime | The metal cabinet secured to the wall of the staircase half landing below this ceiling hatch which might contain a portable ladder to access the external roof could not be opened using an FB key. | I would recommend that the caretaker is asked to check this ladder cabinet to see why an FB key would not open the lock fitted to the cabinet. If the lock fitted is not an FB one I would recommend that an FB lock is fitted. | Neighbourhood Management | Wendy Stevenson | 2016-01-14 | Email sent to John to check on the 18.11.15. John has confirmed that these are operartional and seemed to have been locked previously with a broken key. | 2016-01-14 | Fully Completed |  |  |  | 2015-06-29 10:10 | 2016-01-15 12:23
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:13 | S217010180014 | ST MARKS GROVE 13-48 | 203736 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Wendy Stevenson |  | I have run a report and the monthly electrics tests have been documented over the last three months. | 2015-12-01 | Fully Completed | Nicola Rees | 2015-06-29 10:13 | 2015-07-20 10:15 | 2015-06-29 10:13 | 2015-12-02 16:22 | -21 | In target
ST MARKS GROVE FLATS 14 - 48 - 2015.06.15 | 2015-06-29 10:15 | S217010180014 | ST MARKS GROVE 13-48 | 203737 | Completed | 23c | High | Inspection Regime | Is the caretaker undertaking the occupier's tests, checks and inspections of this building as per the caretakers check list? | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | ESA (John Whall) confirms inspectiosn undertaken & recorded on PDA | 2015-10-09 | Fully Completed | Janice Wray | 2015-06-29 10:15 | 2015-07-20 10:16 | 2015-06-29 10:15 | 2015-10-12 13:44 | -21 | In target
STABLE WAY - 2014.10.20 | 2014-10-31 10:55 | S217008220100 | STABLE WAY SITE | 167740 | Completed | 23 | Information Only | Fire Extinguisher | I would recommend that the fire extinguishers located in the red plastic box at the fire point are visually checked at the same time as the fire extinguishers within the site office. | I would recommend that the visual check on the fire extinguishers in the red plastic box at the fire point alarm is recorded in the site offices fire logbook. This is so that there is no duplication of fire logbooks and records. | Neighbourhood Management | Daniel Mason |  | Order raised ofr the erection of fire extinguisher box Fire book updated | 2014-11-06 | Fully Completed |  |  |  | 2014-10-31 10:55 | 2014-12-17 15:02 |  |  | 2014-10-31 10:55 | 2014-12-08 14:12 | Daniel Mason
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:09 | S217008220100 | STABLE WAY SITE | 105896 | Completed | 2 | Medium | Smoking In Communal Area | 2 Medium There are not any "No Smoking" signs displayed in this building. | No Smoking signage should be displayed in this building. Daniel -please contact Adrian for NO SMOKING SIGNS | Neighbourhood Management | Daniel Mason |  | Sign erected it all rooms and passage way | 2013-10-18 | Fully Completed | Daniel Mason | 2013-09-12 14:09 | 2013-11-11 14:11 | 2013-09-12 14:09 | 2013-11-29 15:04 | -60 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:23 | S217008220100 | STABLE WAY SITE | 105907 | Completed | 23b | High | Fire Alarm | It appears that the weekly occupier's tests of the buildings fire alarm and warning system are not being undertaken? | Weekly occupier inspections of the buildings fire alarm and warning system should be undertaken, with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Daniel Mason |  | Weekly inspection and testing of fire alarm conducted | 2013-09-20 | Fully Completed | Daniel Mason | 2013-09-12 14:23 | 2013-10-03 14:25 | 2013-09-12 14:23 | 2013-11-29 15:06 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:27 | S217008220100 | STABLE WAY SITE | 105911 | Completed | 23d | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting units/ system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting units/system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Daniel Mason |  | Lights tested and result recorded | 2013-12-17 | Fully Completed | Daniel Mason | 2013-09-12 14:27 | 2013-10-03 14:29 | 2013-09-12 14:27 | 2013-12-24 10:43 | -21 | In target
STABLE WAY OFFICE - 2013.09.12 | 2013-09-12 14:28 | S217008220100 | STABLE WAY SITE | 105913 | Completed | 23e | Medium | Fire Extinguisher | Monthly occupier testing and inspections of the portable fire extinguishers, exit doors and escape routes are not being undertaken. | Monthly occupier testing and inspections of the portable fire extinguishers, exit doors and escape routes in the building should be undertaken, with the results recorded as proof of testing etc. | Neighbourhood Management | Daniel Mason |  | Testing of exit doors and inspection of portable fire extinguishers carried out and result recored | 2013-09-19 | Fully Completed | Daniel Mason | 2013-09-12 14:28 | 2013-11-11 14:30 | 2013-09-12 14:28 | 2013-11-29 15:25 | -60 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:32 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151153 | Completed |  |  |  | It appears that somebody is sleeping in the old BT room on the ground floor level by flat 25. This was reported to the TMO Health and Safety team whilst I was on site. | I would recommend that this room is emptied out of all items and the door secured locked shut using a different type of lock so that this room cannot be accessed unless by authorised persons only. | Neighbourhood Management | Martin Barr |  | Clearance and locking of this room was arranged | 2014-11-05 | Fully Completed |  |  |  | 2014-07-01 12:32 | 2014-11-06 15:50
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:42 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151163 | Completed | 8a | High | Communal Area Storage | There are quantities of waste and combustible items in the three of the six unused rooms off the staircases in this building. These rooms are supposed to be kept empty and secured locked shut so that no items are placed in them. There are present only metal security doors to these rooms, and the contents of the rooms is increases the fire loading of the rooms. | The 3 rooms with items in them should be emptied out immediately, I would recommend that different locks are placed on the doors of these rooms so that only authorised persons can access these rooms. Checks should be undertaken in future to ensure that the rooms remain free of any items. Alternatively if these rooms are to be used for the storage of items etc then the metal doors should be removed and 30 minute fire doors fitted, please also see item s 12a and 14 below. | Neighbourhood Management | Martin Barr |  | Clearance and locking of these rooms was arrangd | 2014-11-05 | Fully Completed | Martin Barr | 2014-07-01 12:42 | 2014-07-22 12:45 | 2014-07-01 12:42 | 2014-11-06 15:55 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:46 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151164 | Completed | 8b | High | Miscellaneous | There are quantities of waste, combustible items and rubbish in the ground floor electrical room next to flat 25. | The rubbish etc in the ground floor electrical room next to flat 25 should be removed immediately. Alternatively if this electrical room is going to be used for storage then please see item 14 below. | Neighbourhood Management | Martin Barr |  | Removal of items was arranged | 2014-11-05 | Fully Completed | Martin Barr | 2014-07-01 12:46 | 2014-07-22 12:48 | 2014-07-01 12:46 | 2014-11-06 16:03 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:49 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151165 | Completed | 8b | High | Miscellaneous | There are quantities of waste, combustible items and rubbish in the ground floor electrical room next to flat 25. | The rubbish etc in the ground floor electrical room next to flat 25 should be removed immediately. Alternatively if this electrical room is going to be used for storage then please see item 14 below. | Neighbourhood Management | Martin Barr |  | Removal of items was arranged | 2014-11-05 | Fully Completed | Martin Barr | 2014-07-01 12:49 | 2014-07-22 12:51 | 2014-07-01 12:49 | 2014-11-06 16:05 | -21 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 12:52 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151168 | Completed | 8c | Medium | Communal Area Storage | Outside flat 75 on the ground floor on the walkway there are old wooden shelves, suitcases and cardboard boxes. | I would recommend that the occupant of this flat is reminded that combustible items should not be stored in the common parts of the building. These items should be removed, there is also a push bike here which can remain, unless the occupant persists in storing items in the common parts then I would recommend that all items are removed. | Neighbourhood Management | Martin Barr |  | Resident was instructed to remove items. There are now bike stands outside the block as well. | 2014-11-05 | Fully Completed | Martin Barr | 2014-07-01 12:52 | 2014-08-30 12:54 | 2014-07-01 12:52 | 2014-11-06 16:13 | -60 | In target
STONELEIGH PLACE - 2014.6.18 | 2014-07-01 13:02 | S217010257701 | STONELEIGH PLACE 1-83 ODD | 151174 | Completed | 14 | High | Communal Area Storage | The six rooms located off the staircases, two at each floor level and the two ground floor level electrical rooms each have air bricks in their walls on to the staircase or the walkway/ balcony. | If these rooms are to be used for storage or any other used and not maintained completely empty then suitable fire stopping of the rooms should be undertaken. This will entail the removal of the air bricks in the walls of these rooms and replacing them with normal bricks or covering the air bricks over with a fire rated material suitably secured. If all of these rooms are kept completely empty of all storage then no action is required. | Neighbourhood Management | Martin Barr |  | Removal of items was arranged, therefore fire stopping works was not necessary. | 2014-11-05 | Fully Completed | Martin Barr | 2014-07-01 13:02 | 2014-07-22 13:07 | 2014-07-01 13:02 | 2014-11-06 17:29 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:26 | S217012770006 | TALBOT GROVE HOUSE | 177717 | Completed | 8a | High | Communal Area Storage | The balcony area outside flat 27 is very narrow and cluttered with old plant pots, a wooden table and chairs, the width of the balcony has been reduced thus effecting the means of escape route from the flat. This is the end flat so only the occupants of this flat are affected. | I would recommend that the occupant of this flat is asked to remove some of the items from the balcony, this will improve the means of escape route from the flat in an emergency. If the occupant does not what to remove some of the items I would recommend that all of the items on the balcony are removed and the balcony kept completely clear and free of all pots of plants, tables and chairs etc. This will reduce any fire loading on this area to zero. | Neighbourhood Management | Siobhan Rumble |  | housing officer to write to tenant to remove or have removed | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-12 11:26 | 2015-02-02 11:27 | 2015-01-12 11:26 | 2015-07-14 15:06 | -21 | In target | 2015-01-12 11:26 | 2015-03-18 15:56 | Siobhan Rumble
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:28 | S217012770006 | TALBOT GROVE HOUSE | 177720 | Completed | 8b | Medium | Communal Area Storage | At the base of the staircase of flats 15 to 31, in the alcove area there is an wheel chair, this is covered in dust and dirty as well as cobwebs, so has not moved or been used in a while. | I would recommend that this wheel chair is removed from this area. | Neighbourhood Management | Siobhan Rumble |  | janice Jones has written to tenants to see who chair belongs to, if no response will have removed. | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-12 11:28 | 2015-03-13 11:29 | 2015-01-12 11:28 | 2015-07-14 15:07 | -60 | In target | 2015-01-12 11:28 | 2015-03-18 15:53 | Siobhan Rumble
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:30 | S217012770006 | TALBOT GROVE HOUSE | 177722 | Completed | 8c | Medium | Communal Area Storage | Outside flat 35 on the balcony is an old television set, cardboard boxes and black bags. | I would recommend that the occupant of this flat is reminded that combustible items should not be stored in the common parts of the building. These items should be removed. | Neighbourhood Management | Siobhan Rumble |  | with Housing Officer to speak to tenants and get removed | 2015-07-31 | Fully Completed | Siobhan Rumble | 2015-01-12 11:30 | 2015-03-13 11:31 | 2015-01-12 11:30 | 2015-08-03 12:24 | -60 | In target | 2015-01-12 11:30 | 2015-03-18 15:53 | Siobhan Rumble
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:35 | S217012770006 | TALBOT GROVE HOUSE | 177729 | Completed | 10a | High | Communal Area Storage | Outside the flat entrance door of flat 34 there is a BBQ with the gas pipe disappearing into a large plastic storage container, where I believe that the gas cylinder is located. It is likely that this occupant uses this gas BBQ in this area directly outside the flat door and under the balcony. This is a high fire risk item and a fire hazard. I believe that cooking on a BBQ in this location is not allowed under the tenancy agreement. | I would recommend that the BBQ and gas cylinder are removed from this area immediately. | Neighbourhood Management | Siobhan Rumble |  | Area Manager advises that this is not a BBQ, happy for you to re visit but for now i will mark it complete | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-01-12 11:35 | 2015-02-02 11:36 | 2015-01-12 11:35 | 2015-10-15 11:14 | -21 | In target | 2015-01-12 11:35 | 2015-10-21 11:13 | Janice Wray
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:37 | S217012770006 | TALBOT GROVE HOUSE | 177730 | Completed | 10b | High | Communal Area Storage | On the external balcony outside flat number 38 there is a charcoal BBQ, it is not known if the occupant's uses this BBQ on the balcony, but this is a high fire risk item and a fire hazard. I believe that cooking on a BBQ on a flat balcony is not allowed under the tenancy agreement. | I would recommend that the charcoal BBQ is removed from the balcony area outside of flat 38 immediately. | Neighbourhood Management | Siobhan Rumble |  | Housing Officer arranging for removal | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-12 11:37 | 2015-02-02 11:38 | 2015-01-12 11:37 | 2015-10-15 10:34 | -21 | In target | 2015-01-12 11:37 | 2015-03-18 15:52 | Siobhan Rumble
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 11:50 | S217012770006 | TALBOT GROVE HOUSE | 177737 | Completed | 12a | High | Responsive Item | The cement holding the base of the staircase railing in place on the 3rd floor level between flats 28 and 29 has come, is coming away. The staircase railings are now not fully secure and piece of concrete could fall away and hit persons coming up the staircase. This item was telephoned in the TMO Health and Safety Manager whilst I was on site. | I would recommend that these staircase railings are re-fixed back fully to the concrete staircase and floor. Raised already as an urgent repair thro the CSC (& Siobhan CCed in) so for info for Siobhan now | Neighbourhood Management | Siobhan Rumble |  | this has been completed | 2015-10-14 | Fully Completed | Siobhan Rumble | 2015-01-12 11:50 | 2015-02-02 11:52 | 2015-01-12 11:50 | 2015-10-15 10:36 | -21 | In target | 2015-01-12 11:50 | 2015-08-24 11:22 | Siobhan Rumble
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 12:12 | S217012770006 | TALBOT GROVE HOUSE | 177753 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | yes | 2015-03-06 | Fully Completed | Siobhan Rumble | 2015-01-12 12:12 | 2015-02-02 12:13 | 2015-01-12 12:12 | 2015-03-10 15:38 | -21 | In target
TALBOT GROVE HOUSE - 2015.01.06 | 2015-01-12 12:13 | S217012770006 | TALBOT GROVE HOUSE | 177754 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure.. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Siobhan Rumble |  | yes, all available to see on request | 2015-03-03 | Fully Completed | Siobhan Rumble | 2015-01-12 12:13 | 2015-02-02 12:14 | 2015-01-12 12:13 | 2015-03-10 15:29 | -21 | In target
TALBOT HOUSE -2015.05.11 | 2015-05-20 10:29 | S217009100001 | TALBOT HOUSE | 197949 | Completed | 23c | High | Inspection Regime | It appears that the caretaker is not undertaking the monthly testing and inspections within this building. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, including the monthly checks of the fire extinguishers with in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-18 | Fully Completed | Martin Barr | 2015-05-20 10:29 | 2015-06-10 10:30 | 2015-05-20 10:29 | 2015-09-21 09:42 | -21 | In target
TALBOT WALK AND UPPER TALBOT WALK - 2015.06.22 | 2015-07-09 11:22 | S217012770008 | TALBOT WALK | 205727 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | yes | 2015-07-13 | Fully Completed | Siobhan Rumble | 2015-07-09 11:22 | 2015-07-30 11:23 | 2015-07-09 11:22 | 2015-07-14 16:17 | -21 | In target
TALBOT WALK AND UPPER TALBOT WALK - 2015.06.22 | 2015-07-09 11:26 | S217012770008 | TALBOT WALK | 205732 | Completed | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  |  | 2015-07-13 | Fully Completed | Siobhan Rumble | 2015-07-09 11:26 | 2015-07-30 11:27 | 2015-07-09 11:26 | 2015-07-14 15:22 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 11:59 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215184 | Completed | 8a | High | Communal Area Storage | In some of the riser cupboards there is storage, old pieces of wood in the one opposite flat 163, suitcases in the one opposite flat 193, old plant pots in the one opposite flat 247,boxes of old light fittings in the ones opposite flats 155 and 303 pieces of kitchen work surface in the one opposite flat 127. A golf cart and cardboard boxes of items in the one opposite flat 177 | All of these riser cupboards should be emptied out of all storage. | Neighbourhood Management | Martin Barr |  | Job was raised for OCS to clear storage cupboards | 2015-10-23 | Fully Completed | Martin Barr | 2015-09-07 11:59 | 2015-09-28 15:40 | 2015-09-07 11:59 | 2015-11-02 11:21 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 15:40 | S217010330006 | TAVISTOCK CRESCENT 175-195 ODD | 215294 | Completed | 8b | High | Communal Area Storage | On the balcony area outside flats 185 and 187 there is a washing machine, blue bags of clothes and some household items. As well as push bikes. | All of the combustible items should be removed from this balcony area and the washing machine. The push bike can remain. | Neighbourhood Management | Martin Barr |  | Order was raised for OCS to remove items | 2015-10-23 | Fully Completed | Martin Barr | 2015-09-07 15:40 | 2015-09-28 15:43 | 2015-09-07 15:40 | 2015-11-02 11:23 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 15:43 | S217010330009 | TAVISTOCK CRESCENT 241-261 ODD | 215296 | Completed | 8c | High | Communal Area Storage | On the balcony area outside flat 243 there are suitcases and pieces of timber and wood. | These combustible items should be removed from this area. | Neighbourhood Management | Martin Barr |  | Jobs were raised for OCS to remove items | 2015-10-23 | Fully Completed | Martin Barr | 2015-09-07 15:43 | 2015-09-28 15:44 | 2015-09-07 15:43 | 2015-11-02 11:19 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 15:45 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215297 | Completed | 8d | High | Miscellaneous | In some of the lower ground floor level electrical cupboards there is storage. | Any storage in the electrical cupboards should be removed. | Neighbourhood Management | Martin Barr |  | Job was raised for OCS to clear these items | 2015-10-23 | Fully Completed | Martin Barr | 2015-09-07 15:45 | 2015-09-28 15:46 | 2015-09-07 15:45 | 2015-11-02 11:20 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:12 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215311 | Completed | 12e | Medium | Miscellaneous | The riser cupboards opposite flats 119 and 251 could not be opened. | I would recommend that these cupboards are opened and if there is any storage within them this is removed. | Neighbourhood Management | Martin Barr |  | ESA has checked cupboards and no items have been stored within. | 2015-10-01 | Fully Completed | Martin Barr | 2015-09-07 16:12 | 2015-11-06 16:13 | 2015-09-07 16:12 | 2015-10-16 11:33 | -60 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:21 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215315 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-07 16:21 | 2015-09-28 16:23 | 2015-09-07 16:21 | 2015-09-17 11:04 | -21 | In target
TAVISTOCK CRESCENT FLATS 109 TO 305 - 2015.08.27 | 2015-09-07 16:23 | S217010330003 | TAVISTOCK CRESCENT 109-129 ODD | 215318 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-07 16:23 | 2015-09-28 16:24 | 2015-09-07 16:23 | 2015-09-17 10:52 | -21 | In target
TAVISTOCK CRESCENT FLATS 43 TO 85 - 2015.08.27 | 2015-09-04 12:23 | S217010330002 | TAVISTOCK CRESCENT 65-85 ODD | 214928 | Completed | 12a | Medium | Inspection Regime | The riser cupboard opposite flat 83 could not be opened. | I would recommend that this cupboard is opened and if there is any storage within it this is removed. | Neighbourhood Management | Martin Barr |  | ESA opened & checked cupboard, no items are stored within | 2015-10-23 | Fully Completed | Martin Barr | 2015-09-04 12:23 | 2015-11-03 12:25 | 2015-09-04 12:23 | 2015-11-02 11:23 | -60 | In target
TAVISTOCK CRESCENT FLATS 43 TO 85 - 2015.08.27 | 2015-09-04 12:28 | S217010330001 | TAVISTOCK CRESCENT 43-63 ODD | 214930 | Completed | 13 | High | Miscellaneous | At the time of this assessment there was a mobility scooter parked in the common parts area [REDACTED], at the lower ground floor level of this building. There is an electrical socket on the wall next to this mobility scooter which goes to the landlords power supply. This mobility scooter was not being charged at the time of this assessment. | The H M Government fire safety document for purpose built blocks of flats does not allow the charging of mobility scooters in the common parts of residential buildings. The parking of mobility scooters is allowed but not the charging of them. I would recommend that the electrical socket on the wall is removed so that charging cannot be undertaken in this area. | Neighbourhood Management | Martin Barr | 2016-01-29 | Louie-Ann has confirmed that the electrical socket has now been reomved. | 2016-02-15 | Fully Completed | Louise Nezandonyi | 2015-09-04 12:28 | 2015-09-25 12:29 | 2015-09-04 12:28 | 2016-02-16 10:45 | -21 | In target | 2015-09-04 12:28 | 2016-01-20 21:42 | Louise Nezandonyi
TAVISTOCK CRESCENT FLATS 43 TO 85 - 2015.08.27 | 2015-09-04 12:43 | S217010330001 | TAVISTOCK CRESCENT 43-63 ODD | 214933 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-04 12:43 | 2015-09-25 12:56 | 2015-09-04 12:43 | 2015-09-17 11:20 | -21 | In target
TAVISTOCK CRESCENT FLATS 43 TO 85 - 2015.08.27 | 2015-09-04 12:56 | S217010330001 | TAVISTOCK CRESCENT 43-63 ODD | 214940 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-04 12:56 | 2015-09-25 12:58 | 2015-09-04 12:56 | 2015-09-17 11:20 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:16 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173304 | Completed | 8a | High | Communal Area Storage | There were combustible items and waste stored in electrical intake room 6, rubbish, contractors waste, and a very old metal cabinet. | These items should be removed for this electrical intake room. | Neighbourhood Management | Siobhan Rumble |  | all cleared | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-08 16:16 | 2014-12-29 16:17 | 2014-12-08 16:16 | 2015-03-10 15:01 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-08 16:18 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173306 | Completed | 8b | Low | Miscellaneous | The lower ground floor garages and storage areas of the building are private residential storage areas. | I would recommend that the caretakers carry out checks of these areas to see that the residents are complying with the conditions of their tenancy agreements about storage of items etc and that these area are kept tidy with no excessive amounts of combustible items etc. | Neighbourhood Management | Siobhan Rumble |  | there was an audit that took place in May 2012, we are due to do another this year. the caretakers do not have access to the residents garages. | 2015-03-09 | Fully Completed | Siobhan Rumble | 2014-12-08 16:18 | 2015-06-06 16:20 | 2014-12-08 16:18 | 2015-03-10 15:02 | -180 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:22 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173537 | Completed | 19b | High | Miscellaneous | The padlocks securing/locking the other two water ring main boxes above all of the dry risers at the lower ground floor level are not Fire Brigade (FB) padlocks. | The boxes housing the water main and the dry riser inlets and outlets for that matter should be checked and any found not secured or without FB padlocks fitted to them should be fitted with and secured with FB padlocks only. | Neighbourhood Management | Siobhan Rumble |  | we had the wet risers fitted with non standard padlocks to stop people using and breaking them. if these need to be changed please advise | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-09 15:22 | 2014-12-30 15:23 | 2014-12-09 15:22 | 2015-03-10 15:04 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:34 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173554 | Completed | 23b | High | Fire Alarm | Are the weekly occupier's tests of the fire alarm system in this building being undertaken? | Can it be confirmed that the caretaker(s) are undertaking the weekly occupiers testing of the fire alarm system in this building, there were no records of any testing or a fire logbook available at the time of this assessment. | Neighbourhood Management | Siobhan Rumble |  | I have never done or been told to do a test on the roof windows and they are currently out of order | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-09 15:34 | 2014-12-30 15:35 | 2014-12-09 15:34 | 2015-03-10 15:05 | -21 | In target
TESTERTON WALK - 2014.11.18 | 2014-12-09 15:50 | S217012770012 | TESTERTON WALK 301-39 & 401-6 | 173576 | Completed | 23d | High | Inspection Regime | Are the monthly occupier testing and inspections of the emergency escape lighting system, the fire extinguishers and the buildings structural inspections being undertaken? | Can it be confirmed that the caretakers are undertaking the occupiers monthly testing and inspections of the installed systems, as per the caretakers check list in these buildings? With the results completed records kept as proof of testing having been undertaken. | Neighbourhood Management | Siobhan Rumble |  | all on weekly sheets | 2015-03-06 | Fully Completed | Siobhan Rumble | 2014-12-09 15:50 | 2014-12-30 15:51 | 2014-12-09 15:50 | 2015-03-10 15:06 | -21 | In target
TOR COURT - 2015.06.15 | 2015-06-29 11:45 | S217005550001 | TOR COURT | 203788 | Completed | 23b | High | Emergency Lighting | Caretaker testing and inspections of the installed emergency lighting system and the buildings structure. | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson |  | I have checked whether the monthly H+S have been checked from Aug- October 2015. There has been one missed in September and July. Will speak to ESA about consistency of this check. John knows how to check the emergency lighting. | 2015-11-18 | Fully Completed | Nicola Rees | 2015-06-29 11:45 | 2015-07-20 11:46 | 2015-06-29 11:45 | 2015-11-19 16:56 | -21 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:12 | S217008170001 | TREADGOLD HOUSE | 205782 | Completed | 13 | High | Mobility Scooters | At the time of this assessment there was a mobility scooter parked under the only staircase of this building at the ground floor level. This location is next to the lift as well. There is an electrical socket on the wall next to this mobility scooter but the mobility scooter was not being charged at the time of this assessment. | The H M Government fire safety document for purpose built blocks of flats does not allow the charging of mobility scooters in the common parts of residential buildings. The parking of mobility scooters is allowed but not the charging of them. I would recommend that the electrical socket on the wall is removed / secured so that charging cannot be undertaken in this area. As per e-mail please arrange for socket to be secured so only authorised users can access | Neighbourhood Management | Martin Barr |  | The scooter and the electric socket was removed | 2015-10-01 | Fully Completed | Martin Barr | 2015-07-09 12:12 | 2015-07-30 12:15 | 2015-07-09 12:12 | 2015-10-16 10:26 | -21 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:21 | S217008170001 | TREADGOLD HOUSE | 205787 | Completed | 23b | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Can it be confirmed that the monthly occupiers testing and inspections of the emergency lighting system in this building is being undertaken, with the results recorded as proof of testing having been undertaken. If they are not then regular testing of the installed emergency lighting system should start immediately with the tests and any results recorded as proof of the testing. | Neighbourhood Management | Martin Barr | 2015-09-17 | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 12:21 | 2015-07-30 12:22 | 2015-07-09 12:21 | 2015-09-18 17:58 | -21 | In target
TREADGOLD HOUSE - 2015.06.29 | 2015-07-09 12:24 | S217008170001 | TREADGOLD HOUSE | 205791 | Completed | 23d | High | Inspection Regime | Is the caretaker undertaking the occupier's tests, checks and inspections of this building as per the caretakers check list? | Can it be confirmed that the caretaker is undertaking the monthly occupier checks as per the caretakers check list, in this building. With the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-17 | Fully Completed | Martin Barr | 2015-07-09 12:24 | 2015-07-30 12:25 | 2015-07-09 12:24 | 2015-09-18 17:57 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:22 | S217008770001 | TRELLICK TOWER | 136747 | Completed |  | High | Inspection Regime | There appears to be people sleeping on the external ramp opposite the entrance/exit of this building at the lower ground floor level. | I would recommend that this external ramp at the lower ground floor level is inspected and any mattresses etc removed from this area. | Neighbourhood Management | Martin Barr |  | Mattresses have been removed. Ramp will soon be used as entry and exit point for accessing basement storage area which will hopefully deter rough sleepers. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 16:22 | 2014-04-16 16:23 | 2014-03-26 16:22 | 2014-04-28 16:33 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:25 | S217008770001 | TRELLICK TOWER | 136751 | Completed | 2 | High | Inspection Regime | There were discarded used cigarette ends seen on the staircase landings of both the central and end staircases of the taller tower block. | I would recommend that the cleaners are asked to remove all discarded and used smoking materials from the staircase landings and that any residents found smoking in these areas is reminded of the no smoking policy. | Neighbourhood Management | Martin Barr |  | Stairs are routinely swept three times and litter picked twice a week. If residents are seen smoking by concierge or estate staff they will be advised of the policy. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 16:25 | 2014-04-16 16:28 | 2014-03-26 16:25 | 2014-04-28 16:47 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:28 | S217008770001 | TRELLICK TOWER | 136753 | Completed | 3 | High | Inspection Regime | At the time of this assessment the refuse chute in this building was blocked, the refuse chute rooms had bags of rubbish and waste in them and there were piles of bags of waste on the lift lobby's as well. | I would recommend that when the refuse chute is blocked that cleaners are tasked with regularly checking the refuse chute rooms and the lift lobby areas to make certain that piles of rubbish and waste do not accumulate in these areas and all waste and rubbish is removed from the building. | Neighbourhood Management | Martin Barr |  | There is already an arrangement for the cleaners to remove refuse from the lobby areas when the chute is blocked. This is done twice a day. We are working on steps to try and minimise chute blockages. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 16:28 | 2014-04-16 16:32 | 2014-03-26 16:28 | 2014-04-28 16:48 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:32 | S217008770001 | TRELLICK TOWER | 136757 | Completed | 8a | High | Inspection Regime | The disused car park located under the taller tower block is not secured and has combustible items, contractors waste and storage in it along with combustible rubbish. | I would recommend that this area is completely tided up and all the old and stored items are removed and the area secured locked shut. | Neighbourhood Management | Martin Barr |  | The area has been secured. There are metal doors Gerda locks on most of the entrance points. The only other gate has been secured with a heavy duty chain and padlock. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 16:32 | 2014-04-16 16:37 | 2014-03-26 16:32 | 2014-04-28 16:49 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:39 | S217008770001 | TRELLICK TOWER | 136762 | Completed | 8c | Information Only | Inspection Regime | The 3rd and 6th floor level bulk storage rooms off the lift lobby areas contain a lot of personal household property, Paintings wrapped in bubble wrap, suitcases, bags of clothes, kitchen white goods etc as well as push bikes. | Are the TMO aware that these store areas are being used for personnel storage. | Neighbourhood Management | Martin Barr |  | Yes, they have been used for short term storage to allow space in individual flats so that rewiring work can take place. | 2014-04-25 | Fully Completed |  |  |  | 2014-03-26 16:39 | 2014-04-28 16:50
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:52 | S217008770001 | TRELLICK TOWER | 136780 | Completed | 12h | High | Inspection Regime | The floor surface in some link corridors and in parts of some of the lift lobby areas is badly damaged or the floor tiles have been completely removed or are coming off. | The floor surfaces should be inspected and any areas where there is a damaged floor surface should be repaired or a new floor surface laid so as not to be a trip hazard in the event of any emergency. | Neighbourhood Management | Martin Barr |  | These areas are reported when they become damaged. Repairs had replaced the flooring but it was badly applied and needed re-fitting from scratch. This is with RD. | 2014-06-05 | Fully Completed | Martin Barr | 2014-03-26 16:52 | 2014-04-16 16:53 | 2014-03-26 16:52 | 2014-06-06 09:48 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:56 | S217008770001 | TRELLICK TOWER | 136783 | Completed | 12k | Information Only | Miscellaneous | A new door has been fitted at the basement level of the central staircase, this door does not have a FB lock fitted to it, the concierge has a key for this door lock though. | I would recommend that a FB lock is fitted to this do so that caretakers and TMO employees can access the basement area without the need to get a specific key. Martin - do we want to change this or would this compromise the security of the area? | Neighbourhood Management | Martin Barr |  | We do not want an FB lock on this door. FB keys are not very secure and this leads to the pump room. | 2014-04-25 | Fully Completed |  |  |  | 2014-03-26 16:56 | 2014-04-28 16:56
TRELLICK TOWER - 2014.3.6 | 2014-03-26 16:58 | S217008770001 | TRELLICK TOWER | 136784 | Completed | 14 | High | Miscellaneous | In the end staircases some boarding has been removed from above or to the side of the electrical riser cupboards and new cabling has been installed. | Any boarding that has been removed from around the electrical riser cupboards in the end staircases should be fixed back securely and correctly. Martin Could Clinton advise Repairs of the precise locations please | Neighbourhood Management | Martin Barr |  | 7 panels were identified as damaged. Job number 201511027 has been raised to fix these. | 2015-06-03 | Fully Completed | Martin Barr | 2014-03-26 16:58 | 2014-04-16 17:00 | 2014-03-26 16:58 | 2015-06-04 10:56 | -21 | In target
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:21 | S217008770001 | TRELLICK TOWER | 136799 | Completed | 19c | Information Only | Inspection Regime | The hasp and staple of the wet riser outlet box at the 21st floor level has been damaged, the outlet box is still secured by the padlock. This hasp and staple has been fitted to replaced the broken fixed yale lock on the riser outlet box. | I would recommend that this riser outlet box is checked regularly by the caretakers to see that it is maintained securely locked shut. | Neighbourhood Management | Martin Barr |  | ESA checks this area routinely. The box has remained locked. | 2014-04-25 | Fully Completed |  |  |  | 2014-03-26 17:21 | 2014-04-28 16:57
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:23 | S217008770001 | TRELLICK TOWER | 136800 | Completed | 22 | Information Only | Miscellaneous | When the Metropolitan Police use this building, the roof levels etc during the Notting Hill Carnival. As the building's owners, the TMO must co-ordinate their FRA and its significant findings with another occupier. Especially as the police are increasing the risk of a fire occurring in this building. | I would recommend that the Metropolitan Police are asked for a copy their Fire Risk Assessment (FRA) when they use this building during the Notting Hill Carnival etc. Including the significant finding sheets. | Neighbourhood Management | Kiran Singh |  | Risk assessment provided by the Police and confirmation of public liability insurance. | 2014-08-22 | Fully Completed |  |  |  | 2014-03-26 17:23 | 2014-10-09 17:37
TRELLICK TOWER - 2014.3.6 | 2014-03-26 17:28 | S217008770001 | TRELLICK TOWER | 136803 | Completed | 23c | High | Inspection Regime | Are the monthly occupier tests and inspections of the fire extinguishers, wet riser, the lifts and emergency lighting units and the buildings structural items being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment, lifts emergency lighting etc and the other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | Checks are carried out and recorded as a check to say if they have been carried out. Detail isn't recorded unless an item fails a check. We will be moving to an electronic system for recording checks in future. | 2014-04-25 | Fully Completed | Martin Barr | 2014-03-26 17:28 | 2014-04-16 17:30 | 2014-03-26 17:28 | 2014-04-28 16:59 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 14:52 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181371 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-02 14:52 | 2015-02-23 14:53 | 2015-02-02 14:52 | 2015-05-19 12:12 | -21 | In target
TRELLICK TOWER COMMUNITY ROOM - 2014.6.2014 | 2015-02-02 14:54 | S217008770027 | TRELLICK TOWER COMMUNITY ROOM | 181373 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the fire fighting equipment and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier tests of fire extinguishers and the buildings structure. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2015-02-02 14:54 | 2015-02-23 14:55 | 2015-02-02 14:54 | 2015-05-19 12:13 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 15:44 | S217015000050 | TREVERTON TOWER CLUBROOM | 239867 | Completed | 1 | Information Only | Miscellaneous | Very Important I have used a maximum occupancy number of 60 persons for undertaking this Fire Risk Assessment for this clubroom. | If an occupancy of more than 60 persons is required for this clubroom it is very important that you read the "Any other relevant information on this premises" section on pages 6 and 7 of the Fire Risk Assessment document. If a maximum of 60 persons is acceptable then no actions are required accept from those listed here. Sharon Baah to amend the hire agreements schedule to state the maximum capacity of people is 60 | Neighbourhood Management | Sharon Baah | 2016-02-25 | Hires are informed prior to them hiring the space of the maximum capactiy of 60 people. In addition the schedule on the actual hire agreements also states the maximum capacity. All future publicity material will also state the maximum capacity and it should ne exceeded. | 2015-12-01 | Fully Completed |  |  |  | 2016-01-27 15:44 | 2016-02-03 11:44
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 15:53 | S217015000050 | TREVERTON TOWER CLUBROOM | 239870 | Completed | 2 | High | Signage | There is not a "No Smoking" sign installed in this premises. | Display a No Smoking sign in this premises. | Neighbourhood Management | Sharon Baah | 2016-02-25 | A fire sign has been put up inside the centre | 2016-01-26 | Fully Completed | Sharon Baah | 2016-01-27 15:53 | 2016-02-17 16:04 | 2016-01-27 15:53 | 2016-02-03 11:39 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:06 | S217015000050 | TREVERTON TOWER CLUBROOM | 239886 | Completed | 1(b) | Information Only | Miscellaneous | Advice This premises has recently undergone a refurbishment, including new fire alarm, emergency lighting systems, structural work and electrical wiring work. | Has the Building Regulations final completion certificate been issued for this work? If not I would recommend that one is obtained, this should be kept in the buildings file. Copy to be provided to H&S & SB | Neighbourhood Management | Sarah Lynch | 2016-02-25 | Final completion certificate received | 2016-05-31 | Fully Completed |  |  |  | 2016-01-27 16:06 | 2016-06-01 12:55
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:09 | S217015000050 | TREVERTON TOWER CLUBROOM | 239887 | Active | 1a | High | Miscellaneous | It is not known if an electrical test certificate has been provided by the electrical contractor for the electrical fixed wiring in this building? | Can it please be confirmed that the electrician has provided a fully completed electrical test certificate for the electrical wiring etc within this building stating that the buildings fixed electrical wiring is satisfactory. If they have not I would recommend that one is asked for. Copy to be provided to HS & SB | Neighbourhood Management | Sarah Lynch | 2016-02-25 | Cert has been provided by electrical contractor - to be provided to H&S | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-27 16:09 | 2016-02-17 16:10 |  |  | 386 | 386 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:17 | S217015000050 | TREVERTON TOWER CLUBROOM | 239889 | Completed | 8a | High | Miscellaneous | In the large electrical intake room at the rear of this clubroom is a fridge/freezer. | This fridge/freezer should be removed from this electrical intake room. | Neighbourhood Management | Sharon Baah | 2016-02-25 | The fridge has been removed. | 2016-02-05 | Fully Completed | Sharon Baah | 2016-01-27 16:17 | 2016-02-17 16:21 | 2016-01-27 16:17 | 2016-02-15 20:57 | -21 | In target | 2016-01-27 16:17 | 2016-02-21 20:56 | Janice Wray
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:22 | S217015000050 | TREVERTON TOWER CLUBROOM | 239891 | Completed | 8b | High | Miscellaneous | There are tins of paint and other decorating items in the large electrical intake room at the rear of this clubroom. | All of these items should be removed from this electrical intake room, this is a restricted area for authorised persons only. Move into ESA office? | Neighbourhood Management | Sharon Baah | 2016-02-25 | The paints have been removed. | 2016-02-05 | Fully Completed | Sharon Baah | 2016-01-27 16:22 | 2016-02-17 16:24 | 2016-01-27 16:22 | 2016-02-08 13:35 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:24 | S217015000050 | TREVERTON TOWER CLUBROOM | 239892 | Completed | 13a | High | Miscellaneous | There is an emergency pull cord in the disabled toilet. | Please can it be confirmed that persons using this clubroom will know how this system works? How to reset it etc? A Display sign to be put up to inform people where the reset button is | Neighbourhood Management | Sharon Baah | 2016-02-25 | The resent button lable is on, hirers will be shown how to operate the disable alarm prior to them hiring the community centre | 2016-02-05 | Fully Completed | Sharon Baah | 2016-01-27 16:24 | 2016-02-17 16:26 | 2016-01-27 16:24 | 2016-02-15 20:59 | -21 | In target | 2016-01-27 16:24 | 2016-02-21 20:59 | Janice Wray
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:33 | S217015000050 | TREVERTON TOWER CLUBROOM | 239895 | Active | 13b | High | Miscellaneous | There is an emergency pull cord in the disabled toilet. | Can it be confirmed that a commissioning certificate has been handed over for this emergency pull cord system? If not one should be asked for. Copy of cert to be provided to H&S & SB | Neighbourhood Management | Sarah Lynch | 2016-02-25 | Cert has been provided by electrical contractor - copy to be passed to H&S | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-27 16:33 | 2016-02-17 16:34 |  |  | 386 | 386 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:35 | S217015000050 | TREVERTON TOWER CLUBROOM | 239897 | Active | 15a | High | Emergency Lighting | There is an emergency lighting system/units installed in this clubroom, has the electrical contractor provided an emergency lighting commissioning certificate for this system? | Can it please be confirmed that the certificates as required by BS 5266 Part 1 2011 have been obtained from the electrical contractor who installed the emergency lighting in this property. If they have not then the certificates as per the model certificate in the British Standard should be asked for from the contractor. | Neighbourhood Management | Sarah Lynch | 2016-02-25 | cert has been provided to Sarah by electrical contractor - copy to be given to H&S | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-27 16:35 | 2016-02-17 16:36 |  |  | 386 | 386 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:37 | S217015000050 | TREVERTON TOWER CLUBROOM | 239898 | Active | 15b | High | Emergency Lighting | There is an emergency lighting system/units installed in this clubroom, has the electrical contractor provided marked up drawings showing the "as installed" system/units? | Can it please be confirmed that the electrical contractor has provide the as installed marked up drawings as required by BS 5266 Part 1 2011. If the drawings have not been provided then they should be asked for from the contractor. | Neighbourhood Management | Sarah Lynch | 2016-02-25 | Request made tocntractor - once received will be passed to H&S | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-27 16:37 | 2016-02-17 16:38 |  |  | 386 | 386 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-27 16:55 | S217015000050 | TREVERTON TOWER CLUBROOM | 239904 | Completed | 16b | High | Signage | There were no fire action notices displayed next to the 2 fire alarm system break glass call points of this clubroom at the time of my visit. | Fire action notices should be displayed next to each of the 2 fire alarm system break glass call points in this clubroom. PC to up fire action notices | Neighbourhood Management | Sharon Baah | 2016-02-25 | A fire action notice has been placed inside the entrance of the building next to the fire alarm. | 2016-01-26 | Fully Completed | Sharon Baah | 2016-01-27 16:55 | 2016-02-17 16:57 | 2016-01-27 16:55 | 2016-02-03 16:35 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 15:54 | S217015000050 | TREVERTON TOWER CLUBROOM | 240126 | Completed | 17a | High | Fire Alarm | There is no zone diagram/plan next to the fire alarm system control panel. | A zone diagram/plan should be displayed next to the fire alarm system control panel as required by the BS. | Neighbourhood Management | Sharon Baah | 2016-02-26 | It's a one room unit, access and exit is via the same door. | 2016-06-08 | Fully Completed | Sharon Baah | 2016-01-28 15:54 | 2016-02-18 15:56 | 2016-01-28 15:54 | 2016-06-09 21:10 | -21 | In target | 2016-01-28 15:54 | 2016-06-15 21:09 | Janice Wray
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 15:56 | S217015000050 | TREVERTON TOWER CLUBROOM | 240129 | Active | 17b | High | Miscellaneous | Certificates etc for the premises new fire alarm system. | Can it please be confirmed that the certificates etc as required by BS 5839 Part 1 :2013 have been obtained from the contractor who installed the fire alarm system. If they have not then these should be asked for, these certificates should be the same as the model standard ones in annex H of BS 5839 Part 1 2013, certificates H1 to H5 as appropriate, fully completed by a competent quailed fire alarm engineer. Sarah Lynch | Neighbourhood Management | Sarah Lynch | 2016-02-26 | Contractor requested to provide certs and drawings. | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-28 15:56 | 2016-02-18 15:58 |  |  | 385 | 385 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 15:59 | S217015000050 | TREVERTON TOWER CLUBROOM | 240132 | Active | 17c | High | Fire Alarm | Has the fire alarm contractor provided the "as installed" drawings etc for this system as required by the British Standard? With audibility level readings marked on them. | Please can it be confirmed that the fire alarm contractor has provided the "as installed" drawings for the fire alarm system as required by the British Standard? If not then a set of as installed drawing should be obtained from the fire alarm system installer. | Neighbourhood Management | Sarah Lynch | 2016-02-26 | As installed FA drawings requested from contractor | 2017-03-08 | Partially Completed | Janice Wray | 2016-01-28 15:59 | 2016-02-18 16:00 |  |  | 385 | 385 days overdue
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 16:01 | S217015000050 | TREVERTON TOWER CLUBROOM | 240133 | Completed | 17d | High | Fire Alarm | The fire alarm system's control panel is located on the rear wall of this clubroom, this is technically correct as this panel is in sight of the entrance door, but the panel cannot be read unless somebody goes to the furthest point of the room away from the entrance/exit door. Therefore endangering a person who has to go to this panel to read any information is the panel activates. | I would recommend that the fire alarm contractor is asked why the fire alarm control panel has been positioned at the furthest point away from the entrance/exit door of this clubroom and not by the entrance/exit door. | Neighbourhood Management | Sarah Lynch | 2016-02-26 | in situ and work handed over so need to live with ezisting position. Not ideal but can be seen from entrance door | 2016-05-31 | Fully Completed | Janice Wray | 2016-01-28 16:01 | 2016-02-18 16:04 | 2016-01-28 16:01 | 2016-06-01 12:58 | -21 | In target
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 16:04 | S217015000050 | TREVERTON TOWER CLUBROOM | 240134 | Completed | 17e | Information Only | Fire Alarm | It appears this premises fire alarm system is not remotely monitored. Can it please be confirmed if this premises fire alarm system is remotely monitored or not? | If it is not will it be remotely monitored? | Neighbourhood Management | Sharon Baah | 2016-02-26 | Currently no plans to remotely monitor the fire alarm in this clubroom. To be reviewed as usage increases | 2016-02-14 | Fully Completed |  |  |  | 2016-01-28 16:04 | 2016-02-15 21:02 |  |  | 2016-01-28 16:04 | 2016-02-21 21:00 | Janice Wray
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 16:16 | S217015000050 | TREVERTON TOWER CLUBROOM | 240141 | Completed | 23a | High | Inspection Regime | Are the weekly occupier's tests of the premises fire alarm system being undertaken. | Weekly testing of the buildings fire alarm system should be undertaken with the tests and any results recorded in the building fire logbook. | Neighbourhood Management | Sharon Baah | 2016-02-26 | This action is undertaken as part of the weekly test which is carried out on the checklist. | 2016-02-14 | Fully Completed | Sharon Baah | 2016-01-28 16:16 | 2016-02-18 16:18 | 2016-01-28 16:16 | 2016-02-15 21:04 | -21 | In target | 2016-01-28 16:16 | 2016-02-21 21:03 | Janice Wray
TREVERTON CLUBROOM - 2015.11.19 | 2016-01-28 16:19 | S217015000050 | TREVERTON TOWER CLUBROOM | 240143 | Completed | 23b | High | Inspection Regime | Will the monthly inspections, checks and tests of the fire equipment, emergency lighting and checks on the buildings structure as per the caretakers checklist be undertaken. | Monthly inspections and tests of the buildings fire equipment, emergency lighting and checks on the buildings structure as per the caretakers check list should be undertaken and the results recorded as proof of testing. | Neighbourhood Management | Sharon Baah | 2016-02-26 | Regular weekly checks are taking place following a check list which is similar to a caretakers check list. | 2016-01-26 | Fully Completed | Sharon Baah | 2016-01-28 16:19 | 2016-02-18 16:20 | 2016-01-28 16:19 | 2016-02-15 21:06 | -21 | In target | 2016-01-28 16:19 | 2016-02-21 21:05 | Janice Wray
TREVERTON TOWER - 2014.5.28 | 2014-06-11 16:11 | S217010420001 | TREVERTON TOWER | 148249 | Completed | 12a | Medium | Communal Area Storage | On going Outside flats 42 and 43 there are a lot of plants but not an excessive amount, presently these plants are not restricting the width of the balcony or causing an obstruction/trip hazard. | I would recommend that the caretaker is asked to regularly check this balcony to make certain that the plants do not become obstruct the balcony or reduce the width of the balcony so that persons can freely move along it. Lf the balcony becomes overloaded with plants then so must be removed. | Neighbourhood Management | Martin Barr |  | Tenants have agreed to keep walkway clear. It is not obstructed | 2015-06-03 | Fully Completed | Martin Barr | 2014-06-11 16:11 | 2014-08-10 16:45 | 2014-06-11 16:11 | 2015-06-04 13:24 | -60 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:06 | S217010420001 | TREVERTON TOWER | 148283 | Completed | 12a | Medium | Communal Area Storage | On going Outside flats 42 and 43 there are a lot of plants but not an excessive amount, presently these plants are not restricting the width of the balcony or causing an obstruction/trip hazard. | I would recommend that the caretaker is asked to regularly check this balcony to make certain that the plants do not become obstruct the balcony or reduce the width of the balcony so that persons can freely move along it. Lf the balcony becomes overloaded with plants then so must be removed. | Neighbourhood Management | Martin Barr |  | Tenants have agreed to keep walkway clear. It is not obstructed | 2015-06-03 | Fully Completed | Martin Barr | 2014-06-11 17:06 | 2014-07-02 17:07 | 2014-06-11 17:06 | 2015-06-04 13:24 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:11 | S217010420001 | TREVERTON TOWER | 148287 | Completed | 12d | Information Only | Communal Area Storage | The metal security gate fitted in front of the flat entrance door of flat 36 has been removed and is now propped against the wall of the building. | I would recommend that if this security gate is now not being used it is removed from outside this flat. | Neighbourhood Management | Martin Barr |  | Order raised to remove and dispose of gate | 2015-06-03 | Fully Completed |  |  |  | 2014-06-11 17:11 | 2015-06-04 13:25
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:20 | S217010420001 | TREVERTON TOWER | 148292 | Completed | 16a | High | Signage | In the basement level cleaners and caretakers area somebody has displayed "Fire door Keep Shut" signs on most the doors at this level. These doors do not appear to be fire doors or if they are fire doors then there are large gaps and hole in the walls above or beside these doors. | I would recommend that the "Fire door Keep Shut" signs displayed on the doors in the basement level cleaners and caretakers area are removed (Alternatively all the doors could be changed for certified 30 minute fire rated doors and all the gaps and holes in the walls above and beside the doors could be filled with a suitable fire rated material.) | Neighbourhood Management | Martin Barr |  | The signs have been removed as suggested | 2015-06-03 | Fully Completed | Martin Barr | 2014-06-11 17:20 | 2014-07-02 17:22 | 2014-06-11 17:20 | 2015-06-04 13:29 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:29 | S217010420001 | TREVERTON TOWER | 148296 | Completed | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2014-06-11 17:29 | 2014-07-02 17:30 | 2014-06-11 17:29 | 2015-05-19 12:14 | -21 | In target
TREVERTON TOWER - 2014.5.28 | 2014-06-11 17:31 | S217010420001 | TREVERTON TOWER | 148297 | Completed | 23c | High | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretaker is undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs complete all checks as agreed with H&S team. This includes testing of emergency lighting systems on a monthly basis where we have been made aware of them and the location of the testing point. All records are now submitted & logged electronically. | 2015-04-07 | Fully Completed | Martin Barr | 2014-06-11 17:31 | 2014-07-02 17:32 | 2014-06-11 17:31 | 2015-05-19 12:14 | -21 | In target
WALMER HOUSE - 2015.08.13 | 2015-09-02 12:23 | S217008220003 | WALMER HOUSE | 214518 | Completed | 12b | Information Only | Inspection Regime | There are a lot of plants on the balcony outside flat 12. | I would recommend that the caretaker is asked to check this area each time he undertakes a visit to this building to make certain that the occupants of flat 12 can use the balcony easily and that the balcony is not obstructed by the plants. | Neighbourhood Management | Martin Barr |  | ESA has checked and spoken to residents involved. It doesn't affect any other flat/resident. | 2015-10-01 | Fully Completed |  |  |  | 2015-09-02 12:23 | 2015-10-16 10:27
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:04 | S217005570001 | WALNUT TREE HOUSE | 103458 | Completed | 8a | High | Inspection Regime | In the electrical cupboard of the left hand side central staircase at the ground floor level there are cardboard boxes of old light fittings and other pieces of old electrical equipment. | All the cardboard boxes and old light fittings etc should be removed from this cupboard immediately. | Neighbourhood Management | Wendy Stevenson | 2013-09-10 | Removed a long time ago, as per ESA John Whall. | 2013-09-10 | Fully Completed | Wendy Stevenson | 2013-08-23 11:04 | 2013-09-13 11:06 | 2013-08-23 11:04 | 2013-09-11 14:31 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:06 | S217005570001 | WALNUT TREE HOUSE | 103459 | Completed | 8b | High | Inspection Regime | In the bin yard by flat 1 there is a three piece suite, settee and 2 chairs plus other items of furniture and old suitcases. | All the furniture and other household items should be removed from this bin yard and the gate secured locked shut so that persons cannot dump bulk items in this area. | Neighbourhood Management | Wendy Stevenson | 2013-09-10 | Actioned a long time ago - via ESA John Whall. | 2013-09-10 | Fully Completed | Wendy Stevenson | 2013-08-23 11:06 | 2013-09-13 11:08 | 2013-08-23 11:06 | 2013-09-11 14:32 | -21 | In target
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 11:08 | S217005570001 | WALNUT TREE HOUSE | 103460 | Completed | 10 | High | Communal Area Storage | On the external balcony of I believe flat 10 there is a BBQ and gas cylinder it is likely that this occupant uses this BBQ on the balcony. This is a high fire risk item and a fire hazard. I believe that cooking on a BBQ on a flat balcony is not allowed under the tenancy agreement. | I would recommend that the BBQ and gas cylinder are removed from this balcony area immediately. | Neighbourhood Management | Wendy Stevenson | 2013-09-13 | Forwarded to Neighbourhood Officer Svetlena Koleva, as this is a tenancy issue. SK - Letter dated 9/09/13 sent to the tenant with a request the BBQ and gas cylinder are removed from his balcony area immediatelly quoting relevant parts of his tenancy agreement. Tenant advised that the ESA will be inspection the property in order to provide a report on the situation. Also, t/c to the tenant to discuss the matter, no answer. Message on his mobile to contact me back as soon as possible. | 2013-09-06 | Fully Completed | Wendy Stevenson | 2013-08-23 11:08 | 2013-09-13 11:33 | 2013-08-23 11:08 | 2013-09-24 10:30 | -21 | In target | 2013-08-23 11:08 | 2013-09-16 09:31 | Svetlena Koleva
WALNUT TREE HOUSE-2013.07.30 | 2013-08-23 12:30 | S217005570001 | WALNUT TREE HOUSE | 103508 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the building being undertaken along with the other items on the caretaker's checklist, with records kept? | Monthly occupier testing and inspections of the fire fighting equipment and other building structural items should be undertaken as per the caretaker's checklist. With the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2013-09-13 | Inspections and tests are being done, although ESA does not know how to do electrical testing. Results recorded and retained. | 2013-09-10 | Fully Completed | Wendy Stevenson | 2013-08-23 12:30 | 2013-09-13 12:31 | 2013-08-23 12:30 | 2013-09-11 13:37 | -21 | In target
WESTFIELD HOUSE - 2015.01.28 | 2015-02-03 11:21 | S217012760001 | WESTFIELD HOUSE | 181544 | Completed | 3 | Information Only | Inspection Regime | The bin storage area for this building is located internally in a purpose built cupboard/ room off the ground floor entrance hall/lobby area, at the base of the staircase. | I would recommend that the caretaker regularly checks to see that the door to this bin storage area is secured shut at all times. | Neighbourhood Management | Wendy Stevenson |  | Jimmy Lemos has provided photo to connfrim this door is now secured with a lock | 2015-10-09 | Fully Completed |  |  |  | 2015-02-03 11:21 | 2015-10-12 13:27 |  |  | 2015-02-03 11:21 | 2015-10-16 13:27 | Janice Wray
WHISTLER TOWER, BLANTYRE STREET, LONDON SW10 0ED - 2016.07.28 | 2016-09-20 15:48 | S217012740010 | WHISTLER TOWER 1-61 | 271006 | Completed | 2 | High | Inspection Regime | On the flat/lift lobby area by the lift on the floor level by flats 43 and 44 there are used cigarette ends on the floor and other discarded, used smoking materials. | All used smoking material and cigarette ends etc should be removed from this flat/lift lobby area. The residents on this floor level should be informed of the TMO's no smoking policy. | Neighbourhood Management | Nicola Rees | 2016-10-18 | Email sent to Gary with deadline of 14.10.16 to provide feedback. Items were removed and door knock completed | 2017-01-13 | Fully Completed | Nicola Rees | 2016-09-20 15:48 | 2016-10-11 15:54 | 2016-09-20 15:48 | 2017-01-16 10:43 | -21 | In target
WHISTLER TOWER, BLANTYRE STREET, LONDON SW10 0ED - 2016.07.28 | 2016-09-20 15:58 | S217012740010 | WHISTLER TOWER 1-61 | 271008 | Active | 8b | Medium | Inspection Regime | A timber ramp has been installed up to the entrance door of flat number 43 the side of this ramp is in front of the entrance door of flat 44 as well. This could be a trip hazard. | Are the TMO aware of this ramp and is the TMO Health and Safety team happy with the positioning of the ramp? | Neighbourhood Management | Nicola Rees | 2016-12-06 | Email sent to Gary to take photos and advise if trip hazard. This has been forward to H+S. Please advise of further action from Estate services. Adrian visited and advises that there is a lot of evidence of smoking in and around (and possibly underneath) this ramp - is it possibly to lift it and thoroughly clean under it and replace into a position so that it isn't possible for smokers materials to get underneath? | 2017-01-16 | Partially Completed | Nicola Rees | 2016-09-20 15:58 | 2016-11-19 15:59 | 2016-09-20 15:58 | 2017-01-19 12:05 | -60 | In target | 2016-09-20 15:58 | 2017-01-25 12:02 | Janice Wray
WHISTLER TOWER, BLANTYRE STREET, LONDON SW10 0ED - 2016.07.28 | 2016-09-20 16:43 | S217012740010 | WHISTLER TOWER 1-61 | 271019 | Completed | 23d | High | Inspection Regime | Are the monthly occupier tests and inspections of the emergency lighting system and checks on the fire extinguishers in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Nicola Rees | 2016-10-18 | There are some performance management issues with this ESA in terms of consistency and completing these. There is an action plan around these and regular meetings. | 2017-01-13 | Fully Completed | Nicola Rees | 2016-09-20 16:43 | 2016-10-11 16:45 | 2016-09-20 16:43 | 2017-01-16 10:51 | -21 | In target
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:11 | S217012740010 | WHISTLER TOWER 1-61 | 102278 | Completed | 8a | Medium | Communal Area Storage | There is contractors waste and combustible material (cardboard boxes with rubbish in them) stored in both riser cupboards on the 1st and 4th floor levels and household items and old kitchen units etc stored in the in the double riser cupboards on the 11th floor level flat/lift lobby and old light fitting in the single riser cupboard on the 17th floor level flat/lift lobby area. | I would recommend that all the contractors waste and other material are removed from these riser cupboards. I would also recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all waste etc has been removed from site. | Neighbourhood Management | Wendy Stevenson | 2013-10-23 | Bulk clearance arranged today - 13th Oct. Update 23rd Oct 2013 - items still in place because padlocks faulty. Repair orders will be raised so that then clearances can be arranged. Update 01.11.13 - all items cleared except 1st floor. Clearance to be arranged by ESA. | 2014-01-07 | Fully Completed | Wendy Stevenson | 2013-08-16 15:11 | 2013-10-15 15:14 | 2013-08-16 15:11 | 2014-01-08 10:45 | -60 | In target | 2013-08-16 15:11 | 2014-01-14 10:45 | Janice Wray
WHISTLER TOWER-2013.04.01 | 2013-08-16 15:14 | S217012740010 | WHISTLER TOWER 1-61 | 102280 | Completed | 8b | Medium | Communal Area Storage | On the 14th and 15th floor level flat/lift lobby areas there are household items, bedroom units and pieces of wooden beds or metal cabinets being stored. | These household items etc should be removed from these flat/lift lobby areas | Neighbourhood Management | Wendy Stevenson | 2013-10-15 | Items already gone upon inspection today. | 2013-10-16 | Fully Completed | Wendy Stevenson | 2013-08-16 15:14 | 2013-10-15 15:20 | 2013-08-16 15:14 | 2013-10-17 14:25 | -60 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:23 | S217009090002 | WHITCHURCH HOUSE | 142377 | Completed | 12c | Medium |  | Outside flat 38 in the corridor there are considerable amount of plants in pots and large planters. As present these are not restricting the width of the corridor nor are they causing an obstruction or trip hazard. | I would recommend that warden is asked to regularly check the corridor outside flat 38 to make certain that the plants do not become a trip hazard or obstruct the corridor. If they do then some of them should be removed and if this is an issue with the resident of the flat then all the plants should be removed. Jacqueline Bull - to monitor | Neighbourhood Management | Hash Chamchoun | 2014-04-01 | JB monitoring as per agreed actions. | 2014-04-01 | Fully Completed | Hash Chamchoun | 2014-05-06 14:23 | 2014-07-05 14:28 | 2014-05-06 14:23 | 2014-05-13 11:24 | -60 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:38 | S217009090002 | WHITCHURCH HOUSE | 142390 | Completed | 17 | High | Fire Alarm | Currently there are no automatic fire detection devices fitted in the store cupboards/rooms off the corridors, 1 per floor level. These rooms present have storage in them, this issue was highlighted by the Fire Officer during his audit and on the Deficiency Notice issued after his audit. | If these rooms were to be used for storage etc the buildings fire alarm system should be extended so that automatic fire detection devices are fitted in these cupboards/rooms. Alternatively the rooms can be emptied out and kept secured locked shut and empty at all times. Jacqueline Bull Can the storage be removed from these areas? | Neighbourhood Management | Hash Chamchoun | 2014-05-12 | JB confirmed store rooms have been emptied and secured. | 2014-05-12 | Fully Completed | Hash Chamchoun | 2014-05-06 14:38 | 2014-05-27 14:40 | 2014-05-06 14:38 | 2014-05-13 11:26 | -21 | In target
WHITCHURCH HOUSE - 2014.4.7 | 2014-05-06 14:48 | S217009090002 | WHITCHURCH HOUSE | 142399 | Completed | 21b | High | Miscellaneous | There are automatic opening ventilation units/smoke control installed on the windows in the corridors of this building. | Have all of the staff employed in this building been given specific instructions on how to use these installed units and how the units interface with the fire alarm system including making certain that the windows that open are not obstructed with pots of plants etc. | Neighbourhood Management | Hash Chamchoun | 2014-05-12 | On site SHO aware of how units operate and interface with fire alarm system. SHO tests system weekly and monitors to ensure windows automatically close after each test. Outstanding actions to be picked up by H&S Team: Arrange for on site SHO to have key for the vent controls. Check that local caretaker has been instructed. | 2014-05-12 | Fully Completed | Hash Chamchoun | 2014-05-06 14:48 | 2014-05-27 14:49 | 2014-05-06 14:48 | 2014-05-13 12:31 | -21 | In target | 2014-05-06 14:48 | 2014-05-19 12:31 | Janice Wray
WHITSTABLE HOUSE, SILCHESTER WAY, LONDON W10 6SB - 2016.01.21 | 2016-05-19 09:08 | S217009980001 | WHITSTABLE HOUSE | 261316 | Active | 12g | High | Inspection Regime | There are cold smoke seals fitted to the self closing fire doors off the flat/lift lobby areas to the refuse chute balcony and on to the lobby area before the staircase and on to the staircase. Some of these cold smoke seals are damaged or there are pieces missing. | As the TMO have fitted fire doors with cold smoke seals to these areas they must be maintained to the standard as when the doors were installed. All missing and damaged cold smoke seals should be replaced. Os has agreed to include in his inspections | Neighbourhood Management | Louise Nezandonyi | 2016-06-17
WHITSTABLE HOUSE, SILCHESTER WAY, LONDON W10 6SB - 2016.01.21 | 2016-05-19 09:14 | S217009980001 | WHITSTABLE HOUSE | 261318 | Active | 14a | High | Inspection Regime | On the 1st floor flat/lift lobby area where the dry riser is located on the upper floor levels there are pieces of boarded placed in the duct riser. | These pieces of boarding are badly fitted and damaged. I would recommend that the boarding on this 1st floor level area is repaired or new boarding installed. Could Os please check and raise order as necessary | Neighbourhood Management | Louise Nezandonyi | 2016-06-17
WHITSTABLE HOUSE, SILCHESTER WAY, LONDON W10 6SB - 2016.01.21 | 2016-05-19 09:17 | S217009980001 | WHITSTABLE HOUSE | 261322 | Active | 14b | High | Inspection Regime | There are metal cover plates fixed over a cable duct on the flat/lift lobby areas which provide fire stopping for the duct. It appears that contractors have removed these metal cover plates on most floor levels and not secured them back again fully thus compromising the fire stopping of the walls surface. These metal plates are heavy sheets of metal and might also fall off the wall and cause a serious injury if they were to hit a person. | These metal cover plates should be re-fixed securely back to the wall so providing suitable fire stopping for the cable duct and also to stop these heavy metal plates from falling on somebody. I would recommend that in future checks are carried out after contractors have undertaken work in the building to make certain that all the structural elements of the buildings remain fire rated. Os has agreed to check & make good | Neighbourhood Management | Louise Nezandonyi | 2016-06-17
WHITSTABLE HOUSE, SILCHESTER WAY, LONDON W10 6SB - 2016.01.21 | 2016-05-19 09:33 | S217009980001 | WHITSTABLE HOUSE | 261332 | Active | 23b | High | Inspection Regime | Are the monthly occupier tests and inspections of the installed emergency lighting units, fire extinguishers and sprinkler system in this building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting and sprinkler systems in this building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Louise Nezandonyi | 2016-06-17
WHITSTABLE HOUSE, SILCHESTER WAY, LONDON W10 6SB - 2016.01.21 | 2016-05-19 09:38 | S217009980001 | WHITSTABLE HOUSE | 261335 | Active | 23d | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Louise Nezandonyi | 2016-06-17
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:14 | S217012746601 | WORLDS END ESTATE CAR PARK | 134331 | Completed |  | High |  | There are plant and electrical rooms and areas are located off the open car park area, access to these plant and electrical rooms is needed at all times, night and day in case of an emergency situation in the residential areas above. | If at any time in the future this car park is not used by the TMO or under its control I would recommend that a legal "right of way" or "way leave" agreement is completed with any new operators so that the TMO has the legal right to access the car park at any time night or day in an emergency situation. Keys or codes to doors etc will need to be available in the Worlds Ends concierge's office for the emergency services. This is so that there is access to all of the electrical and plant room areas located off this ground floor level car park. | Neighbourhood Management | Nick Rendle | 2014-03-31 | We will ensure that any future lease, should such be entered into, will include access provisions as outlined above. Note that there are no such proposals at the present time. | 2014-03-31 | Fully Completed | Nick Rendle | 2014-03-12 16:14 | 2014-04-02 16:17 | 2014-03-12 16:14 | 2014-04-01 15:15 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:17 | S217012746601 | WORLDS END ESTATE CAR PARK | 134332 | Completed |  | High | Miscellaneous | There were persons smoking and drinking in this car park at the time this assessment was being undertaken. | This was reported to the TMO's Health and Safety team. | Neighbourhood Management | Olivia Hutchison |  | There is no CCTV in car park however i have asked the ESAs to monitor this area. | 2014-03-14 | Fully Completed | Olivia Hutchison | 2014-03-12 16:17 | 2014-04-02 16:26 | 2014-03-12 16:17 | 2014-03-17 15:27 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 16:40 | S217012746601 | WORLDS END ESTATE CAR PARK | 134345 | Completed | 2 | High | Smoking In Communal Area | ]Whilst the assessment of this car park was being undertaken a group of 6 to 7 men were smoking and drinking at the rear of a car in this car park. The boot area of the car was being used to hold bottles of drink and food. This is a car parking area with "No Smoking " signs displayed, I asked the men not to smoke but was ignored. This information on the smoking and drinking was passed on to the TMO's Health and Safety team whilst I was at this building. | This is a car park where cars have petrol in them, I would recommend that the No Smoking requirements in this area are enforced. | Neighbourhood Management | Olivia Hutchison |  | There is no CCTV in car park however i have asked the ESAs to monitor this area. | 2014-03-14 | Fully Completed | Olivia Hutchison | 2014-03-12 16:40 | 2014-04-02 16:41 | 2014-03-12 16:40 | 2014-03-17 15:26 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:02 | S217012746601 | WORLDS END ESTATE CAR PARK | 134353 | Completed | 9b | High | Inspection Regime | At the time of this assessment contractors waste and materials are spread widely around this car park. | I would recommend that the TMO caretakers are asked to inspect this car park regularly to see that none of the pedestrian/emergency exits from the car park are obstructed by contractors waste or materials. This also includes access to electrical rooms the means of escape route/staircase from the car park with contractor's materials or waste etc. | Neighbourhood Management | Wendy Stevenson |  | Full inspection sheet took place 20th March 2014 - Gary Chin-Fatt and his manager Wendy Stevenson. A number of issues were noted, mostly Apollo contractors materials and bulk refuse. The ESA has been instructed to dfo at least a monthly check in future, noting all findings and taking necessary action. | 2014-03-20 | Fully Completed | Wendy Stevenson | 2014-03-12 17:02 | 2014-04-02 17:03 | 2014-03-12 17:02 | 2014-03-24 11:01 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:03 | S217012746601 | WORLDS END ESTATE CAR PARK | 134354 | Completed | 9c | High | Miscellaneous | At the time of this assessment contractors waste and materials are spread widely around this car park. | I would recommend that the TMO caretakers are asked to inspect this car park regularly to check that access to all of the plant and electrical rooms etc are freely available with no plant or electrical room doors obstructed this contractors materials or waste etc. | Neighbourhood Management | Wendy Stevenson | 2015-04-02 | Rolls of vinyl flooring are being stored in the vestibule to one of the plant rooms. To be issued to Simon Girling please - in charge of kitchen and bathroom works on site. | 2014-03-21 | Fully Completed | Wendy Stevenson | 2014-03-12 17:03 | 2014-04-02 17:04 | 2014-03-12 17:03 | 2014-03-24 10:58 | -21 | In target
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:08 | S217012746601 | WORLDS END ESTATE CAR PARK | 134358 | Completed | 12 | High | Miscellaneous | Some of the doors to the plant rooms etc are damaged and do not shut fully or cannot be secured shut, ie the bin room door. | I would recommend that a full check of all of the plant, electrical and bin room doors is undertaken and any damaged doors should be repaired or replaced and any locks repaired etc so that these rooms can be secured locked shut. | Neighbourhood Management | Wendy Stevenson |  | Can it be clarified which bin room door? The Whistler Tower bin room door was unlocked, but appeared to have been left so by the OCS contractors. The ESA was instructed to lock up and to remind the OCS contractors in future. Update 11th July 2014 - all completed. | 2014-07-11 | Fully Completed | Wendy Stevenson | 2014-03-12 17:08 | 2014-04-02 17:09 | 2014-03-12 17:08 | 2014-07-14 17:36 | -21 | In target | 2014-03-12 17:08 | 2014-03-28 12:58 | Wendy Stevenson
WORLDS END CAR PARK GROUND FLOOR BLANTYRE STREET - 2014.02.25 | 2014-03-12 17:27 | S217012746601 | WORLDS END ESTATE CAR PARK | 134375 | Completed | 23d | High | Inspection Regime | Monthly caretaker testing and inspections of the emergency lighting units and the buildings structure. | Can it be confirmed that the caretakers are undertaking the monthly occupier's inspections as per the caretakers check list. Monthly occupiers tests of the installed systems/equipment/fittings etc must be undertaken with the completed sheets kept as a record. | Neighbourhood Management | Wendy Stevenson | 2014-05-02 | Commenced 20th March 2014 | 2014-03-20 | Fully Completed | Wendy Stevenson | 2014-03-12 17:27 | 2014-04-02 17:29 | 2014-03-12 17:27 | 2014-03-24 11:02 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:41 |  |  | 122463 | Completed | 8b | High | Communal Area Storage | There is a pile of old light fittings on the floor in the secondary exit corridor underneath the extractor switches. | These old light fittings should be removed. | Neighbourhood Management | Wendy Stevenson | 2014-01-24 | Light fitting items removed from the fire exit area, altho wider area susceptible to overload as used for estate bulk refuse storage until collection. ESA has been asked to raise regular bulk clearances to keep the area accessible. | 2014-01-30 | Fully Completed | Wendy Stevenson | 2014-01-03 11:41 | 2014-01-24 11:42 | 2014-01-03 11:41 | 2014-01-31 14:02 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:46 |  |  | 122468 | Completed | 23a | High | Fire Alarm | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? | Can it be confirmed that the concierge or the caretaker(s) are undertaking the weekly occupiers testing of the fire alarm system as the only record of any testing in the fire alarm logbook is for the 3rd of September 2013. If weekly testing is not being undertaken it should start immediately with the results recorded as proof of the inspections having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2014-01-24 | The ESA wasn't aware he had to inspect this area as it is closely managed by WERA. However, he will now be regularly inspecting and recording the details. The correct logbook has been obtained and testing devices (fire alarm) provided. | 2014-01-16 | Fully Completed | Wendy Stevenson | 2014-01-03 11:46 | 2014-01-24 11:48 | 2014-01-03 11:46 | 2014-01-17 15:43 | -21 | In target
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:50 |  |  | 122471 | Completed | 23c | High | Emergency Lighting | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? | Monthly occupier testing and inspections of the emergency lighting system in the building should be undertaken, with the results recorded as proof of testing having been undertaken. | Neighbourhood Management | Wendy Stevenson | 2014-01-24 | ESA's don't know how to test the emergency lighting. Training arranged for 4th Feb 2014 - then reguakr testing will be undertaken and recorded. | 2014-01-06 | Fully Completed | Wendy Stevenson | 2014-01-03 11:50 | 2014-01-24 11:52 | 2014-01-03 11:50 | 2014-01-08 10:43 | -21 | In target | 2014-01-03 11:50 | 2014-01-14 10:42 | Janice Wray
WORLDS END RESIDENTS ASSOCIATION CLUB ROOM (WERA) - -2014.01.03 | 2014-01-03 11:52 |  |  | 122472 | Completed | 23d | Medium | Inspection Regime | Caretaker testing and inspections of the buildings structure etc. | Can it be confirmed that the caretakers are undertaking the tasks as per the caretakers check list in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Wendy Stevenson | 2014-03-04 | Inspections had not previously been done by estate staff as it was believed that this area was private to the residents' association. The ESA will now be makling regular inspections and noting any findings. | 2014-01-15 | Fully Completed | Wendy Stevenson | 2014-01-03 11:52 | 2014-03-04 11:53 | 2014-01-03 11:52 | 2014-01-16 11:00 | -60 | In target
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 13:25 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215923 | Completed | 2 | Medium | Signage | There are not any "No Smoking" signs displayed in the entrance lobby areas of these buildings. | "No Smoking" sign's should be displayed in each entrance lobby area of these buildings. | Neighbourhood Management | Martin Barr |  | Signs have been replaced | 2015-10-01 | Fully Completed | Martin Barr | 2015-09-10 13:25 | 2015-11-09 13:27 | 2015-09-10 13:25 | 2015-10-16 11:01 | -60 | In target
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 14:57 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215957 | Completed | 4 | Medium | Inspection Regime | Some of the doors of the wall mounted gas meter boxes for these dwellings gas meters are missing or are damaged. | I would recommend that new doors are fitted to any gas meter boxes where they are missing or damaged. | Neighbourhood Management | Martin Barr |  | ESA has reported these for repair | 2015-10-01 | Fully Completed | Martin Barr | 2015-09-10 14:57 | 2015-11-09 14:58 | 2015-09-10 14:57 | 2015-10-16 11:01 | -60 | In target
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 14:58 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215958 | Completed | 8a | High | Inspection Regime | In most of the electrical rooms/cupboards there is storage, from cardboard boxes of old light fittings to car parts in the one by flat 10's entrance door. | All of the electrical rooms/cupboards should be emptied out of all storage. | Neighbourhood Management | Martin Barr |  | Cleaning contractors have cleared items | 2015-10-01 | Fully Completed | Martin Barr | 2015-09-10 14:58 | 2015-10-01 15:00 | 2015-09-10 14:58 | 2015-10-16 11:02 | -21 | In target
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 15:00 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215960 | Completed | 8b | High | Inspection Regime | In some of the entrance lobby areas in the alcoves beside the staircase entrance doors there are suitcases and other combustible items being stored. As well as push chairs and push bikes. | All of the combustible items should be removed from this lobby areas, the push chairs and push bikes can remain but these must not block the entrance doors or the stairs. | Neighbourhood Management | Martin Barr | 2016-01-29 | ESA has confirmed that all combustible items have been removed | 2016-02-08 | Fully Completed | Louise Nezandonyi | 2015-09-10 15:00 | 2015-10-01 15:01 | 2015-09-10 15:00 | 2016-02-09 13:58 | -21 | In target | 2015-09-10 15:00 | 2016-01-20 21:43 | Louise Nezandonyi
WORNINGTON ROAD FLATS 2 TO 20 AND 22 TO 50, EVEN NUMBERS ONLY - 2015.08.27 | 2015-09-10 15:08 | S217010657703 | WORNINGTON ROAD EVEN (2-20) | 215969 | Completed | 23 | High | Inspection Regime | Caretaker testing and inspections of the buildings structure. | Can it be confirmed that the caretaker(s) are undertaking the monthly occupier checks as per the caretakers check list ,in this building, with the completed sheets kept as a record and as proof of testing etc. | Neighbourhood Management | Martin Barr |  | ESAs (caretakers) carry out monthly H&S inspections of blocks with the records stored electronically. These inspections include checking emergency lighting (where possible) and fire fighting equipment. | 2015-09-16 | Fully Completed | Martin Barr | 2015-09-10 15:08 | 2015-10-01 15:09 | 2015-09-10 15:08 | 2015-09-17 10:49 | -21 | In target