## Fire Risk Assessment Priority A
[6 empty] | Priority |  | Total Actions | Total Actions Completed |  | Percentage Completed
[6 empty] | High |  | 78 | 78 |  | 100%
[6 empty] | Information Only |  | 11 | 11 |  | 100%
[6 empty] | Medium |  | 2 | 2 |  | 100%
91
Fire Risk Assessment Actions
Total Records: 91
Risk Assessment | Process Start Date | Process No | Property Ref | Block | Priority |  | Risk |  |  | Action due date |  | Action taken | who | Category | Full or partial | Comp date
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:12 | 172131 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Work is presently being undertaken to convert some areas on the lower 3 floor levels of this building into domestic dwellings along with other work and the over cladding of the whole building. Proposals have been submitted to the local Authority Building Control department under the Building Regulations process. |  |  |  |  | The Building Control officer has the full application and has met with the contractor, and is taking issues forward with the fire brigade as necessary. We do not get approval until the end of the period. | Claire Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:17 | 172134 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | Contractors are currently working in this building to construct some new dwellings on the floor levels previously used as offices etc. |  |  |  |  | I agree, and will notify Janice Wray when handover of the project is undertaken - potentially end of Oct 2015. | David Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:19 | 172136 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | When the construction/refurbishment work is completed on this building all information as required by the Building Regulations must be handed over to the TMO by the contractors before they hand over the areas now under their control. |  |  | 2015-03-25 |  | The information above will all be part of the O&M manual or H&S file produced by the contractor at completion. | Claire Williams |  | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:21 | 172138 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | The service road/area on the right hand side of this tower block is used by the emergency services to park their vehicles, this area has been handed over to the contractors and is presently under their control. The contractors have stated that the LFB are happy with the current parking arrangements whereby the contractors are using part of the service road/area. |  |  |  |  | Contractor Rydon had spoken to the fire brigade about the fact that the service road is within their compound. All watches had seen it and as the access was locked by an FB key, there were no issues with it. An email from Rydon to the Fire Brigade confirming this situation, and the FB's response is in thehousing part of W2. | Claire Williams | Miscellaneous | Fully Completed | 2015-06-18
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:25 | 172140 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | According to the contractors label on the main electrical supply/distribution board of this building the next fixed electrical wiring test is due in December of this year. |  |  |  |  | INSTALLATION TESTED AND CERT SUPPLIED | Alex Bosman | Electrical Wire Check | Fully Completed | 2015-11-17
GRENFELL TOWER - 2014.10.17 | 2014-12-01 09:29 | 172141 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | At the time of this assessment the lighting was not working in the roof level room where the water tanks are located. |  |  | 2016-02-16 |  | all necessary works completed on 201552556 | John Tatham | Responsive Item | Fully Completed | 2016-02-16
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:06 | 172154 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The locking mechanism on the entrance door to this building from the walkway level is damaged and this door cannot be secured locked shut. |  |  |  |  | S&Mackman completed works end of Dec, but probs over Christmas meant revisit and works completed mid Jan 2015. | Claire Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:08 | 172155 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The fire fighter entry over ride device fitted to the entrance door of this building did not function and release the locking device on the door and open the door. This over ride device allows the Fire and Rescue Service to access the building in an emergency without the use of a key. |  |  | 2015-05-08 |  | Siobhan Rumble confirmed that this safety check should be undertaken regularly by her estates services team. As a result of the latest report on 10/4 SR instructed Paul Steadman to carry out this check. Confirmed checked and working as at today's date 8 May 2015. Please transfer to SR as regular monitoring is within her team responsibility | Claire Williams | Miscellaneous | Fully Completed | 2015-05-08
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:14 | 172156 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | At the time of this assessment there was some damage noticed to the installed lightning protection system in this building. At the time of the last service on this lightning protection system, 4th February 2014, the system was compliant. |  |  | 2015-03-25 |  | Held meeting with M&E team and Rydon. Rydon said they would consider looking at items on servicing list, but none received. CW passed back to Alex Bosman - before Christmas 2014. | Claire Williams | Lightning Protection | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:16 | 172159 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | On the 19th and 20th floor levels push bikes have been chained to the dry rising main outlets. |  |  |  |  | these have been removed | Siobhan Rumble | Communal Area Storage | Fully Completed | 2015-03-06
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:18 | 172160 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a secondary exit route from the basement boiler room area. |  |  |  |  | Secondary fire exit is now in place and unobstructed. This is being monitored by Rydon's own H&S team because of ongoing works to the boiler basement. | Claire Williams | Miscellaneous | Fully Completed | 2015-06-18
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:20 | 172161 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a secondary exit route from the basement boiler room area. It is not known when this hatch was last opened and checked to see that it operated correctly. |  |  |  |  | The secondary access above is not being used. A new access has been formed by a scaffold with ladder access that comes up on the west elevation close to the walkway. This was put in place with Rydon's H&S officer's agreement to overcome issues of the heavy hatch highlighted above. | Claire Williams | Miscellaneous | Fully Completed | 2015-06-18
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:22 | 172163 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The access door to the external roof from the internal corridor has had both of the "Gerda" locks removed from it, this door is now only secured by a normal latch type lock opened by a door handle. This door is now damaged and does not shut securely. |  |  | 2014-12-22 |  | 201554098 RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-03-05
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:23 | 172164 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The contractors are going to erect new cupboards on each of the residential flat/lift lobby areas to enclose pipe work. |  |  | 2015-04-10 |  | The new cupboards will be FD30 doors as described above. | Claire Williams | Miscellaneous | Fully Completed | 2015-04-10
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:25 | 172168 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The fire door to the refuse chute room on the 14th floor level grounds and will not shut fully. |  |  | 2015-01-06 |  | RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-02-22
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:28 | 172169 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The fire door to the staircase from the lift lobby areas on the 2nd and 19th floor levels are damaged and do not shut fully. |  |  | 2015-01-06 |  | RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-02-22
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:29 | 172170 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | On the 10th floor level the refuse chute hopper head is damaged - it's handle is missing and it does not shut fully |  |  | 2014-12-22 |  | 201554019 RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-03-05
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:32 | 172171 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The door frame and door within the boiler room at the base of the staircase from ground level down into the boiler room (which is located at basement level under Grenfell Tower) is damaged and the door does not shut fully. |  |  | 2015-03-25 |  | Remedial works were completed Jan 2015. | Claire Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:33 | 172174 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The door handle of the staircase door (separating lift lobby and staircase) is missing on the staircase side on the 13th floor level. |  |  | 2015-12-22 |  | RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-02-01
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:36 | 172176 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | The following flat entrance doors are the original fire rated flat entrance doors and which were fitted with a self closing device. These are flush solid doors and are all close fitting. These flats are numbers 56, 61, 86, 92, 112, 142, 154, 156, 165,166, 174.185, 195, and 206. |  |  |  |  | None | David Ward | Flat Door | Fully Completed | 2014-12-08
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:43 | 172177 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are two largish holes in the wall linings of the ground floor electrical room from the base staircase into the electrical room. |  |  | 2015-03-25 |  | completed jan 2015. contractor Rydon will check, and it is understood that Carl Stokes FR Assessor will liaise if at any visits any further issues arise. | Claire Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:46 | 172180 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | On the 2nd and the 15th floor levels the panels covering the cable ducts have been removed and not refitted correctly. One is held on with tape. |  |  | 2015-12-22 |  | RD confirm completion | John Tatham | Responsive Item | Fully Completed | 2016-02-01
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:48 | 172182 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Some new emergency lighting units have been installed by the contractor on the walkway level in the new entrance hall area. |  |  | 2015-05-08 |  | Certificate attached. Put in through 'housing' part of W2 | Claire Williams | Emergency Lighting | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:49 | 172185 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are no fire action notices displayed in this building next to the break glass call points of the fire alarm system. This is in the basement boiler room and in the roof level areas of this building. These notices describe the actions to be undertaken in the event of discovering a fire or if the fire alarm sounds. There are manual break glass call points in each electrical room. |  |  |  |  | Fire action notioces now installed by handyman. COMPLETED | Janice Wray | Signage | Fully Completed | 2014-12-01
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:51 | 172187 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Medium |  | The floor number on staircase landing on the 16th floor level has been altered to look like an 18. Floor numbers aid the fire service if there is an incident in this building. |  |  |  |  | all done | Siobhan Rumble | Signage | Fully Completed | 2015-03-06
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:53 | 172190 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Medium |  | The sign displayed in the ground floor level entrance lobby area of this building informing the emergency services which flats are located on which floor levels now needs to be moved up to the walkway level. This sign aids the fire service or other emergency service to where an incident in this building maybe. |  |  | 2015-03-25 |  | As comment on 'action taken' fire brigade have said they will entre thro the ground floor, and all watches have done familiarisation visits. NFA required. | Claire Williams | Signage | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:55 | 172191 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | When the new pipe work cupboards are constructed on each flat/lift lobby area the floor number on wall will be covered in by the cupboard. Floor numbers aid the fire service if there is an incident in this building. |  |  | 2015-03-25 |  | As actions - Rydon to paint or fit numerals onto cupboard doors. Temporary signs proposed until final version installed when doors fitted and decorated. | Claire Williams | Signage | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:57 | 172192 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a fire alarm system installed in this building there are no TMO employees who work in this building now. |  |  | 2015-08-20 |  | FA monitored by CAS / Tunstall Telecom | Janice Wray | Fire Alarm | Fully Completed | 2016-08-31
GRENFELL TOWER - 2014.10.17 | 2014-12-01 10:59 | 172193 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The contractor has moved the buildings fire alarm control panel up from the ground floor level to the walkway level. |  |  | 2015-05-08 |  | Certificate stored on W2 under 'housing' part of system. This says that the panel is in the same working order as it was taken over. The assumption is that this is still being serviced by Chubb - please check with Alex Bosman's team. | Claire Williams | Fire Alarm | Fully Completed | 2015-05-08
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:03 | 172195 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The fire alarm control panel was showing faults in both zones 9 and 22 at the time of this assessment. |  |  | 2015-03-25 |  | Panel now functionning as remedial works undertaken. | Claire Williams | Fire Alarm | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:05 | 172201 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | In the old ground floor reception there are the fire alarm control panels for the fire alarm detection systems in the nearby TMO buildings. |  |  | 2015-04-10 |  | Alex Bosman leading on getting smoke ventilation systems for nearby blocks working as connection with Grenfell severed and system clearly not been in full working order for a while. AB looked at intro perm vent through atrium roofing, but outcome not known. AB to update. | Claire Williams | Fire Alarm | Fully Completed | 2015-04-10
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:07 | 172203 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | When the new cupboards are constructed on the flat /lift lobby area the presently installed smoke detectors on these lift lobby areas will be inside the new cupboards in some cases. |  |  |  |  | As action to be taken comments. smoke detection alarms to be 500mm distant from smoke vents or other obstructions. | Claire Williams | Fire Alarm | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:20 | 172211 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The lifts in this building are fire fighter/evacuation lifts, the entrance to this building is now from the walkway level. It is not known if the fire service override controls for these lifts have been moved? |  |  | 2015-03-25 |  | as 'actions to be taken', fire brigade enter building from gf, so the fire service override control stays in the same position. | Claire Williams | Lifts | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:23 | 172213 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are fire fighting hose reels in the basement boiler room of this building, these hose reels have not been serviced according to the servicing labels attached to each item since August 2012. I am told that these hose reels are due to be removed as part of the boiler room refurbishment work. |  |  |  |  | Confirmed fire hose reels will be removed during boiler works | Alex Bosman | Hose Reels | Fully Completed | 2015-12-01
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:30 | 172214 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The dry rising main in this building is overdue its service according to the last service certificate seen. |  |  |  |  | Chub satisfactory test cert held carried out 27.4.2015 | Alex Bosman | Dry or Wet Riser | Fully Completed | 2015-12-01
GRENFELL TOWER - 2014.10.17 | 2014-12-01 11:32 | 172215 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The contractors, Rydon's are going to be working to upgrade the installed smoke extraction system on the flat/lift lobby areas and the refuse chute rooms of this building. |  |  | 2015-04-10 |  | Fire brigade informed that the smoke vent system being worked on, therefore not working. They have sent all watches to site to understand the set up. Subsequently at a small fire, LFB turned up with breathing apparatus - so all were aware of situation. Passive system due to be complete by end of May, new fans etc just received building control ok - completion summer when certification will be received. | Claire Williams | Miscellaneous | Fully Completed | 2015-04-10
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:09 | 172230 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | As part of the refurbishment work to be undertaken in this building the dry riser inlet is to be moved from its current located in the ground floor lobby area to an external position on the face of the building |  |  | 2015-03-25 |  | awaiting M&E team to provide certification on current dry riser before Rydon's touch it. Alex Bosman leading on this. Cert provided to assessor | Claire Williams | Dry or Wet Riser | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:12 | 172234 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are contractors working in this building refurbishing the lower floor levels, the street level to the walkway level, this includes constructing some new dwellings. |  |  | 2015-03-25 |  | attached | Claire Williams | Miscellaneous | Fully Completed | 2015-03-25
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:13 | 172235 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are contractors working in this building refurbishing the lower floor levels, the street level to the walkway level, this includes constructing some new dwellings. |  |  |  |  | Contractor has their fire risk procedure, which will be amended as works progress/issues change. I attach a version of their risk assessment. It is noted that Rydon H&S team visit site regularly, as well as their own site managers' responsibility for safety checks. | Claire Williams | Miscellaneous | Fully Completed | 2015-05-08
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:18 | 172239 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The emergency lighting system installed to cover the common parts of this building appears to be overdue for its annual service, maintenance and discharge test. |  |  | 2016-01-21 |  | AP confirmed service complete 9.12.2015 | Alex Bosman | Emergency Lighting | Fully Completed | 2016-01-21
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:19 | 172240 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? |  |  |  |  | these were done by RGE 6 monthly under contract. inspectors check the block lighting to check if all bulbs and emergency lighting are working and records are kept | Siobhan Rumble | Miscellaneous | Fully Completed | 2015-03-06
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:23 | 172242 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Are the weekly occupier's tests of the buildings fire alarm and warning system being undertaken? Including testing the automatic smoke vents |  |  |  |  | being done by rydons | Siobhan Rumble | Fire Alarm | Fully Completed | 2015-03-06
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:25 | 172245 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Caretaker testing and inspections of the buildings structure etc. |  |  |  |  | yes and these are available for inspection at any time | Siobhan Rumble | Inspection Regime | Fully Completed | 2015-03-06
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:28 | 172246 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | The fire alarm system installed in this building is due for a test/service and maintenance next month, November 2014. |  |  |  |  | complete - system no longer present | Alex Bosman | Fire Alarm | Fully Completed | 2015-11-17
GRENFELL TOWER - 2014.10.17 | 2014-12-01 12:30 | 172247 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The external face of this building is to be over clad. The piece of cladding fixed to the external wall at the moment is on timber battens. |  |  |  |  | The contractor has provided information on cladding, inc fixings, fire barriers. This is being inspected as work progresses by the Clerk of Works employed by the TMO as well as Building Control officer (John Hoban). Building control payment for services attached. The final cert will not be issued by them until the end of the job. | Claire Williams | Miscellaneous | Fully Completed | 2015-05-08
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 15:45 | 269272 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | No Item Number High When the construction/refurbishment work is completed on this building all information as required by the Building Regulations, must be handed over to the TMO by the contractors before they hand back the building to the TMO. |  |  | 2016-09-05 |  | Claire Williams confirms that Buildig Regns Completion Certificate received & stored on T:drive A&R / Grenfell | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:04 | 269274 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | The layout floor level drawings of this building now do not reflect the building layout after the recent construction work has been undertaken. |  |  | 2017-02-06 |  | Drawings provided to Fire Risk Assessor by Claire Williams | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:07 | 269277 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The electrical fixed wiring in this building is presently within test date, but this building has had major electrical work undertaken on some fixed wiring during the present refurbishment. |  |  | 2016-09-05 |  | Confirm RMA have completed the testing and on asite works & Certificate awaited | Alex Bosman | Wiring Inspection | Fully Completed | 2016-11-07
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:09 | 269278 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | At the time of this assessment the lighting was not working in some roof level areas of this building. A check should be undertaken on all of the lighting circuits and light units at the roof level and any defect wiring or bulbs etc repaired or replaced so that the lighting is in full working order. |  |  | 2016-09-05 |  | Alex Bosman confirms that RMA have completed works on site - Certificate awaited | Nicola Bartholomew | Inspection Regime | Fully Completed | 2016-11-07
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:12 | 269280 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Behind the wire mesh gate off the staircase on the upper floor level to the roof there are used cigarette ends on the floor. |  |  | 2016-09-05 |  | inspections ongoing | Nicola Bartholomew | Inspection Regime | Fully Completed | 2017-03-13
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:14 | 269281 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | There is no fireman override switch fitted to the ground floor entrance hall to lift lobby area door. There is one fitted to the buildings entrance/exit door. |  |  | 2017-02-06 |  | CONFIRMED | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:16 | 269282 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The contractor's are presently working on the boilers in the basement area, there are no flue gas print outs should be attached to the gas boilers. Gas safety certificates have been forwarded to the TMO for the installation work undertaken. |  |  | 2016-09-05 |  | Documents attached. In O&M manual - not in basement. | Claire Williams | Boiler | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:18 | 269283 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | At the roof level the last entry in the service book for the plant and extraction equipment located here was on the 5th April 2016, before this there were more frequent servicing and maintenance visits. For the basement water pumps the last check/service was on the 16th April 2016. |  |  | 2016-09-05 |  | Completed. Equipment on Engie servicing programme. Monthly inspections carried out | Alex Bosman | Miscellaneous | Fully Completed | 2017-01-06
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:21 | 269284 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a secondary exit route from the basement boiler room area. This metal hatch and the frame is badly rusted. |  |  | 2016-09-05 |  | Hatch is being overhauled & hinges replaced etc. John Griffin progressing work. | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:37 | 269290 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a lot of contractors waste in the basement boiler room. |  |  | 2016-09-05 |  | All have been removed. | Alex Bosman | Miscellaneous | Fully Completed | 2016-09-08
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-08 16:49 | 269294 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The timber doors of the new cupboards erected on each of the flat/lift lobby areas are not marked as 30 minute fire rated doors. |  |  | 2016-09-05 |  | Claire W confirms that documentation has been obtained to confirm doors are complaint - this is available at the Grenfell audit location on the T drive | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:22 | 269356 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Some of the new doors in this building are not fitted with cold smoke seals as required by the Building Regulations. The Building Control Officer has stated that smoke seals should not be fitted to these doors. |  |  | 2016-09-06 |  | E-mail from Building Control provided to Assessor (& in H&S Fire directory) | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:26 | 269357 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | It was noted that some of the intumescent strips on the newly installed fire doors have been painted over. |  |  | 2016-09-06 |  | C Stokes asked to provide location details and ESA asked to monitor for any damage to these and report asap | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:29 | 269361 | S217012770009 | GRENFELL TOWER LANCASTER WEST ESTATE | Information Only |  | Raised in error |  |  | 2016-10-28 |  | RAISED IN ERROR | Janice Wray | Miscellaneous | Fully Completed | 2016-09-07
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:29 | 269363 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is a metal louvered door separating the ground floor lift lobby area from the shaft and electrical intake room. |  |  | 2016-09-06 |  | Claire Williams confirms that an FD30 door has now been installed behind this louvred door | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:32 | 269364 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The door and frame at the base of the basement staircase is badly damaged as are other fire doors in this basement area. |  |  | 2016-09-06 |  | Order requested - 26th Aug 2016 201622988 & VARIATION ORDER COMPLETED | Janice Wray | Responsive Item | Fully Completed | 2017-05-25
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:35 | 269366 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The flat entrance door of flat 24 is damaged with the letter box missing. |  |  | 2016-09-06 |  | ESA confirms completion | Janice Wray | Flat Door | Fully Completed | 2017-01-18
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:37 | 269367 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | 12h High The flat entrance door of flat 112 is being replaced, this new door is not marked as a fire rated door and it does not have a self closing device fitted to it. Cold smoke seals are fitted. |  |  | 2016-09-06 |  | leaseholder emailed by CW but no response. Chased today 16/8. ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | Claire Williams | Flat Door | Fully Completed | 2017-10-19
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 12:40 | 269368 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Some of the staircase doors are not being closed fully by the self closing devices fitted to the doors. These doors should be picked up during the caretakers inspections of the doors. |  |  | 2016-09-06 |  | Repairs raised & completed - monitoring ongoing | Nicola Bartholomew | Responsive Item | Fully Completed | 2017-03-13
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 13:50 | 269374 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The staircase door at the 16th floor level is damaged. |  |  | 2016-09-06 |  | ESA confirms repair completed | Nicola Bartholomew | Responsive Item | Fully Completed | 2017-03-13
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 13:52 | 269375 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is no emergency light unit in the disabled toilet of the new community area. |  |  | 2016-09-06 |  | Emergency light fitted at the end of July. Elec cert in O&M manual. | Claire Williams | Emergency Lighting | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:16 | 269381 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The contractors are still working in areas of this building. |  |  | 2016-09-06 |  | Elec certs in O&M manual. CW to try and upload onto W2 in next week | Claire Williams | Miscellaneous | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:18 | 269383 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are TMO standard fire action notices are displayed next to each of the fire alarm break glass call points in the basement boiler room and in the roof level areas of this building. |  |  | 2016-09-06 |  | Fire Action Notices installed on each lift lobby adjacent to lift - design and content agreed with assessor | Nicola Bartholomew | Signage | Fully Completed | 2017-03-13
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:20 | 269387 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are 2 areas of this building covered by BS 5839 Part 1 manual and automatic fire detection systems, the roof level area and the basement boiler room. |  |  | 2016-09-06 |  | Rydons did not work in the roof area. Need to investigate requirement further with assessor & seek inspection /maintenance records ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | Janice Wray | Miscellaneous | Fully Completed | 2017-10-19
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:25 | 269388 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There appears to be no fire detector in the ground floor level area off the lift lobby area in front of the electrical intake room, there is a smoke vent in the ceiling of this area. |  |  | 2016-09-06 |  | Whole gf lift lobby is treated as one area for fire purposes. See strategy drawing attached. | Claire Williams | Miscellaneous | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:28 | 269389 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are fire detection devices installed in this building to activate the newly installed smoke extraction system. |  |  | 2016-09-06 |  | CW confirms that EXOVA fire strategy agreed with Building Control Commissionig Certificate dated March 2016 provided | Janice Wray | Miscellaneous | Fully Completed | 2016-12-09
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:32 | 269391 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | It appears that the mains gas supply to this building is interfaced with the automatic opening ventilation system and shuts off if the AOV system operates, the lifts could also be interfaced. LIFTS NOT INTERFACED - CWiliams |  |  | 2016-09-06 |  | Specification to separate main smoke system from basement with gas boilers is in production, with works due to take place this financial year. ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | Claire Williams | Miscellaneous | Fully Completed | 2017-10-19
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:41 | 269393 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | In some of the new dwellings the domestic fire detection systems are not fitted as per the requirements of BS5839 Part 6 2013. The installed devices are to LD3 standard in some flats, to LD 1 in others, some have 2 smoke detectors in the hallway a couple of meters apart others only one detector. Some dwellings have heat detectors installed in the kitchen areas other do not. |  |  | 2016-09-06 |  | Rydon responded that the new flats have a lesser specification because of their size and their lower location in the building. We have the building regulations certification on the building - in the O&M manual. | Claire Williams | Fire Alarm | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-09 14:47 | 269394 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | At the roof level there is a coil of fire alarm cable not connected at one end to anything. |  |  | 2016-09-06 |  | Order raised for Allied Protect to attend site with ESA, investigate and report back. To be raised with Rydons at Defects Inspection. (currently not connected) ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | Nicola Bartholomew | Miscellaneous | Fully Completed | 2017-10-19
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:35 | 269423 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | BS 5839 Part 1 2013 fire alarm systems are being provided in the boxing club and children's nursery areas of this building. These are stand alone systems. |  |  | 2016-09-07 |  | No FA in Boxing Club - AOV only Nursery responsible for testign fire alarm in their area and ensuring any hirers are aware of procedure Grenfell FA linked to CAS / Tunstall Telecom | Janice Wray | Fire Alarm | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:37 | 269424 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are 2 smoke detectors fitted on the 7th floor level ceiling, the 2nd detector is a different style of smoke detector to the newly installed one. This device is on the ceiling near to the flat entrance door of flat 46. The contractor does not know anything about this 2nd device. |  |  | 2016-09-07 |  | Confirmation that second "detector" is actiually a CCTV camera | Nicola Bartholomew | Smoke Alarms | Fully Completed | 2016-12-09
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:39 | 269425 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are no operating instructions or as installed diagrams located next to the Automatic Opening Vents (AOV) control panel, how is this control panel accessed? |  |  | 2016-09-07 |  | Written instructions provided - diagram within Hub Room on site. (Hub room accessed via key stored in keysafe installed in bin room - accessed via FB14 key) | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:41 | 269427 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | It is not known if training on the operating of the AOV system has been given to all TMO staff who requires it. |  |  | 2016-09-07 |  | 2 sessions in familiarisation completed by Rydons. LFB also attended for familiarisation | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:47 | 269432 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The keys to operate the manually operated individual AOV over ride devices should be on site, they will be in the AOV control box, but there are no keys there at present and the system is in use. |  |  | 2016-09-07 |  | Keys stored in Keysafe located in bin room - accessed via FB key | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 09:53 | 269439 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There is an AOV in the area outside of the ground floor electrical room, how is this AOV activated as there is no smoke detector in this area? Please see item 17b above as well |  |  | 2016-09-07 |  | Whole gf lift lobby is treated as one area for fire purposes. See strategy drawing attached | Janice Wray | Miscellaneous | Fully Completed | 2016-11-15
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:06 | 269441 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The AOV system and the installed fire alarm systems in this building is remotely monitored. |  |  | 2016-09-07 |  | The alarms go to CAS, who: - tell estates services - whether in working hours or OOH - call the fire brigade 1 Indicators at gf panel show the fire brigade where alarm has been activated. Discussion with fire brigade over how they evidence they have been on site and resolved issue and reset system knowing all is safe. 2 Local estates services teams have been shown how to reset alarms once fire brigade have visited. 3 Residents been notified of stay put policy unless at risk. | Claire Williams | Miscellaneous | Fully Completed | 2016-08-16
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:08 | 269444 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | It is not known if the fire service controls for the lifts been moved back down to the street level? |  |  | 2016-09-07 |  | COMPLETED | Janice Wray | Miscellaneous | Fully Completed | 2016-12-09
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:11 | 269445 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | Information Only |  | When the boxing club and the children's nursery occupy their areas of this building they should be asked to undertake a fire risk assessment (FRA) for their area. |  |  | 2017-02-08 |  | Confirmed this is a requirement of the lease in both cases | Janice Wray | Miscellaneous | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:15 | 269446 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | In the roof level lift motor and plant rooms and in the basement boiler room there is BS 5839 Part 1 fire detection systems fitted. Where is the control panel(s) for these BS5839 Part 1 systems and who is undertaking the servicing etc of this systems? Keystone checked |  |  | 2016-09-07 |  | ACTION CLOSED DOWN ON W2 on 19th Oct 2017 as system will no longer be available ACTION REMAINS PARTIALLY COMPLETE | Janice Wray | Fire Alarm | Fully Completed | 2017-10-19
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:17 | 269447 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are BS 5839 Part 1 fire detection systems fitted in this building, is weekly occupier testing of these systems being undertaken? |  |  | 2016-09-07 |  | ESA (Paul Steadman) confirms fire alarm tested on weekly basis - Fridays at 10am | Nicola Bartholomew | Fire Alarm | Fully Completed | 2017-05-24
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 10:19 | 269449 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | The lightning protection system installed on this building was last serviced/tested in September 2015. It does not state if the system passed or failed this test? Keystone checked. |  |  | 2016-09-07 |  | Certificate provided to assessor | Janice Wray | Lightning Protection | Fully Completed | 2016-08-31
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 12:31 | 269482 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | There are emergency lighting units installed on the means of escape routes of this building plus in the roof level lift motor and plant rooms and in the basement area of this building. |  |  | 2016-09-07 |  | Last service carried out 17/1/17 | Alex Bosman | Emergency Lighting | Fully Completed | 2017-06-05
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:48 | 269520 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Are the monthly occupier tests and inspections of the emergency lighting system in the building being undertaken with records kept? |  |  | 2016-09-07 |  | Confirmed | Nicola Bartholomew | Inspection Regime | Fully Completed | 2016-12-09
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:49 | 269521 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | According to the contractors labels on the fire extinguishers in this building they are all out of test date. The last date on the contractors test/servicing labels is October 2014. |  |  | 2016-09-07 |  | All serviced on 24th Oct 2016 | Alex Bosman | Fire Extinguisher | Fully Completed | 2016-11-07
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:51 | 269522 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Are the weekly occupier's tests of the buildings automatic smoke ventilation system being undertaken? |  |  | 2016-09-07 |  | tested weekly on Fridays | Nicola Bartholomew | Inspection Regime | Fully Completed | 2017-03-13
GRENFELL TOWER, GRENFELL ROAD, LONDON W11 1TQ 2016.06.20 | 2016-08-10 16:52 | 269524 | S217008800001 | GRENFELL TOWER GRENFELL ROAD | High |  | Caretaker testing and inspections of the buildings structure etc. |  |  | 2016-09-07 |  | Confirmed | Nicola Bartholomew | Inspection Regime | Fully Completed | 2016-12-09
91