        1 Monday, 26 November 2018

        2 (10.00 am)

        3 SIR MARTIN MOORE-BICK: Good morning, everyone. Welcome to

        4 today's hearing.

        5 We are going to continue this morning with the

        6 evidence of Dr Lane.

        7 MS GRANGE: Yes.

        8 SIR MARTIN MOORE-BICK: Could you ask Dr Lane to come back

        9 in, please. Thank you.

        10 DR BARBARA LANE (continued)

        11 Questions by MS GRANGE (continued)

        12 SIR MARTIN MOORE-BICK: All right, ready to carry on?

        13 THE WITNESS: Yes.

        14 SIR MARTIN MOORE-BICK: Good, thank you very much.

        15 Yes, Ms Grange.

        16 MS GRANGE: Thank you.

        17 Just to signpost what we're going to be dealing with

        18 today, I want to focus today on the active and passive

        19 fire safety measures inside the building, and the extent

        20 to which they failed to control the spread of fire and

        21 smoke and contributed to the speed at which the fire

        22 spread.

        23 In general, we're going to be looking at certain

        24 passive measures first, including the flat and stair

        25 doors, and then looking at the active systems later in
        1

        1 the day, including the fire main, the lift and the smoke

        2 control system.

        3 Mr Chairman, I want to just give a very minor

        4 trigger warning at this stage on the basis that, during

        5 the next two sections dealing with doors, we will look

        6 at some images of fire doors in Grenfell Tower,

        7 including some images of the doors when tested with

        8 smoke and flame around them. So it's just a minor

        9 trigger warning now in case anyone would find those

        10 images distressing.

        11 Before we start, I understand, Dr Lane, that there

        12 is one point of clarification that you would like to

        13 provide in relation to your evidence from last Thursday.

        14 A. Yes, there is.

        15 I think it was just before lunch, there was quite

        16 a rapid series of questions about non-combustible,

        17 combustible and flammability.

        18 SIR MARTIN MOORE-BICK: Yes.

        19 A. So I just want to speak very briefly about that.

        20 The question about non-combustible was, I think: did

        21 I agree it dealt with calorific content only? My answer

        22 is no, because sustained flaming, mass loss and

        23 temperature difference must also be measured and, within

        24 limits, that's what becomes the definition of

        25 a non-combustible material.
        2

        1 The word "flammability" threw me because it's not

        2 a defined term in reaction to fire tests or in general;

        3 it's a word I won't use as a fire safety engineer.

        4 I think if the person meant sustained flaming, if

        5 sustained flaming is part of assessing combustible and

        6 non-combustible materials, the answer is yes, with zero

        7 required for a non-combustible material, and then

        8 different quantities of sustained flaming. Remember we

        9 talked about the B down to F then for other materials.

        10 So it's a very technical point but I just felt quite

        11 bad I didn't answer it on Thursday.

        12 SIR MARTIN MOORE-BICK: That's helpful, thank you.

        13 MS GRANGE: Thank you.

        14 Yes, so just before we consider flat doors

        15 specifically, I just want to start by considering the

        16 overall consequences once we have a multi-storey fire in

        17 existence.

        18 Once that was the case, so we have this external

        19 fire spread, what fire safety features of the building

        20 do you think became most critical inside the building?

        21 A. Okay, so I haven't given an order of contribution yet,

        22 as you know, so I wouldn't mind actually talking about

        23 that for just a little while.

        24 So once the cladding fire had become a multi-storey

        25 fire, then, over time, internal fires also commenced,
        3

        1 and so we now, over time, had a multi-storey internal

        2 fire condition.

        3 So it's two multi-storey events, if you will, one

        4 caused by the other.

        5 I also made clear on Thursday that in the next phase

        6 of my work I'm going to be looking at intrinsic risk and

        7 risk assessments. And this is important, because

        8 a non-compliant system will either play a role or not in

        9 terms of a hazard posed to an individual, or a grouping

        10 of individuals, as a function of the fire hazard in that

        11 location.

        12 So, giving a theoretical example, a non-compliant

        13 fire door may have a substantial contribution to the

        14 severe consequences in one location for a grouping of

        15 people, and it may have had no contribution in another

        16 location where the consequences were not extreme.

        17 So the non-compliance status is important, and we'll

        18 be talking a lot about that today and in terms of health

        19 and safety duties.

        20 But the next thing, then, is the overall assessment

        21 of risk, understanding the hazards to the people who

        22 lost their lives particularly in those locations, and

        23 how each active and passive fire safety measure

        24 contributed to what's called "severe harm".

        25 I've put in section 2 of my report a document I want
        4

        1 to make you aware of. It's called PAS 79. That sets

        2 out a fire risk assessment methodology. And risk is

        3 a function of probability of occurrence and consequences

        4 of failure, and where there is multiple loss of life,

        5 that's defined as "severe harm".

        6 So we know the consequences and we know the

        7 probability, and the next step, then, is to analyse, for

        8 each grouping of people who lost their lives, how each

        9 one of the active and passive measures contributed.

        10 So I can't pick one more than the other for all

        11 conditions, because the fire hazard is different as

        12 a function of one's location.

        13 SIR MARTIN MOORE-BICK: Yes.

        14 MS GRANGE: Just in terms of particular features that are

        15 critical, would you agree that the protected stairs and

        16 the lobbies are two particularly important spaces?

        17 A. Yes. So in Grenfell Tower, there was only one staircase

        18 and, when a resident was in a flat, one lobby leading to

        19 one staircase. So once the fire had spread through the

        20 cladding on multiple floors, there was only one way to

        21 leave the building, and so the staircase, but

        22 particularly the lobby, immediately became the most

        23 important protection measure for those persons when they

        24 were evacuating.

        25 For people who stayed, various active and passive
        5

        1 fire protection measures were needed or relied upon by

        2 them to make that staying put safe in that context.

        3 Okay?

        4 So the stairs and the lobby become very important,

        5 but the compartmentation to the flats was exceptionally

        6 important for people who did not walk down the stairs of

        7 their own accord, within particularly the first

        8 40 minutes.

        9 I've gone into considerable detail on this subject

        10 in section 14 particularly.

        11 Q. I just wanted to get you to give an overview at this

        12 stage, and what you're saying there is that flat doors

        13 and stair doors, which we're going to come to in

        14 a moment, become particularly important?

        15 A. They become particularly important, but there are other

        16 openings in the lobby that are a potential for fire and

        17 smoke spread. So any riser breaking through the lobby,

        18 such as the smoke control riser, when it's shut, must

        19 also prevent fire and smoke spread.

        20 There were multiple other services in the lobby

        21 built as part of the primary refurbishment, and they too

        22 needed to prevent fire and smoke spread.

        23 But in terms of the immediate line between a person

        24 in a flat and the conditions in the lobby and the

        25 conditions in the stairs, the doors are particularly
        6

        1 important, in my opinion.

        2 Q. Just one more question before we get specifically to

        3 flat doors.

        4 In terms of the active and passive safety systems in

        5 the building, I think your evidence is that the greater

        6 number of layers of safety which fail, the greater the

        7 likelihood of a major incident; is that correct?

        8 A. Yes, that's correct, and that's not, let's say, you

        9 know, an opinion I formulated on my own; it's kind of

        10 classic disaster or catastrophe theory, where the more

        11 layers -- just as the statutory guidance builds in

        12 layers and multiple layers, we spoke a lot about cavity

        13 barriers on Thursday, there's at least three, for

        14 example, between one window and the next.

        15 So the more layers that are defective or entirely

        16 defective, the higher the risk and the more severe the

        17 consequences.

        18 Q. So turning, then, to specifically look at flat doors,

        19 it's really chapter 15 and it's particularly

        20 chapter 15.5 and appendix I that are going to be

        21 relevant here, if you want to make sure you have those

        22 to hand.

        23 A. Yes.

        24 Q. Picking up on that theme about flat doors and their

        25 importance, in the LGA guide on purpose-built blocks of
        7

        1 flats, it says that flat doors are critical to the

        2 safety of the common parts. Would you agree with that?

        3 A. Yes, I do.

        4 Q. In terms of the relevant legal framework, and what

        5 happened at Grenfell Tower, we know that there was

        6 a significant flat door replacement in 2011 --

        7 A. Yes.

        8 Q. -- in Grenfell Tower.

        9 At that time, 106 flat doors were replaced. You

        10 give the figures in your report. That's 58 unglazed

        11 flat doors --

        12 A. Yes.

        13 Q. -- and 48 glazed.

        14 Both types of door were Masterdor Suredor doors.

        15 A. That's correct.

        16 Q. Is that correct?

        17 In addition, there were 14 doors that were not

        18 replaced at that time which you believe may have been 12

        19 leaseholder doors and two tenanted doors; is that

        20 correct?

        21 A. Yes.

        22 Q. We should perhaps note at this point that you've noted

        23 that in certain chronologies produced to the inquiry,

        24 there's some reference to flat door replacement works in

        25 or about 1985. But is it right that we don't have any
        8

        1 documentation at this stage to assist us in what

        2 would've been the scope of those works?

        3 A. That's correct.

        4 Q. As we've already discussed, back last Thursday, your

        5 view is that Grenfell Tower was originally constructed

        6 in accordance with the guidance set out in CP3 1971, and

        7 you've explained to us what the CP3 1971 guidance

        8 would've been for doors.

        9 You've said the recommended performance

        10 specification was for something called a type 3

        11 fire-resisting door.

        12 A. Yes.

        13 Q. Is that correct?

        14 A. Yes.

        15 Q. You've explained in your report that that meant they

        16 must have freedom from collapse for at least 30 minutes,

        17 resistance to passage of flame for at least 20 minutes

        18 and fitted with automatic self-closing devices; is that

        19 correct?

        20 A. That's correct.

        21 Q. Building up towards the 2011 flat door replacement, you

        22 note that there was some DCLG guidance in 2006, "Fire

        23 safety risk assessments: sleeping accommodation", often

        24 referred to as the DCLG sleeping guide, and that that

        25 was available and in force at the time the 2011 door
        9

        1 replacement was being considered; is that correct?

        2 A. Yes.

        3 Q. You say that that assisted in any risk assessment

        4 relating to doors; is that correct?

        5 A. It should do.

        6 Q. You say that a key point that is made in that DCLG

        7 guidance was that all doors onto a protected corridor

        8 should have a self-closing device; is that correct?

        9 A. Yes.

        10 Q. You also note that from July 2011, there was the Local

        11 Government Association, LGA, guide on purpose-built

        12 blocks of flats --

        13 A. Yes.

        14 Q. -- which also applied to doors in Grenfell Tower; is

        15 that correct?

        16 A. Correct.

        17 Q. Is it right that this represents guidance to assist

        18 responsible persons to discharge their duties under the

        19 Fire Safety Order 2005?

        20 A. Yes, it is.

        21 Q. I just want to look at a few potentially relevant parts

        22 of that guidance.

        23 A. Okay.

        24 Q. So if we can pull that up. If we can go to

        25 CTAR00000033, at page 98, this is internal page 95 of
        10

        1 the LGA guide.

        2 If we could blow up that table at the bottom, that's

        3 great.

        4 Can you see that okay?

        5 A. Yes. Actually, it's probably worth saying, nothing has

        6 been made available to me, and I would've thought it

        7 should have been by now, as to what the performance spec

        8 for those works actually were, and so what document was

        9 actually relied upon or considered.

        10 Q. Yes.

        11 SIR MARTIN MOORE-BICK: All right.

        12 MS GRANGE: That's helpful.

        13 What I'm going to do is look at the LGA guide now,

        14 and then we'll look at the relevant parts of ADB which

        15 you've summarised.

        16 Sticking with this, the LGA guide, this is giving

        17 benchmarks for existing blocks of flats.

        18 A. Yes.

        19 Q. What it's saying is if you've got different travel

        20 distances, you may be advised to do different things

        21 with your doors; is that correct?

        22 A. That's correct.

        23 Q. At Grenfell Tower -- we'll come back to your diagram in

        24 a moment -- you've measured travel distance in the lobby

        25 as up to 10.5 metres.
        11

        1 A. Yes.

        2 Q. Which means -- are we on the second-to-last bullet point

        3 here?

        4 A. Exactly. So if one agrees with the LGA guide, it says

        5 that for a travel distance between 10 to 15 metres, in

        6 an existing building, as a minimum the existing doors

        7 should be upgraded as opposed to being replaced with

        8 a new door.

        9 Q. Yes.

        10 So just to read that:

        11 "• In ventilated lobbies and corridors, travel

        12 distances of ten to 15m may be acceptable, providing all

        13 doors to the common corridor or lobby are at least

        14 'upgraded FD30S' doors ... and the smoke ventilation

        15 comprises PVs or AOVs."

        16 A. That's correct. So it's travel distance and ventilation

        17 provision.

        18 Q. Just to be clear what PV or AOV means --

        19 A. Permanent vent and automatically openable vent, yes.

        20 Q. Thank you.

        21 If we can then stay with this LGA guide for a moment

        22 and go to paragraph 62.17, that's on internal page 101.

        23 A. Yes.

        24 Q. So here, what it's saying is it's not going to be

        25 practicable to test existing doors to confirm their
        12

        1 actual fire resistance; therefore, various options exist

        2 in relation to doors.

        3 A. Yes.

        4 Q. So this is saying you can either accept the door as it

        5 is, upgrade the door or replace the door; is that

        6 correct?

        7 A. Well, it's the view of this guide that it's not

        8 practicable to test existing doors, and so it offers you

        9 some other approaches to consider.

        10 Q. Yes.

        11 A. Do you want me to explain?

        12 Q. And one of those is replacement of the door.

        13 A. Yes, it is indeed.

        14 Q. Exactly.

        15 It might be helpful at this point, because this is

        16 going to come up in relation to doors generally, where

        17 we have upgrading of the door, it talks about fitting

        18 intumescent strips and smoke seals.

        19 Could you just explain to the chairman what the

        20 difference is between an intumescent strip and a smoke

        21 seal?

        22 A. Yes, I can.

        23 So an intumescent strip operates under heat, and

        24 it's intended to prevent the passage of flame as well as

        25 the gaseous products of combustion.
        13

        1 A smoke seal is intended to prevent the passage of

        2 gaseous products of combustion only. It's also called

        3 a cold smoke seal.

        4 Q. Again, just sticking with this guide for the moment, can

        5 we go to page 102 and look at 62.20.

        6 So is it right that that is making clear:

        7 "62.20. The fitting of suitable self-closing

        8 devices - whether to replace rising butt hinges

        9 (pictured below) or because the doors are not fitted

        10 with self-closing devices - must be undertaking the

        11 short term as a matter of priority.

        12 So in this guide, it is very clear that you must fit

        13 self-closing devices as a priority; is that correct?

        14 A. Absolutely, which aligns with the statutory guidance.

        15 Q. Which we're going to come to next.

        16 Can we also look at paragraph 62.22 of the LGA

        17 guide. That's at the bottom there.

        18 Is it right that that makes clear that:

        19 "62.22. Any new or replacement doors within

        20 an existing block of flats should meet current standards

        21 for fire-resisting doors ..."

        22 So if you choose to put in a new door, you need to

        23 put it in in accordance with current standards?

        24 A. Yes, that's correct, and so one would be expected to

        25 have the relevant test evidence to either the national
        14

        1 class or the European class.

        2 Q. Thank you.

        3 Just before we come on to Approved Document B, we

        4 talked about travel distances and your assessment of

        5 travel distances.

        6 You've put a very clear figure in your addendum to

        7 your report, BLAS0000037 on page 24, figure 15.5. If we

        8 could bring that up.

        9 (Pause)

        10 It's within that same addendum, and it's figure

        11 15.5.

        12 (Pause)

        13 A. I'm not sure the figure can really do --

        14 Q. If you want to explain --

        15 A. Be as powerful as it might be looking at the moment.

        16 SIR MARTIN MOORE-BICK: You tell us what you want to tell

        17 us.

        18 A. I think on the drawing I marked up the travel distance

        19 from each door, and it's quite striking, actually, when

        20 you think about consequences later, the difference in

        21 terms of journey distance as a function of what flat you

        22 lived in. And in terms of the LGA guide, that the

        23 travel distances are exceeded.

        24 I don't know if you wanted to cover anything else --

        25 Q. We can come back to that in bit. We'll check we have
        15

        1 the right diagram.

        2 A. So, for example, flat 1s --

        3 Q. Page 25.

        4 A. -- the travel distance is only 4.5 metres, it's a very

        5 short distance, but for other flats it's in excess of

        6 10 metres. That's why this situation about the hazard

        7 experienced in specific locations is going to become so

        8 important.

        9 Q. Yes, that's it. If we can zoom in on that middle

        10 figure, blow that up.

        11 A. Yes.

        12 Q. So does that illustrate your --

        13 A. Yes.

        14 Q. -- travel distances?

        15 A. Yes.

        16 So you can see occupants of flat 4 have to travel

        17 over double that of, say, somebody living in flat 1.

        18 Q. I now want to go to your summary of the requirements of

        19 the relevant part of Approved Document B, and this is

        20 table I3 of your report, if we could bring that up on

        21 the screen. That's BLAS0000030 at 36.

        22 Thank you.

        23 You've explained in your report that at the time of

        24 the flat door replacement work in 2011, Approved

        25 Document B 2010 would've been in place; is that correct?
        16

        1 A. That's correct.

        2 Q. What you've sought to do in this table, which I think

        3 appears in A3 landscape in your report, is to summarise

        4 the key performance requirements that are there in

        5 Approved Document B 2010; is that correct?

        6 A. That's correct.

        7 Q. I just want to pick out some of the key ones at this

        8 stage?

        9 A. Mm.

        10 Q. So if we go the fourth column along, you have "Fire

        11 resistance", and there you have no integrity failure up

        12 to 30 minutes when tested to the relevant British

        13 Standards; is that correct?

        14 A. That's correct.

        15 Q. That's 30 minutes' integrity.

        16 A. 30-minute door, yes.

        17 Q. Just remind us what integrity is.

        18 A. It's a measure of preventing flame and temperature

        19 coming through cracks. That's a very simplistic

        20 definition. There's certain ways of measuring it during

        21 the test, but it's basically to make sure there's no

        22 cracks and no flames protruding.

        23 Q. Yes.

        24 In the next column you have "Smoke leakage

        25 performance standard", and you refer to -- they have to
        17

        1 have a leakage rate not exceeding 3 cubic metres per

        2 metre per hour when tested in certain ways; is that

        3 correct?

        4 A. Yes, that's correct, and measuring that leakage is

        5 deemed to represent the smoke leakage condition.

        6 Q. Yes.

        7 Two other points on this table.

        8 "Glazing", in the sixth column, it makes it clear:

        9 "No glazing unless the glazing as per table A4

        10 unless the glazing has been demonstrated to achieve

        11 an insulation performance equivalent to the required

        12 integrity performance."

        13 Is that correct? That's saying your glazing has not

        14 got to be a weak point; is that correct?

        15 A. That's correct. So on escape routes, the glazing

        16 basically has to be detailed up to not be a weak spot

        17 and not allow heat transfer through the glass. So

        18 insulation performance is about preventing -- detailing

        19 to prevent temperature rise on the unheated side. So

        20 it's protecting the person walking past the closed door

        21 if the fire's behind that door.

        22 Q. The point you made earlier about self-closing device is

        23 in the very next column, self-closer performance

        24 standard. So that makes it clear that it is required,

        25 under Approved Document B 2010:
        18

        1 "Must close door from any angle and against any

        2 latch ..."

        3 Is that correct?

        4 A. That's correct.

        5 Q. That's what you were emphasising earlier, that this

        6 statutory guidance, the LGA guide, the DCLG sleeping

        7 guide, they're all clear about self-closing devices.

        8 A. They're all entirely aligned about the provision of

        9 self-closers, and the guidance since the 1970s has been

        10 very clear about what the role of a self-closer is and

        11 why it is so important.

        12 Q. Do you want to just explain why it's so important?

        13 I mean, it may sound obvious, but --

        14 A. To shut the door. To shut the door after a person, to

        15 make sure the door can close.

        16 Q. Yes.

        17 A. I can't say anything else.

        18 SIR MARTIN MOORE-BICK: To make sure it does close, really.

        19 A. Did I say make sure it doesn't close?

        20 SIR MARTIN MOORE-BICK: No, no, you said "can".

        21 A. No, to make sure it does close, yes. Yes.

        22 MS GRANGE: I now want to run through your conclusions about

        23 the performance of the flat doors based on your

        24 investigations.

        25 A. Yes.
        19

        1 Q. Primarily we're looking at the 106 Masterdor doors that

        2 were replaced.

        3 A. Yes.

        4 Q. You say in your report that you surveyed eight of these

        5 Masterdor doors during your site visit; is that correct?

        6 A. Yes.

        7 Q. You've noted a large number of problems with these

        8 doors.

        9 A. Yes.

        10 Q. I just want to pick up on some of the key ones. There's

        11 a lot of detail in appendix I --

        12 A. Yes.

        13 Q. -- but I want to focus on some of the key points you

        14 seem to be making.

        15 You say that the 106 doors were not tested for

        16 30 minutes' integrity from both sides of the door and,

        17 therefore, were not compliant with the requirements of

        18 Approved Document B; is that correct?

        19 A. Yes. So there's the door installed in Grenfell Tower

        20 and then there's the door that was tested and used as

        21 the relevant test evidence. So the test door was tested

        22 from one side only. But as you know, the test door type

        23 isn't what was installed at Grenfell Tower.

        24 Q. I understand.

        25 A. Okay? So the door was tested from one side only.
        20

        1 Q. Yes.

        2 A. Yes.

        3 Q. It's worthwhile, I think, at this point, noting that you

        4 have referred to the BRE global test report that the MPS

        5 obtained on one of these doors.

        6 A. Yes.

        7 Q. They tested one of these doors on 13 February 2018 for

        8 fire integrity.

        9 A. Yes.

        10 Q. The door achieved just 15 minutes integrity; is that

        11 correct?

        12 A. That's correct, and with the glazing panel in it.

        13 Q. I'd like to look at that test report because I think

        14 that's useful. If we can bring that up, there we go,

        15 this is the test report MET00019996.

        16 If we go to internal page 25 of this test report, if

        17 you can perhaps zoom in on that image.

        18 Here we have the door, and it says in the label:

        19 "Exposed face of specimen at time of first integrity

        20 failure (15 minutes)."

        21 Can you talk us through what we're seeing in that

        22 picture?

        23 A. Well, I mean, it's a bit blurry. So what I see is flame

        24 coming out presumably where the glazed area is in that

        25 door.
        21

        1 Q. Yes.

        2 A. That's around here (Indicates).

        3 Q. Is it potentially significant that we're also seeing

        4 smoke coming from the sides of the door?

        5 A. Yes, so that's a bit complicated, actually, because if

        6 that smoke isn't hot enough, by definition, in the test,

        7 it doesn't matter that that smoke is coming around the

        8 door. And I have to be honest that I also witnessed

        9 some other doors being tested, and it really struck me

        10 during those tests that that was deemed to be

        11 acceptable.

        12 Q. If we then go just one page on at page 26, that is the

        13 door at 28 minutes, is that right, at the end of the

        14 test?

        15 A. Yes.

        16 Q. I wanted to kind of --

        17 A. Yes.

        18 Q. So we can see the difference between --

        19 A. So total failure of the door.

        20 Q. Yes.

        21 You note that this is a retrospective test of a door

        22 taken from Grenfell Tower.

        23 A. Yes.

        24 Q. And it's obviously a glazed specimen that we're looking

        25 at here.
        22

        1 A. Yes.

        2 Q. In those circumstances, how representative do you think

        3 this test result to be of the those doors' performance?

        4 A. I think it was nearly half the doors had glazing in

        5 them.

        6 Q. Yes.

        7 A. Yes.

        8 Q. Where there's a glazed door, you consider this test

        9 evidence to be relevant?

        10 A. Yes. Well, my understanding is this is the door that

        11 was installed at Grenfell Tower, but the BRE and the

        12 police would need to just confirm all of that. But my

        13 understanding is that is one of the doors.

        14 Q. Yes.

        15 A. And so it is representative.

        16 Q. On glazing, that's another one of the issues you've

        17 identified in your report, you've noted that the glazed

        18 test specimen used for the original fire test report in

        19 support of those flat doors used a different

        20 specification of glass to that which was actually used

        21 in the 2011 upgrade; is that correct?

        22 A. That's correct, they're not described the same way, and

        23 obviously if we wanted to proceed with that further, it

        24 would be useful to understand exactly the exact

        25 technical specification that was proposed and what was
        23

        1 installed in the tower. But I personally don't need

        2 that level of detail because I'm clear the door failed

        3 in the test.

        4 Q. You say for that reason that that test evidence that

        5 came with the doors is not relevant test evidence in

        6 circumstances where the glazing is different.

        7 A. Exactly. So it's made very clear in the statutory

        8 guidance document the importance of taking care with the

        9 glass, and so when one is offering a door with glazing

        10 for installation in a residential building, it's

        11 important to make sure that glazed element is a glazed

        12 element that's been tested satisfactorily, and will

        13 allow the door to perform to the required standard.

        14 Q. You've also concluded that the flat doors don't comply

        15 with certain cold smoke leakage requirements --

        16 A. Yes.

        17 Q. -- in ADB, table B1. What you've the said is there's no

        18 information in the test report about cold smoke leakage

        19 performance.

        20 A. Exactly. So there's two points here.

        21 So in terms of works, there is no technical

        22 specification for the works, so I don't know who asked

        23 for what type of door. I have to rely on a spreadsheet

        24 from Masterdor, and they are for FD30 doors with no S

        25 stated. The test report I have is also FD30 with no S
        24

        1 test done.

        2 So you could say they match, but I don't understand

        3 why an FD30 door was installed, when an FD30S door

        4 should have been installed.

        5 So it's two separate points.

        6 S doesn't appear to have been called for, and S was

        7 not provided.

        8 Q. S is about cold smoke leakage; yes?

        9 A. Yes, it is.

        10 Q. Again, can you just explain to us what cold smoke

        11 leakage is referring to, in simple terms?

        12 A. So the door in its final form, with any fixtures and

        13 fittings, any intumescents, anything at all needed for

        14 fire resistance, is put under pressure and the leakage

        15 measured. It has to be lower than a defined value, and

        16 that represents what the door would do when smoke is

        17 attempting to pass through it.

        18 Q. You've also concluded that the doors contained different

        19 hardware, including locks, hinges, letter plates, letter

        20 boxes, than in the test reports.

        21 A. That's correct.

        22 Q. Can you explain why that is potentially so significant,

        23 different hardware in doors?

        24 A. Yes. Well, the statutory guidance document, Approved

        25 Document B, makes that clear, and the test reports for
        25

        1 fire doors makes that clear.

        2 It seems to be because, if you want to use the

        3 phrase, getting the door through the test, it's

        4 a sensitive business. So any piece of metal, any gap,

        5 you know, so locks or letter boxes, may act as a heat

        6 transfer route, as a flame spread route or a hot smoke

        7 spread route, and so would cause the door to fail.

        8 So a door, when sold, can be detailed up to perform

        9 perfectly satisfactorily, but then it must be installed

        10 that way too because of those sensitivities. And

        11 I consider those sensitivities to be very well

        12 documented as an issue.

        13 Q. In terms of intumescent seals, in your report you've

        14 compared the intumescent seals that were specified for

        15 the 109 replacement doors with those included in the

        16 test specimens.

        17 A. Yes.

        18 Q. Again, you found that none were specified with the same

        19 intumescent seals as the test report.

        20 A. So some of the seals near the locks and the hinges were,

        21 but the main seals around the leaf were not. So the

        22 majority of the seals were not as communicated in the

        23 test report provided as being relevant.

        24 Q. In terms of self-closing mechanisms --

        25 A. Yes.
        26

        1 Q. -- you've noted that the door-closers which were

        2 specified for the refurbishment were not the same as the

        3 door-closer in the one specimen that was tested; is that

        4 correct?

        5 A. That is correct. It was an overhead closer, that

        6 classic arm closer, in the test, and most of the doors

        7 I saw had that internal closing device using the chain.

        8 But you'll see in the detail in my report, for

        9 example, there's photos from London Fire Brigade after

        10 the fire where they did observe a door, one door, with

        11 an overhead closing device. But I don't know why that

        12 was there, because the chain-closing mechanism appears

        13 to have been the one specified during the door

        14 replacement works.

        15 Q. You've highlighted in your report several instances of

        16 door-closers malfunctioning or breaking based on the

        17 written evidence you've seen.

        18 Do you agree that we've heard more examples of that

        19 in the oral evidence from the BSRs during the course of

        20 the BSRs' evidence?

        21 A. Yes, I do.

        22 Q. You've also noted, in terms of frequency of inspections,

        23 in your report that the LGA guide suggests six-monthly

        24 inspections and preventative maintenance for

        25 fire-resisting doors.
        27

        1 A. Yes, that's correct.

        2 Q. Aimed at identifying defects such as missing or

        3 ineffective closing devices; is that correct?

        4 A. That's correct.

        5 Q. You also note that there's a relevant British Standard,

        6 BS 8412 2008, which recommended six-monthly checks of

        7 the door-closers.

        8 A. Yes.

        9 Q. You also say the DCLG guidance suggested more

        10 frequently; perhaps monthly checks.

        11 A. Yes. I think they're more making sure, I would consider

        12 when you're doing a monthly inspection, if the door is

        13 able to close, and the six-monthly inspection would be

        14 a careful review of the door.

        15 Q. You've noted that the TMO policy was for fire risk

        16 assessments on an annual or two-yearly basis; is that

        17 correct?

        18 A. Apparently so.

        19 Q. So if that -- and we'll have to look at the evidence on

        20 this in Phase 2 -- was the only time the door-closers

        21 were checked, for example, hypothetically, what you're

        22 drawing attention to is that there's other guidance that

        23 suggests more frequent inspections.

        24 A. Yes. So I haven't dealt with maintenance yet. So, yes,

        25 the frequency seems to be different, but in Phase 2 I'll
        28

        1 be more interested in the quality of the inspection and

        2 the maintenance that occurred in the tower.

        3 Q. Before we come on to the impact of these issues on the

        4 events of the night, just on the 14 doors that were not

        5 replaced --

        6 A. Yes.

        7 Q. -- in 2011, that's 12 leaseholder doors and two tenanted

        8 doors, you say in your report you can't confirm the

        9 specification of the original 1970s installation or any

        10 subsequent replacement of the doors because they've now

        11 been lost in the fire.

        12 Is that correct?

        13 A. Yes. So I couldn't inspect the doors because they're

        14 all gone, and no relevant paperwork has been made

        15 available to me about them.

        16 The only thing I know was what the risk assessor

        17 said to the TMO, which is in my report, and he

        18 considered those doors to be fire retardant, which isn't

        19 a relevant term regarding fire-resisting doors.

        20 Q. You've said in your report that the compliance of these

        21 doors cannot be determined at this time, and that

        22 because the doors have been lost, their compliance will

        23 not be able to be determined. Is that your position?

        24 A. Unless the TMO or other parties produce the paperwork

        25 and information they relied upon when they decided the
        29

        1 performance of those doors.

        2 Q. I now want to look at the impact of those issues that

        3 you've identified on the events of the night.

        4 You summarise the potential contribution that these

        5 issues may have caused in your report at

        6 paragraph 19.5.28. Can we go to that. That's

        7 BLAS0000019 at page 20.

        8 You have crystallised for us here what you say are

        9 a number of ways in which the flat entrance doors failed

        10 to control the spread of smoke and fire to the

        11 lobbies --

        12 A. Yes.

        13 Q. -- in these paragraphs. I just want to take you through

        14 them and just summarise.

        15 A. Okay.

        16 Q. So you say in a):

        17 "a) Failure to prevent the spread of smoke and flame

        18 by leakage through gaps between the door leaf and door

        19 frame."

        20 Is that correct?

        21 A. That's correct, and that's important in the early stages

        22 of a fire, or if one is waiting some time in a flat

        23 remote from a hazard and smoke is spreading from the

        24 lobby.

        25 Q. In b) what you're drawing attention to there I think is:
        30

        1 "b) Failure of the fire door to resist the spread of

        2 fire and smoke from a flashover fire within an apartment

        3 due to the presence of multiple untested components

        4 within the doors ..."

        5 A. Yes.

        6 Q. That would include hardware, glazing, et cetera; is that

        7 correct?

        8 A. That's correct. So once a severe fire happened near

        9 a door or there was a flashover in an apartment or any

        10 kind of localised heating condition, failure of the door

        11 would be expected in theory, and obviously it's

        12 supported by witness evidence.

        13 Q. Yes.

        14 At c) you've got:

        15 "c) Failure of the fire door to resist the spread of

        16 fire and smoke from a flashover fire within the

        17 apartment due to the presence of glazing ..."

        18 Expected, you say, to cause early failure based on

        19 the test evidence.

        20 A. That's correct, yes.

        21 Q. At d) we have:

        22 "d) Failure of an unknown number of doors to

        23 self-close after an occupant escape."

        24 Is that correct?

        25 A. That's correct. Yes.
        31

        1 Q. You also say in the next paragraph, if we could go to

        2 the next page at the top of your report:

        3 "19.5.29. The fire doors also failed in a second

        4 way; to resist the spread of fire and smoke from the

        5 lobby — given that fire doors are required to perform in

        6 both directions."

        7 A. That's correct.

        8 Q. Is that the key point you're making there?

        9 A. Again, I'm back to this issue of: what is the hazard in

        10 a specific location and at a specific time? That's very

        11 important.

        12 So in the event that one was in a flat with no fire

        13 within it, it may be there was a hazard in the lobby

        14 that you required protection from.

        15 Q. Do you have a current view as to which of those are

        16 potentially the most significant on the night?

        17 A. I want to look at the hazard in a specific location

        18 before I give a final opinion. I do consider the fire

        19 doors to be a very significant fire safety measure in

        20 general, and I think, therefore, their contribution to

        21 the events on the night require very careful review.

        22 Q. What would you say to the point which can be made that

        23 the doors, even if compliant, would've only had

        24 30 minutes' integrity?

        25 A. That's correct, yes. So it's not 60 minutes, it's not
        32

        1 120 minutes, it is 30 minutes.

        2 Q. Given that such doors are not intended to provide

        3 indefinite protection, isn't it inevitable that they're

        4 going to fail at some point?

        5 A. It is indeed inevitable that they're going to fail at

        6 some point, but the important point is what happens

        7 before that failure occurs.

        8 So I don't think it's acceptable to consider,

        9 because they might fail anyway, it doesn't really matter

        10 what happens in the time period before that. I think

        11 that's very important, particularly for people who are

        12 waiting in flats.

        13 Q. I've been asked to put to you the following proposition:

        14 to the extent the flat entrance doors were

        15 non-compliant, that had at most only a limited effect on

        16 the spread of fire and smoke and the outcome of fire.

        17 Would you agree with that?

        18 A. I don't agree with that at all.

        19 Q. Do you agree that --

        20 SIR MARTIN MOORE-BICK: Would you like to explain why?

        21 A. I think that those fire doors were needed for so many

        22 different reasons as a function of where one was living

        23 or waiting for rescue in the tower. So we have

        24 conditions where -- you know, protection from fire or

        25 protection from smoke, either in one's own apartment, in
        33

        1 a lobby, and, say, from another flat on the floor.

        2 So wherever you're located, there may be nearby fire

        3 or remote fire, and you are relying on those lines to

        4 prevent those products eventually reaching your

        5 location.

        6 I'm not avoiding the answer, that's why I emphasised

        7 at the start today the location of the flat and the

        8 location of the person is so important in terms of what

        9 that fire protection measure was needed for. And doors

        10 protect against fire and smoke, and so I would give

        11 a view, therefore, on how those doors performed, in the

        12 lobbies, for the lobbies, for the flats, when I carry

        13 out my risk assessment in Phase 2. Okay?

        14 So it's not appropriate, therefore, either to simply

        15 say they all failed, they all have the same

        16 contribution. It's relevant to location, and the hazard

        17 they were required to protect a person from.

        18 MS GRANGE: So will it be relevant to your analysis at

        19 Phase 2 that we can see examples from the BSRs' evidence

        20 of some residents where they are talking about smoke

        21 coming in through the front door, whether underneath the

        22 bottom, around the sides, a couple of clear examples

        23 through the letterbox?

        24 A. That's correct.

        25 Q. Those are all areas you're interested in?
        34

        1 A. I'm very interested in those areas.

        2 Q. I'm not going to go through them all now, but there are

        3 a number of examples from the BSRs' oral evidence.

        4 A. Yes, there are, and that's why, again, I don't want to

        5 give any kind of overall opinion on one measure.

        6 I think there's a really important piece of analysis per

        7 flat, per lobby, required to give a fair view on what

        8 those systems did.

        9 Q. Because would you accept that there are some examples of

        10 flat doors appearing to fair well on the night -- for

        11 example, Antonio Roncolato[sic], who was there for

        12 a very long time, who was the last person rescued --

        13 A. I think that's a really good example, actually. So the

        14 hazard in that flat was entirely different to, for

        15 example, flat 1 up at level 23. So when I'm looking at

        16 the doors in that context, I will explain the hazard in

        17 that flat and why it was so different to the hazard in,

        18 for example, flat 1 at level 23, and so explain the

        19 relevance of the non-compliant fire doors.

        20 Q. Does it often come down to a matter of timing in terms

        21 of, as you said before, people staying in their flats

        22 and waiting in accordance with the stay-put instruction,

        23 and the length of time that that door is protecting them

        24 from hazards?

        25 A. That's quite a general question and I would not want to
        35

        1 answer it generally. I don't think it would be

        2 appropriate. It's all about specific hazards and

        3 specific protection needed.

        4 Q. Would it be possible to estimate how much smoke might

        5 seep out from a representative, closed, non-compliant

        6 door, as compared with a compliant door? Would it be

        7 possible to do that exercise --

        8 A. I'm sure there's somebody clever somewhere who can run

        9 a CFD analysis and work that out, if it was important.

        10 Q. Do you think that exercise would be a useful one?

        11 A. At the moment, I don't have any plans to do that, but

        12 I'll let you know if I change my mind in Phase 2.

        13 Q. I think you've answered this, but in terms of doing

        14 a flat-by-flat analysis, of the impact, for example of

        15 no self-closing device or inadequate self-closing

        16 device, whether the door nevertheless shut or was shut

        17 behind, is that the kind of analysis you're flagging for

        18 Phase 2?

        19 A. Exactly, exactly.

        20 Q. Would you agree that the presence of smoke in the

        21 lobbies is most likely to have been caused by

        22 a combination of factors which may have also included

        23 flat entrance doors being held open or propped open,

        24 flat entrance doors being broken down by firefighters to

        25 fight fires? Would you agree that all of those factors
        36

        1 are going to be relevant in terms of the presence of

        2 smoke on lobbies?

        3 A. All those factors will be relevant, but I don't think we

        4 should overstate those other features in terms of

        5 quantity of location that actually occurred. So saying

        6 the Fire Brigade broke down doors, you know, it sounds

        7 as if that was happening -- I think it's a bit of

        8 a sweeping statement, isn't it? So there's very

        9 specific activity on specific floors and I will look at

        10 the doors carefully in that regard.

        11 In terms of smoke in the lobby, I've made clear

        12 there are other and there may be more contributory

        13 features also, and I will take each measure in turn.

        14 Q. Just in terms of the early presence of smoke on the

        15 lobbies, some firefighters say they were very surprised

        16 to find smoke in lobbies at a very early stage in the

        17 fire. We get the evidence of, for example, Badillo, who

        18 is going up, and Firefighter Secrett similarly.

        19 Do you have any view at this stage about what

        20 factors might have been important in terms of explaining

        21 that early presence of smoke in some lobbies or would

        22 you give the same answer?

        23 A. Well, I mean, again, I want to do the

        24 location-by-location review, but there was a trend in

        25 terms of the location of the external flame front and
        37

        1 the progression of early smoke in the lobbies.

        2 So clearly there was a smoke spread route from the

        3 cladding fire out to the lobby.

        4 Q. Will part of your analysis look at the flat 6s and

        5 specific --

        6 A. Yes.

        7 Q. -- importance of the flat 6s and their self-closing

        8 device or their door --

        9 A. Yes.

        10 Q. -- in the fire?

        11 A. Yes, because remember, the whole point about having

        12 a self-closer is that when a person evacuates, they

        13 don't cause harm. I don't like to -- you know, that's

        14 not a nice way of putting it, but the whole point of

        15 having a self-closer is the door closes behind the

        16 person who has evacuated and, therefore, the protection

        17 is maintained. That's why they are so incredibly

        18 important.

        19 Q. I'm now going to turn to a different but related topic

        20 of the stair doors.

        21 A. Yes.

        22 Q. For this purpose, it's really chapter 16 and

        23 appendices I and a little bit of M, but mainly I, that

        24 is relevant, if you want to make sure you have those to

        25 hand.
        38

        1 A. I think I'm okay, thank you.

        2 Q. Turning to the stair doors, therefore, in your revised

        3 report, you've done a considerable amount of work to try

        4 and ascertain the history of the stair doors at

        5 Grenfell Tower, including whether they were compliant

        6 with relevant standards over time, including looking at

        7 their original installation at Grenfell Tower; is that

        8 correct?

        9 A. Yes. So I just probably wouldn't mind being able to say

        10 that I have been contented since I wrote my report about

        11 the CP3 requirements for stair doors, but I know that

        12 other people had a lot of concern with my view, so

        13 that's why I did that extra work to try and explain with

        14 a lot of detail the performance of historic fire doors,

        15 and I've done that work. But my position remains about

        16 the CP3 requirements for those doors, because doors and

        17 ventilation together protect a lobby or protect the

        18 stair.

        19 Q. Prior to asking you some more detailed questions about

        20 that and about the stair doors in detail, can we just

        21 look at your conclusion at paragraph 19.7.27 of your

        22 report BLAS0000019 at page 45.

        23 Could I ask you to read that paragraph to yourself

        24 for a moment.

        25 A. Yes, so this is the failure to prevent smoke spread.
        39

        1 Q. Into the stairs; is that correct?

        2 A. Into the stair, yes:

        3 "The stair doors appear to be the primary route of

        4 spread of smoke and heat to the stair."

        5 Because I didn't find any other opening:

        6 "No other significant failures in the construction

        7 separating the stair from the lobby or flats has been

        8 observed."

        9 Q. Yes, and then I want to focus on the next stage. You

        10 say:

        11 "At this stage the stair doors being opened, or held

        12 open, by either fire-fighting equipment or other objects

        13 appears to be the primary failure."

        14 A. Yes, that's correct, because I didn't observe in the

        15 tower severe damage to the concrete in the staircase.

        16 Q. Yes.

        17 A. I would expect to see severe damage in the staircase,

        18 for example, if the door had entirely failed, so

        19 collapsed in some form. I haven't seen that, so I can't

        20 say they failed that way.

        21 So I have to assume, therefore, that any heating

        22 effects I observed in the staircase, or the smoke

        23 observed in the staircase, came through the activity of

        24 the doors.

        25 Q. Would you agree we need to bear that in mind when it
        40

        1 comes to any potential problems in terms of the

        2 performance of these stair doors, your conclusion there?

        3 A. I don't know what you mean.

        4 Q. You are saying you think the primary failure appears to

        5 have been open doors. Do we need to bear that in mind

        6 when we then come and look at your detailed analysis?

        7 A. Oh, yes. I think I've been quite clear on that, yes.

        8 Q. Just in general, can you explain the importance of stair

        9 doors in a building like Grenfell Tower with a single

        10 staircase?

        11 A. Yes. So they have two roles: to prevent smoke from the

        12 fire flat, which may have entered the lobby, entering

        13 the staircase, and so preventing escape from above the

        14 fire.

        15 The second role is -- and that's why it's to

        16 a higher standard, actually -- again to prevent smoke

        17 entering the staircase, to protect firefighters who are

        18 moving up and down in that staircase, carrying out their

        19 various duties.

        20 Q. As you say, because of that dual role, it has

        21 a particularly protected status, that staircase.

        22 A. Yes, it does, yes.

        23 Q. Does that make it all the more important as a safety

        24 feature?

        25 A. All the more important -- I think it's important, yes,
        41

        1 I think it's important. I'm probably not ready to say

        2 "all the more important" about anything just yet.

        3 MS GRANGE: I'm about to go to a more detailed passage. I'm

        4 happy to stop now or carry on in terms of a break.

        5 SIR MARTIN MOORE-BICK: Would you like a break at this

        6 point?

        7 THE WITNESS: I'm okay, but would it be another three hours

        8 if you don't have a break or 20 minutes?

        9 SIR MARTIN MOORE-BICK: I would suggest we have a break now.

        10 THE WITNESS: Okay.

        11 SIR MARTIN MOORE-BICK: And maybe have another one in about

        12 an hour's time.

        13 THE WITNESS: Okay, perfect.

        14 SIR MARTIN MOORE-BICK: So you go with the usher. Don't

        15 talk to anyone about your evidence while you're out of

        16 the room.

        17 THE WITNESS: Thank you very much.

        18 SIR MARTIN MOORE-BICK: We'll come back at 11.05.

        19 All right, 11.05, then, please.

        20 (11.00 am)

        21 (A short break)

        22 (11.10 am)

        23 SIR MARTIN MOORE-BICK: All right?

        24 THE WITNESS: Yes.

        25 SIR MARTIN MOORE-BICK: Happy to go on?
        42

        1 THE WITNESS: Yes.

        2 SIR MARTIN MOORE-BICK: Yes, Ms Grange.

        3 MS GRANGE: Thank you.

        4 I just have a small correction to make to the

        5 transcript and an apology.

        6 At page 35 of the transcript I'm recorded as saying

        7 Antonio Roncolato was the last person to be rescued. In

        8 fact, that's not correct; it was Elpido Bonifacio from

        9 flat 83 who was the last person rescued. I ought to

        10 correct that and apologise. Thank you.

        11 SIR MARTIN MOORE-BICK: Thank you.

        12 MS GRANGE: So in terms of the stair doors.

        13 A. Yes.

        14 Q. You have concluded that all 20 doors on levels 4 to 23

        15 are original 1972 construction doors; is that correct?

        16 A. That's correct.

        17 Q. Can we just look at a couple of pictures of those doors,

        18 just to remind ourselves what they look like.

        19 A. Yes.

        20 Q. You've got two pictures that are helpful in your report,

        21 BLAS0000030 at page 78, figure I.25.

        22 If we can zoom in on that.

        23 So this is a level 6 stair door; is that correct?

        24 A. Yes, it is.

        25 Q. If we can look at the figure at the bottom, figure I.26,
        43

        1 we're going to come back to this picture and look in

        2 a moment, but there we see what the edge looks like of

        3 those doors. You say brush seal present.

        4 I'm not going to ask you questions about that right

        5 now, but this is just to remind ourselves what those

        6 doors look like. So that's the door on level 6.

        7 Can we also look at the level 19 stair door. That's

        8 BLAS0000030 at page 82, figure I.30.

        9 So this is the level 19 stair door after the fire.

        10 A. Yes.

        11 Q. So we can see the single vision panel, the same as we

        12 saw on level 6.

        13 A. Yes.

        14 Q. And you've drawn attention to the rail -- is that a kind

        15 of horizontal supporting --

        16 A. Exactly, yes.

        17 Q. The stile, is that a kind of vertical --

        18 A. Yes.

        19 Q. And then we can also see a little bit of what the edge

        20 looked like.

        21 A. Yes.

        22 Q. So that's the level 19 stair door.

        23 Now --

        24 A. And --

        25 Q. -- as we discussed previously --
        44

        1 SIR MARTIN MOORE-BICK: Sorry, you --

        2 A. Yes, sorry. Just also, actually, because of what you

        3 asked me earlier, if you just have a look around the

        4 door on the concrete, you can't see any spalling

        5 effects, but you can see the significant charring of the

        6 stair door.

        7 You were asking me earlier about why I had chosen

        8 opening rather than a total failure.

        9 So it's the conditions around the door on the stair

        10 side are very important in understanding that. Just

        11 that picture is a good one.

        12 MS GRANGE: Yes, that's helpful.

        13 SIR MARTIN MOORE-BICK: We don't have a picture of the other

        14 side of that door, do we?

        15 A. We do in my report, yes, and they are very interesting

        16 too if you look at them in sequence on every level.

        17 SIR MARTIN MOORE-BICK: Yes.

        18 MS GRANGE: Yes, I think that's in your appendix of

        19 photographs.

        20 SIR MARTIN MOORE-BICK: And they suggest that the doors

        21 actually responded well?

        22 A. So the doors remained stable, they haven't collapsed.

        23 They have undergone significant charring due to heat,

        24 and you can see, very unfortunately, the condition of

        25 the lobby. This is level 19, I think.
        45

        1 Q. Yes.

        2 A. Okay? So that door has remained in place, despite those

        3 conditions.

        4 SIR MARTIN MOORE-BICK: Thank you.

        5 MS GRANGE: Yes.

        6 As we discussed previously, you consider that the

        7 design basis for Grenfell Tower was CP3 1971, and you've

        8 explained in your report that the CP3 1971 requirement

        9 for access to the main stairway was for something called

        10 type 2 doors; is that correct?

        11 A. That's correct.

        12 Q. Can we just look at that definition. If we go within

        13 your report to BLAS0000030 at page 67, under I5.2.5.

        14 A. Yes.

        15 Q. And if we can zoom in on the type 2 door definition.

        16 Thank you.

        17 A. Yes.

        18 Q. You've concluded that the type 2 door must have

        19 a 25-millimetre rebate; is that correct?

        20 A. Yes, so that's pasted directly in from CP3, and for

        21 a type 2 door, it has the 30-minute performance

        22 requirement for collapse and passage of flame, and

        23 a rebate is listed there also of 25 millimetres. And,

        24 again, the self-closing device.

        25 Q. You understand that that's a requirement of
        46

        1 a 25-millimetre rebate rather than a testing condition;

        2 is that correct?

        3 A. I don't understand the question, I'm really sorry.

        4 Q. You're saying that to comply with the type 2 door, it

        5 needed to have a 25-millimetre rebate; is that correct?

        6 A. Yes, it did, yes.

        7 Q. Just --

        8 A. I'm sorry, I understand now.

        9 Yes, it did, and test evidence that exists from the

        10 time supports the reason why that number is written into

        11 the 1971 guidance, yes.

        12 Q. In general, can you just explain, first of all, what

        13 a rebate is, just so everybody's clear --

        14 A. Yes.

        15 Q. -- and what the effect is of a rebate on, for example,

        16 freedom from collapse and passage of flame.

        17 A. Oh, okay.

        18 So a rebate is -- I think they used to call them

        19 like door-stops or smoke-stops in the old days, and it's

        20 just a cut in a piece of timber. So when you push the

        21 door, it can't get through the frame at that part. So

        22 there's a little slot -- I'm trying to see if there's

        23 something to help me.

        24 SIR MARTIN MOORE-BICK: Are we talking about the depth of

        25 what one might call the doorjamb? How far into the
        47

        1 setting the door will go?

        2 A. It's how far into the setting, how far in --

        3 SIR MARTIN MOORE-BICK: Yes.

        4 A. -- and how wide the setting is. So it's got two --

        5 SIR MARTIN MOORE-BICK: Yes, all right.

        6 A. It's an L shape, okay? And I know there's been huge

        7 interest in rebates. There are drawings in my report

        8 with all that I mentioned through all the different

        9 types of doors.

        10 But it's dimensioned and so the door can't move any

        11 further, if you will.

        12 MS GRANGE: Yes, yes.

        13 That return on the rebate is potentially important,

        14 is it, in terms of the freedom from collapse and the

        15 passage of flame or smoke through the door, the L-shape

        16 and the width of that L-shape?

        17 A. Yes. So I refer to -- actually, I brought them -- tests

        18 done in the 1970s by Morris, and it's referenced in my

        19 report so people can read it, and he tested a whole

        20 series of doors with the same leaf as appears to have

        21 been installed in Grenfell Tower with different rebates,

        22 and he found the dimensions to be very important. He

        23 actually concluded, particularly on the 12.5-millimetre

        24 rebate, it prevented the ability for a door to achieve,

        25 in his testing regime, anything more than 12 minutes'
        48

        1 fire resistance.

        2 Q. Yes.

        3 A. Back then.

        4 Q. We'll come back to that in a moment.

        5 Just sticking for a moment with the type 2 doors

        6 under CP 371, that also makes clear that it has to have

        7 a self-closer; is that correct?

        8 A. That's correct.

        9 Q. So, again, we see self-closers there, right back from

        10 the 1970s.

        11 You also note in your report that the DCLG sleeping

        12 guide is again relevant, which requires such doors to be

        13 self-closing; is that correct?

        14 A. Yes.

        15 Q. You've also mentioned in your report the LGA guidance

        16 which we looked at before in purpose-built blocks of

        17 flats.

        18 We can go back to that if you like, but as we noted

        19 earlier, that required at least upgraded FD30S doors; is

        20 that correct?

        21 A. Yes.

        22 Q. Shall we look at that again?

        23 A. Sorry, it's actually not clear on stair doors. Sorry,

        24 nearly said the wrong thing. It's not clear at all on

        25 the replacement or the upgrade of stair doors. It's
        49

        1 very clear on flat entrance doors.

        2 Q. Yes. Let's have a look at that, let's go to

        3 CTAR00000033, page 98.

        4 So if we zoom in on the table again, and we're on

        5 the second-to-last-bullet point:

        6 "• In ventilated lobbies and corridors, travel

        7 distances of ten to 15m may be acceptable, providing all

        8 doors to the common corridor or lobby are at least

        9 'upgraded FD30S' doors ... and the smoke ventilation

        10 comprises PVs or AOVs."

        11 I think you say in your report that on one reading

        12 of that, "all doors to the common corridor or lobby"

        13 could be interpreted as all doors including the stair

        14 door.

        15 A. In my opinion, it should include the stair door.

        16 Q. You've noted that the LGA guidance only recommends

        17 upgrading the door so that it's classed as an upgraded

        18 door, FD30S door, where the existing door satisfied the

        19 specification at the time of construction and was

        20 therefore something called a notional FD30 door.

        21 A. Yes.

        22 Q. Let's look at that in the guidance. So if we go to

        23 page 101 within this document, paragraph 62.17.

        24 Here it's said in this guidance that it's not

        25 practical to test existing doors. Three options exist.
        50

        1 Here what you're referring to is bullet point 1, you

        2 can:

        3 "• accept the door as it is, provided it is a good

        4 fit in its frame and that it satisfied the standard

        5 applicable to fire-resisting doors at the time of

        6 construction of the building or manufacture of the door

        7 ('notional FD30' door)."

        8 Is that correct?

        9 A. Yes, it is, yes.

        10 Q. Again, it's just worth looking at the definition of

        11 an upgraded FD30S door. That's page 182 within this

        12 document.

        13 A. Yes.

        14 Q. I think it's right at the very top.

        15 A. Yes, it is.

        16 Q. The notional FD fire-resisting door is:

        17 "A door assembly that satisfied the current

        18 specification, or fire resistance test, for 30 minutes

        19 at the time of construction of a block of flats or

        20 manufacture of the door."

        21 That's the definition of that; is that correct?

        22 A. Yes, that's correct.

        23 Q. Let's then look at what you saw when you inspected the

        24 doors.

        25 You say in your report that you inspected one door
        51

        1 on level 6 but you consider that door to be

        2 representative; is that right?

        3 A. Yes, that's correct, based on photographic evidence.

        4 Q. So it does appear from what we've seen that all those

        5 doors between levels 4 and 23 were of the same make and

        6 construction; is that correct?

        7 A. It appears to be the case, yes. There's no

        8 documentation available.

        9 Q. What you've noted is that the stair doors had a rebate

        10 depth of 12 millimetres; is that correct?

        11 A. That's correct.

        12 Q. I think we have a picture of that we can look at

        13 BLAS0000016 at page 23.

        14 I think this picture might help us in terms of --

        15 does that show the rebate?

        16 A. Not really, sorry.

        17 Q. Does that help us -- sorry -- on showing the rebate?

        18 A. No.

        19 Q. No. You can see the rebate when you open the door?

        20 A. Yes. When you open the door, you can look in, you see

        21 the edge of the door, where you push the door.

        22 Q. Yes.

        23 A. On the frame on the left there --

        24 Q. Yes.

        25 A. -- you'll just see the little stop made of timber.
        52

        1 Q. You say in your report that that rebate depth of

        2 12 millimetres is too small to comply with the

        3 requirement for type 2 doors under CP3 1971; is that

        4 correct?

        5 A. That's correct.

        6 Q. But what you've said is, following your investigations,

        7 the stair doors appear to have been constructed

        8 potentially as a class A door, a number 3 class A door,

        9 under the London constructional amending bylaws; is that

        10 correct?

        11 A. That's correct.

        12 Q. Right at the beginning of your evidence, we looked at

        13 the different regimes that were in place.

        14 A. Yes.

        15 Q. There were these London constructional bylaws under the

        16 relevant London Building Acts.

        17 A. Yes.

        18 Q. That defines something called a class A door.

        19 A. A type A.

        20 Q. A type A

        21 A. A type A door, yes.

        22 Q. I apologise, a type A door.

        23 A. Yes.

        24 Q. What you've concluded is that that 12-millimetre rebate

        25 would satisfy that standard?
        53

        1 A. Yes. So the London constructional bylaws provide four

        2 forms of type A door. The performance resistance is

        3 actually 30 minutes, which is the same as a type 2 door

        4 in CP3. Okay? So the bylaw door and, let's say, the

        5 CP3 door, the performance resistance is written on paper

        6 the same way.

        7 The issue with the type doors, so the bylaw doors,

        8 is it also gives examples of construction forms one can

        9 select to comply with the type A requirements, and all

        10 of them are stated as being allowed to have a rebate of

        11 12.5 millimetres.

        12 Q. In your report, you go on to say -- and this is what you

        13 were touching on earlier about the Morris research in

        14 the 1970s -- that based on certain research you've done,

        15 that you've identified from the early 1970s, you've

        16 concluded that, in fact, this door may only achieve

        17 20 minutes' integrity and 30 minutes' stability to the

        18 standard applicable at the time of construction; is that

        19 correct?

        20 A. Yes, so he discovered -- so doors with that rebate were

        21 commonly available, let's say, and in his tests he

        22 discovered that once the rebate was 12.5 millimetres,

        23 the resistance could drop as low as 12 minutes.

        24 If the rebate was increased to 25 millimetres and

        25 intumescent strips were also provided to the door leaf
        54

        1 we have at Grenfell Tower, and was very carefully

        2 fitted, you could get that door up to a 30-minute --

        3 30/20 standard.

        4 Q. So as you say, that was only if what you refer to as

        5 tolerances of fit were controlled to less than

        6 1.5 millimetres.

        7 A. Exactly.

        8 Q. Can you help us, what are tolerances of fit?

        9 A. So he observed on the test that unless the door to frame

        10 the gaps around the door leaf were very tiny -- the

        11 paper is very interesting to read -- unless they were

        12 literally down at 1 millimetre or 2, coupled with

        13 a 12.5-millimetre rebate, and even with the

        14 25-millimetre rebate, with that type of door leaf, the

        15 rail and stile leaf, it really altered their fire

        16 performance.

        17 Q. What you say is you've carefully examined the door and

        18 they do seem very similar to these half-hour fire check

        19 doors referred to in a British Standard from 1951; is

        20 that correct?

        21 A. That's correct. So the door leaf with the rail and

        22 stile type, so the timbers, if you will, as to how the

        23 leaf is made, are the same as something called

        24 a British Standard fire check door. They were

        25 considered to offer some performance, but not full fire
        55

        1 resistance performance.

        2 So for a 30-minute door, full fire resistance was

        3 30 minutes, preventing collapse for 30 minutes,

        4 integrity for 30 minutes. A fire check door, the

        5 collapse regime of 30 minutes was retained, but you

        6 couldn't get the integrity at 30 and so a fire check

        7 door was 20 minutes instead.

        8 So they were considered to act as a fire door but

        9 with a lower performance.

        10 Q. Yes.

        11 A. With that rail and stile leaf.

        12 Q. So is it on that basis that you consider the performance

        13 of that door, the class A door, doesn't satisfy the same

        14 stability and integrity requirements of a type 2 door

        15 under CP3 1971?

        16 A. That's correct.

        17 Q. You've highlighted in your report that you consider it

        18 might be worth thinking about an amendment to the

        19 relevant guidance, including the LGA guide, because you

        20 think it might have to flag up that there may be

        21 an entire category of doors still present in tower

        22 blocks today --

        23 A. Yes.

        24 Q. -- which would've met these lower London constructional

        25 bylaw standards --
        56

        1 A. That's correct.

        2 Q. -- but which in fact have a proven lower performance

        3 standard than other doors installed in the 1970s.

        4 A. Exactly.

        5 Q. I think you make clear that even if you upgrade these

        6 doors, so you put in smoke seals, intumescent strips,

        7 the performance is potentially still concerning --

        8 A. Exactly.

        9 Q. -- because of those original issues --

        10 A. Exactly, to do with the closeness of fit and whatever

        11 rebate is installed in that building or this building.

        12 That's very well documented in various papers. I've

        13 given the publications in my report.

        14 Q. Let's just go back and look at figure I.26 on

        15 BLAS0000030, at page 78, and look at what we see in --

        16 yes, if we could blow up figure I.26.

        17 A. Yes.

        18 Q. It's right, isn't it, that you've done certain detective

        19 work in terms of looking really carefully at these doors

        20 and trying to work out what may have happened to them --

        21 A. Yes.

        22 Q. -- over time?

        23 A. Yes, I have, yes.

        24 Q. You note here in the label below, you say:

        25 "... (brush seal present, unknown if intumescent
        57

        1 seal present below the brush seal)."

        2 A. Yes.

        3 Q. Can you just explain to us what a brush seal is?

        4 A. Well, it can be to stop draughts, or it could be for the

        5 purposes of cold smoke.

        6 I don't know what's underneath it, I haven't done

        7 a destructive test of the door, and if, therefore,

        8 there's intumescent hidden behind it, which would act in

        9 the event of a fire to seal up the door for fire

        10 resistance purposes.

        11 Q. So just to be clear, the intumescent seal would be

        12 different to a brush --

        13 A. I think so. It would be underneath it. I showed some

        14 pictures of standard products in my report. It should

        15 be underneath there, as I understand it.

        16 Q. That's what you've said in your report; you say it's

        17 unclear whether there may be an intumescent seal

        18 underneath the brush seal.

        19 A. Yes.

        20 Q. And that only if we did a destructive analysis could we

        21 be able to definitively confirm that; is that correct?

        22 A. Yes, you'd just need to take it out of the door and have

        23 a look, yes.

        24 Q. You've also noted, based on the documents you've seen so

        25 far, that there's potentially inconsistent factual
        58

        1 evidence at this stage as to whether cold smoke seals,

        2 possibly combined with an intumescent seal, could've

        3 been retrospectively installed in order to upgrade these

        4 stair doors; is that correct?

        5 A. That's correct

        6 Q. Again, the difference between a cold smoke seal and

        7 intumescent seal -- what's the difference between those

        8 two things?

        9 A. Okay, so I think there's conflicting evidence about if

        10 works were done to the stair door, and if the works

        11 consisted of installing something as we can see here on

        12 the leaf, what exactly those works were. Okay? It's

        13 not just about if it was a cold seal or an intumescent

        14 seal.

        15 Q. Yes.

        16 A. So different parties have provided different evidence

        17 regarding whether works have been done to the stair door

        18 or not since the tower was constructed.

        19 Q. Yes.

        20 A. In reviewing photos from the time of the primary

        21 refurbishment showing seals being installed on one or

        22 two doors, I still cannot conclude what the seal was for

        23 and how many doors it was installed on or not.

        24 Q. So although, as you note, some photos have been provided

        25 by Mr Stokes that show a seal in some doors that's
        59

        1 visually similar to a combined cold smoke and

        2 intumescent seal --

        3 A. Yes.

        4 Q. -- you're not clear whether work was done to all the

        5 doors or just some of the doors --

        6 A. No.

        7 Q. -- at this stage; is that correct?

        8 A. That's correct, and I've provided a series of

        9 photographs in my report to explain why. I can see

        10 a combined seal in a photo, but I can't see that it has

        11 been consistently installed, and there's a conflict in

        12 whether works were done at all, as I've explained in my

        13 report.

        14 Q. So at this stage, can we draw any conclusions as to

        15 whether or not --

        16 A. I won't draw a conclusion about what works were done,

        17 but I acknowledge that there is a brush seal installed

        18 on some doors.

        19 Q. Yes.

        20 A. I don't know what it's for, who put it there or why.

        21 Q. Is this something that could be looked at further at

        22 Phase 2, investigated further as necessary?

        23 A. Yes. I hope the relevant information will be provided

        24 to me so I can close that out, and I intend to do

        25 a destructive test of the door myself.
        60

        1 Q. You do intend to do that now?

        2 A. Yes, yes, I do.

        3 Q. You note that the BRE has carried out testing --

        4 A. Yes.

        5 Q. -- to a stair door. That was found -- we are going to

        6 look at the test report in a second -- to have just

        7 16 minutes' integrity and 3 minutes' insulation.

        8 A. Yes.

        9 Q. If we just pull up the test report, that's MET00021780.

        10 That's the test report dated September 2018. If we can

        11 go to internal page 22 of this test report, and if we

        12 could just zoom in on that a little.

        13 A. Yes.

        14 Q. So this is the condition of the door after 16 minutes;

        15 is that correct?

        16 A. That's correct, as recorded by the BRE, yes.

        17 Q. I mean, this is one of the stair doors from

        18 Grenfell Tower?

        19 A. Yes, it is.

        20 Q. Is that correct?

        21 A. Yes.

        22 Q. We see the glazing unit, and then we can see a little

        23 bit of flame at the top.

        24 A. Exactly.

        25 Q. And smoke around the edges; is that correct?
        61

        1 A. Yes.

        2 Q. The 3 minutes' insulation is recorded at page 13 of 23.

        3 A. Yes.

        4 Q. If we go back into page 13. There we see --

        5 A. Yes.

        6 Q. -- again, can you just remind us of the difference

        7 between integrity and insulation?

        8 A. So you typically don't have to provide insulation on

        9 a fire door because it can open and, ideally, there

        10 isn't storage of combustibles up against the door, and

        11 insulation is to do with preventing heat transfer onto

        12 the cold side, the unheated side. Integrity is about

        13 preventing flames through cracks.

        14 So I'd imagine that when there's a cotton pad, when

        15 they put that near the flame up on the top left-hand

        16 corner, that's why they recorded failure.

        17 Q. To be fair, you note that the testing standard that was

        18 applied by the BRE is a more recent -- you say it's

        19 a 1987 version of BS 476 --

        20 A. Yes.

        21 Q. -- than would've been applicable at the time of

        22 construction of Grenfell Tower?

        23 A. Yes.

        24 Q. So you say it's not directly comparable with the

        25 30-minute requirement at the time of construction.
        62

        1 A. At the time -- that's correct, yes.

        2 Q. Is that right?

        3 A. Yes. It's a more difficult test to pass, if you will,

        4 because they introduced a pressure differential. It was

        5 in the 1970s. Yes.

        6 Q. So a positive pressure --

        7 A. Yes.

        8 Q. -- against the door.

        9 A. Exactly, and it's more likely the products of combustion

        10 would pass through it.

        11 Q. So we need to bear that in mind when we're looking at

        12 that test report?

        13 A. Yes, we do.

        14 Q. Just to clarify, that was one of the stair doors from

        15 Grenfell Tower.

        16 Do you think that that is representative of the

        17 stair doors we're concerned with between levels 4 and

        18 23, as far as you're aware?

        19 A. So in the BRE test report, I couldn't find information

        20 on the seal to the door they tested, and that would be

        21 useful to know. And then, coupled with hopefully more

        22 information from relevant parties, we could close out

        23 the matter of what seal was there or not, and I could

        24 make a more final conclusion on the actual fire

        25 resistance of the stair door, noting that I haven't
        63

        1 observed a failure caused by the door in the staircase

        2 with respect to that damage I mentioned.

        3 So these are technical matters rather than something

        4 that might substantially change my opinion.

        5 Q. Again, is it potentially relevant that we see varying

        6 damage of the stair doors still in situ in

        7 Grenfell Tower, with some of them only marginally

        8 damaged and perhaps seem to have held up reasonably

        9 well?

        10 A. Yes.

        11 Q. Is that correct?

        12 A. That's correct, and we're back again to this situation

        13 of the hazard in a location, the conditions in that

        14 location, and so what was imposed upon that door over

        15 time.

        16 Q. Finally on this subtopic, you've highlighted in your

        17 report that if you compare these stair doors with the

        18 current guidance in ADB 2013, current standards require

        19 a stair door to achieve FD 60 minutes integrity; is that

        20 correct?

        21 A. That's correct, for firefighting stair protection.

        22 Q. So that's strictly the modern standard and doesn't take

        23 into account any non-worsening principle or

        24 non-worsening in relation to the stair doors?

        25 A. I'm not giving any view on non-worsening at the moment,
        64

        1 but the statutory guidance at this time is for

        2 a 60-minute door to a firefighting shaft.

        3 Q. Again, some similar questions about stair doors to flat

        4 doors.

        5 Would you agree that they're never going to provide

        6 indefinite protection against fire; they're only ever

        7 going to last for, if they were upgraded doors,

        8 30 minutes, and even if they're ADB doors, 60 minutes,

        9 and that they would generally be expected to fail at

        10 some point? Do you think that that's something we need

        11 to bear in mind and --

        12 A. I'm not sure, because I don't know what -- you know, I'd

        13 have to say: what is the definition of "indefinite

        14 protection"? There is a performance required for

        15 specific reasons.

        16 This issue of not replacing doors and simply

        17 upgrading them without having to contemplate anything

        18 else, I don't understand, so that guidance in the LGA.

        19 I typically don't recommend, myself, notional fire

        20 doors, for example, in my own work.

        21 So in my mind, I understand in a major flashover

        22 fire, at some point the door may fail, but it's actually

        23 of considerable importance for the time before that very

        24 severe heating occurs, hence the S rating, the

        25 door-closer and everything else about a fire door. It's
        65

        1 about its function in the early, middle and late stages

        2 of the fire.

        3 Q. Again, do you think it would be possible to estimate how

        4 much smoke might seep through a closed non-compliant

        5 door as compared with a door which was compliant by the

        6 original standards or modern standards, and would that

        7 exercise be relevant and helpful?

        8 A. Yes. So there are very clever smoke modelling people

        9 out there; I am not one of them. That is a numerical

        10 analysis that could be carried out if a person thought

        11 it would be relevant, yes.

        12 SIR MARTIN MOORE-BICK: You'd have to know the manner in

        13 which the door was not compliant, though, wouldn't you?

        14 A. You certainly would, and you'd have to understand the

        15 hazard posed to that door over time.

        16 SIR MARTIN MOORE-BICK: Mm.

        17 MS GRANGE: Is that something you consider would be useful

        18 for your work going forward?

        19 A. I don't feel the need to do that at this time.

        20 Q. Finally on this topic -- I think you, yourself,

        21 mentioned it -- there is some firefighter evidence from

        22 the night that some of the stair doors, when shut, were

        23 fairly effective at preventing smoke from entering the

        24 stairs.

        25 A. Yes.
        66

        1 Q. There's a number of examples of that that we had in some

        2 of the oral and written evidence?

        3 A. Yes.

        4 Q. Do you think that that evidence is potentially

        5 significant when we consider the importance of any

        6 performance non-compliances that you found in the doors?

        7 A. Yes, exactly.

        8 So there's non-compliance and then there is

        9 performance during a hazard. And, yes, that must be

        10 considered, and that's why I keep saying what happens in

        11 each location will become very important.

        12 Q. A slightly different topic now: the refuse chute doors.

        13 I just want to ask some very brief questions about the

        14 refuse chute doors.

        15 So on each of the lobbies, next to the stair door,

        16 along from the stair door to the other side of the

        17 service riser cupboard, is a door that goes onto

        18 a refuse chute that residents could use; is that

        19 correct?

        20 A. That's correct.

        21 Q. You note that CP3 1971 set no standard for any refuse

        22 chute doors. You note that in your report.

        23 A. For the door itself, just for its location and the

        24 location of the chute itself not being in an escape

        25 route, and the requirement for permanent ventilation.
        67

        1 But not for the door, yes.

        2 Q. Do you agree that, based on your inspections of the

        3 tower, those wooden refuse chute doors appear to have

        4 fared better than the stair doors?

        5 A. They do appear to, because in the tower, during my

        6 inspections, I observed the cleanliness and lack of fire

        7 and smoke damage in nearly every refuse chute area. It

        8 was very striking.

        9 Q. Do you think those refuse chute rooms could potentially

        10 have been used as safe places for residents waiting to

        11 be rescued?

        12 A. I understand -- you know, one has those thoughts, I did

        13 have such thoughts myself on site, but the reality is

        14 knowing where they are, making a decision about them

        15 being safe or not -- I just don't know how anyone

        16 could've made that decision during the fire.

        17 I understand that they appear to have been safe

        18 because of their post-fire condition, but I couldn't

        19 honestly say that it's something that would've been

        20 reasonable to consider.

        21 Also, one or two of them actually are -- well,

        22 particularly at level 7, there was one that was very

        23 severely damaged.

        24 The other important thing about that area is there

        25 is actually mechanical ventilation apparently provided
        68

        1 to that room. I don't have enough information on it

        2 yet, but I will be looking at the effect that had in

        3 terms of smoke in the lobby also.

        4 But I couldn't say that it should have been

        5 considered or that it should be considered, no.

        6 Q. A new topic now: gas.

        7 Your appendix K is serving as effectively a briefing

        8 document for the specialist gas expert that the inquiry

        9 has appointed, Mr Rodney Hancox; is that correct?

        10 A. That's correct.

        11 Q. On that basis, I have just a few questions for you on

        12 this topic because this is going to be addressed in much

        13 more detail by Mr Hancox when he opines in his written

        14 report.

        15 A. Yes.

        16 Q. But one of the topics I want to ask you about is about

        17 penetrations that may be relevant to the gasworks at the

        18 tower, in particular about the penetration between the

        19 stairs and the lobbies which you've identified as

        20 potential routes of smoke spread between levels during

        21 the fire.

        22 A. Yes.

        23 Q. Is it right that you've concluded that the wall of the

        24 stairwell -- which, as you've explained, is a protected

        25 shaft, the stairs --
        69

        1 A. Yes.

        2 Q. -- was breached on 13 floors between the 4th and the

        3 21st floor; is that correct?

        4 A. Yes. Are we able to show a photo?

        5 Q. Yes, that's my next -- exactly. If we can look at your

        6 figure K.23. That's BLAS0000032, page 24.

        7 If we zoom in on K.23, which is at the top of that

        8 page.

        9 A. Okay. So --

        10 Q. You explain what we're seeing in this photo.

        11 A. So this is on the lobby side. So you mentioned there on

        12 the stair side a protected shaft was built. There is no

        13 information on how it was built and its fire

        14 performance, and that would be useful to have.

        15 That appears, though, as I've said in my report, to

        16 have performed effectively, in the sense, again, there

        17 is no significant heat damage or, you know, damage to

        18 the concrete enclosure to the staircase in that area at

        19 the moment.

        20 Separately, on the lobby side, where this gas pipe

        21 leaves the staircase enclosure, it breaks through the

        22 concrete here (Indicates), and now we're out on a lobby

        23 near flat 1 and 2. Yes.

        24 What I don't know is -- Cadent have said they were

        25 going to box this in the same way they boxed in the
        70

        1 staircase. Those works hadn't taken place by the time

        2 the fire occurred; they were due around that time.

        3 What I don't know is if there's a fire-stopping

        4 material at the back of this hole in the wall or not,

        5 and I will need to work very closely with the gas expert

        6 and review his survey data to understand if that hole

        7 there was sealed.

        8 Now, that wouldn't impact the stair because the

        9 stair is boxed in. I don't know if we can --

        10 Q. I was about to take you to a photo of that.

        11 A. Maybe show that.

        12 What it does affect is that actually acts as a link

        13 from lobby to lobby, because at the next pipe run above

        14 on the next nearest floor, if the same hole is there,

        15 smoke from one lobby could travel up and out to the next

        16 lobby.

        17 But I don't know that and I need that information

        18 about the fire-stopping on the stair wall to lobby line.

        19 So the staircase seems clear. The lobby requires

        20 further attention.

        21 Q. Just before we leave this photo -- we will go to the one

        22 on the stair side in a moment.

        23 A. Yes.

        24 Q. So these were penetrations --

        25 A. Yes.
        71

        1 Q. -- through the wall to accommodate pipes referred to as

        2 laterals; is that correct?

        3 A. Laterals, yes. They're just running out, yes.

        4 Q. This was all part of the new gas riser installation for

        5 riser number 2.

        6 A. Yes.

        7 Q. So there were, I think, five risers coming up, and one

        8 of those risers was being replaced for the flat 2s.

        9 A. Yes, there were six coming up, and this was the

        10 replacement riser, and it was run through the staircase

        11 and brought out through the wall of the staircase, out

        12 onto the lobbies that required a gas supply. It looks

        13 like that (Indicates).

        14 Then you can see it entering the flat here at the

        15 wall there. Again, I don't know what that seal there is

        16 either.

        17 Q. So let's look at what it looks like from the other side.

        18 Figure K.22, I think, on page 23.

        19 A. Yes.

        20 Q. So you've highlighted these, I think. This is level 13

        21 and level 21.

        22 A. Yes.

        23 Q. Is it right what we can see is the boxing-in on the

        24 stair side.

        25 A. Yes.
        72

        1 Q. I think on the right-hand picture you can see the

        2 vertical boxing-in down the side and then the boxing in

        3 at the top of the wall; is that correct?

        4 A. Yes, that's correct. So here's the vertical gas run

        5 boxed in, and here, because this is a floor where it's

        6 going to come out onto the lobby, it comes across and

        7 then it goes out onto the lobby side.

        8 Q. So what we were seeing in the other photograph was

        9 what's going on on the other side, on the lobby side?

        10 A. Yes.

        11 Q. You've highlighted these two photographs in particular

        12 because what you say is there are missing panels at the

        13 end of these.

        14 A. Yes, that's correct.

        15 Q. But to be fair, what you say in your report is they

        16 could've been taken off by somebody after the fire.

        17 A. Yes.

        18 Q. You're not clear at the moment.

        19 A. Yes, it could be as part of some work by the police that

        20 samples of materials have been taken by the time I got

        21 to site.

        22 Q. Yes.

        23 A. It is a hole in the protection, but if you just look

        24 again, it's about looking at the damage around it. You

        25 can see here at level 13, yes, the light is damaged, but
        73

        1 I explain that later on with regards to the door. At

        2 21, you can see there's no severe damage, for example,

        3 to the concrete.

        4 So at the moment I've no reason to believe they were

        5 particularly relevant, but it will be very helpful to

        6 get a proper explanation of those works.

        7 Q. The significance, just to be absolutely clear, is that

        8 potentially, otherwise, there's a compromising of the

        9 stair compartment by virtue of these holes?

        10 A. Those holes.

        11 Q. Lobby to lobby, is what you're saying?

        12 A. But the ones I showed earlier, it's about smoke being

        13 able to flow from one lobby to the next through the

        14 breaches on the stair wall.

        15 SIR MARTIN MOORE-BICK: Through the trunking we see on the

        16 stairs? What's the route for the --

        17 A. It's a pity we don't have a sealed one, actually. If

        18 this was one of the sealed trunkings, if there is fire

        19 and smoke in the lobby, and that fire-stopping isn't

        20 there on the line, smoke can enter this space, and all

        21 of this is connected on every floor within the box.

        22 SIR MARTIN MOORE-BICK: When you say "this space", you mean

        23 the boxing?

        24 A. Within the box. It's connected then at every floor

        25 within the box. So it mightn't break out onto the
        74

        1 staircase, but it could flow through the box --

        2 SIR MARTIN MOORE-BICK: I understand that.

        3 A. -- back out to another floor.

        4 MS GRANGE: Yes.

        5 I know you have said you want to do further

        6 investigations; are you able to give any opinion at this

        7 stage about the significance of this breach of

        8 compartmentation in terms of smoke spread on the night?

        9 A. So with regards to the fire-stopping on the lobby line,

        10 if it was not there, I would be very concerned about it

        11 as a route for fire and smoke spread.

        12 But I very much want to get proper information about

        13 the fire-stopping at that line before I stray into that

        14 territory.

        15 Q. I understand.

        16 Just on another topic linked to this question of

        17 breaches of compartmentation, then we might have another

        18 break: ventilation ducts in the bathrooms.

        19 A. Oh, yes.

        20 Q. It's been suggested that there appear -- I'm afraid

        21 I don't have any photographs -- to have been ventilation

        22 ducts in each of the six bathrooms on each floor.

        23 A. That's correct.

        24 Q. Is that correct?

        25 A. That is correct.
        75

        1 Q. Is it right that they run in pairs vertically through

        2 the building?

        3 A. Yes, that is correct. Yes, I think in pairs. Yes.

        4 Q. It's been suggested that from level 9, the boxing-in of

        5 those vertical risers appears to have been destroyed by

        6 fire; is that correct?

        7 A. I observed significant damage during my time on site,

        8 yes.

        9 Q. Have you conducted any detailed inspection of those?

        10 A. Me and my team actually tracked those risers, and it's

        11 something that I will go to look at in the next stage of

        12 my work. Because like every other riser, they connect

        13 every floor, and my understanding, from the limited

        14 information made available to me, is there may have been

        15 some new ventilation provided through those risers also.

        16 Q. So do you think this is something that's important to

        17 investigate in terms of the spread of smoke throughout

        18 the building?

        19 A. Yes, I do.

        20 MS GRANGE: Great, thank you.

        21 Mr Chairman, that's probably a good point for

        22 another break.

        23 SIR MARTIN MOORE-BICK: Is that a good point?

        24 MS GRANGE: Yes. Thank you.

        25 SIR MARTIN MOORE-BICK: All right. Well, we'll have another
        76

        1 break now. Is that all right?

        2 THE WITNESS: Okay, thank you.

        3 SIR MARTIN MOORE-BICK: Same as before. Off with the usher,

        4 and we'll come back at 12.10.

        5 MS GRANGE: Yes, that's great.

        6 SIR MARTIN MOORE-BICK: Right, 12.10, please.

        7 (11.55 am)

        8 (A short break)

        9 (12.10 pm)

        10 SIR MARTIN MOORE-BICK: All right, Dr Lane, happy to go on?

        11 THE WITNESS: Yes.

        12 Actually, I thought I should probably clarify

        13 something. You asked me why the laterals and verticals,

        14 how they connect within the staircase --

        15 SIR MARTIN MOORE-BICK: What I wanted to make sure

        16 I understood was that the route of smoke transfer

        17 between lobbies on different floors was through the

        18 boxing and the trunking.

        19 THE WITNESS: Exactly.

        20 SIR MARTIN MOORE-BICK: I thought that was the route, but

        21 I wanted to clarify that. Thank you.

        22 THE WITNESS: And the reason why it could happen is there's

        23 a statutory duty to ventilate that boxing and to provide

        24 ventilation to it in the relevant gas legislation, and

        25 it's considered so important that the fire safety
        77

        1 legislation also makes that clear, and the only way the

        2 laterals and the verticals can be ventilated is if

        3 they're fully open to each other.

        4 So it would be useful to understand the detailing

        5 around that.

        6 SIR MARTIN MOORE-BICK: Thank you, that's helpful.

        7 Yes, Ms Grange.

        8 MS GRANGE: Thank you.

        9 Just a few questions about the hot zone or hot-spot

        10 that you identified in your report.

        11 So in your first report you found evidence that the

        12 plastic stair lights on levels 13, 14 and also the half

        13 levels on 13 and 14 had been fully destroyed --

        14 A. Yes.

        15 Q. -- whereas the plastic stair lights above that on levels

        16 15, the half level of level 15 and 16 you say were

        17 deformed or just partially melted; is that correct?

        18 A. Yes, that's correct.

        19 Q. You also found significant evidence of damage to the

        20 lobbies and the stair doors on those levels as well,

        21 where the lights were completely deformed?

        22 A. Yes, yes, I did.

        23 Q. You consider that this was potentially significant

        24 evidence in terms of a hot zone or hot-spot in the

        25 middle of the stairs at around levels 13 to 16; is that
        78

        1 correct?

        2 A. Yes.

        3 Q. Where you say you think temperatures may have got above

        4 150 degrees Celsius; is that correct?

        5 A. Yes, that's correct.

        6 Q. In your revised report, and having heard the factual

        7 evidence that you've heard, you've highlighted

        8 a particular rescue operation described by

        9 Firefighter Desforges around levels 10/11 with the stair

        10 door being held open after 2.00 am, 2.10 am, possibly.

        11 A. Yes.

        12 Q. You've also noted some resident witness statements which

        13 indicate a lot of firefighter activity around level 14

        14 at around the same time; is that correct?

        15 A. That's correct.

        16 Q. You've said at this stage in your report that the

        17 strongest evidence of the cause of the plastic light

        18 damage in this hot-spot is smoke and heat entering the

        19 stairs from open doors, possibly due to this firefighter

        20 activity; is that correct?

        21 A. Yes that's correct.

        22 Q. Does that remain your view, based on what you've heard

        23 so far?

        24 A. At this stage, yes, it is.

        25 Q. Is it also possible that the reason why there's
        79

        1 a hot-spot or hot zone might be explained, for example,

        2 by gas fires burning later in the piece? Do you think

        3 that's potentially another source of those hot zones or

        4 hot-spots?

        5 A. So I presume what that's meant to mean is causing

        6 a heating beside the stair door so extreme, it can

        7 radiate through the materials and melt the lights.

        8 I have no evidence available to me that that is possible

        9 as a function of how I understand the location of the

        10 gas risers in the flats.

        11 Q. So you think at the moment it's much more likely this is

        12 due to firefighter actions in that part of the building?

        13 A. Yes, and I think in my April report, I put the timing

        14 after the change in stay-put advice, but careful

        15 analysis of resident evacuations shows that there's

        16 a period of time between about 01.45 and 02.25 where no

        17 one exited the tower from above that zone.

        18 Q. Yes.

        19 A. But later on, then, evacuation from that zone and above

        20 occurs.

        21 Q. Yes.

        22 A. At the moment, that's how I've honed in on the time.

        23 Q. Yes. That's very helpful.

        24 I'm now going to turn to consider some of the active

        25 fire safety systems in the building.
        80

        1 In general, I think, is it right here we're looking

        2 at requirements B1 and B5, means of warning and escape,

        3 and facilities to assist the firefighters to save life

        4 and allow for fire engine access? Those are the key

        5 parts of the Building Regulations, the functional

        6 requirements?

        7 A. That's correct.

        8 Q. I want to start with some brief questions about the

        9 interface between fire detection and alarms.

        10 You have concluded in your report that there is no

        11 requirement to have a centralised alarm system, is that

        12 correct, in a building like Grenfell Tower?

        13 A. That's correct. There's no requirement to provide

        14 an alarm sound or voice message in one or all of the

        15 parts. That's correct.

        16 Q. What you've said in your report is that there's a useful

        17 explanation in BS 5588-1:1990 on the reason why there's

        18 no statutory requirement for a common alarm system. Can

        19 we just look at that.

        20 A. Yes.

        21 Q. So that's BLAS0000015 at page 15, at the top of the

        22 page.

        23 So here it says:

        24 "'There is no statutory requirement for a common

        25 fire alarm system to be provided in a building solely
        81

        1 containing flats and/or maisonettes and, in buildings

        2 designed and constructed in accordance with this code,

        3 it is generally unnecessary and undesirable for a fire

        4 alarm system to be provided. A common fire alarm system

        5 ought to be provided only in a building in which some

        6 control can be achieved over the occupants so that a

        7 pre-determined response leading to the evacuation of the

        8 building can be triggered.

        9 "'In flats and maisonettes in normal use this kind

        10 of response cannot be achieved, nor is it necessarily

        11 desirable that evacuation should take place from areas

        12 remote from the fire, unless these areas themselves

        13 become threatened by fire.'

        14 A. That's correct.

        15 Q. You've obviously thought it was important in your report

        16 to highlight these particular features of that British

        17 standard in terms of why an all-out alarm is not

        18 necessary; is that right?

        19 A. Yes.

        20 Q. Is there anything more you want to say on that?

        21 A. No, I think it's that concept about either accidental or

        22 malicious false alarms or, you know, people would have

        23 said before, if someone burns their toast in one flat,

        24 you don't want the whole building having to evacuate.

        25 That would've been the kind of general view and why that
        82

        1 kind of all-out function hasn't been provided to date in

        2 residential buildings.

        3 Q. You say in this context that it's important to

        4 understand what alternatives there are available for

        5 raising the alarm throughout the whole building, which

        6 brings us to chapter 18 of your report, which is about

        7 communication with residents; is that correct?

        8 A. Yes.

        9 Q. I'm going to ask you some questions about that chapter.

        10 Not very many, but just some questions.

        11 A. Yes.

        12 Q. So in that chapter of your report, you consider the

        13 possible means available to the London Fire Brigade of

        14 communicating with residents during the fire and once

        15 the stay-put strategy was formally changed; is that

        16 correct?

        17 A. Yes, that's correct.

        18 Q. First I want to ask you about loudhailers. You note

        19 that this is part of the LFB inventory equipment, but

        20 you consider it impractical due to other background

        21 noise at the fire ground and the height and proportions

        22 of Grenfell Tower; is that correct?

        23 A. Yes, that's correct.

        24 Q. I think you note that loudhailers were used, but for

        25 very specific reasons; for example, if there were
        83

        1 concerns about people --

        2 A. People's safety.

        3 Q. People's safety, jumping or --

        4 A. Yes. Sorry, I just would really like to say that I've

        5 looked into these features, because the building design,

        6 you know, the provisions with the building itself,

        7 provides nothing at all for communication, and so I was

        8 trying to find other methods instead. But I want to

        9 emphasise the absence of any form of communication

        10 device, not just a sounder, in the building itself.

        11 Yes.

        12 Q. Firefighters knocking on doors.

        13 A. Yes.

        14 Q. That's another thing that you've considered. You note

        15 the difficulty with doing this if done for the whole

        16 tower block, and I think you note that you would require

        17 significant resources and significant numbers of

        18 firefighters to be deployed to all floors.

        19 A. Yes, that's correct.

        20 Q. And also logistical issues: whether you break in if

        21 there's no answer -- there may be all sorts of

        22 logistical difficulties you sought to highlight; is that

        23 correct?

        24 A. Exactly, to do it methodically in such circumstances.

        25 Q. You've concluded that this issue of communication with
        84

        1 residents and available methods should be explored

        2 further given the number of other buildings with

        3 a stay-put policy; is that correct?

        4 A. Yes. So the number of other buildings with a stay-put

        5 policy, and an external wall that supports the spread of

        6 fire.

        7 Q. I want to ask you about the option on the night for the

        8 LFB to use the door intercom system, as Fatima Alves

        9 appears to have done, to communicate with other

        10 residents.

        11 I think it's right that you've now considered that

        12 question in detail at section 18.8 of your report,

        13 pages 21 to 24.

        14 A. Yes.

        15 Q. In particular, is it right you've sought to draw

        16 attention to the functionality of the intercom system,

        17 in terms of what it could and couldn't do?

        18 A. Yes.

        19 Q. Which you think is relevant to this; is that right?

        20 A. Yes, that's correct. So, I mean, my understanding, from

        21 the information I have about the intercom system, it

        22 wasn't installed as a life safety feature; a life safety

        23 feature requires backup power and other more resilient

        24 features to make sure it will work during a fire. But

        25 in terms of using it on an ad hoc basis, I've looked
        85

        1 into what the system could potentially do.

        2 I think the list on --

        3 Q. I was going to take you to paragraph 18.8.6.

        4 A. Yes.

        5 Q. That's BLAS0000018, page 23.

        6 A. Yes.

        7 Q. Yes, so I think that this is your summary here:

        8 "... the intercom was not installed with the

        9 necessary robustness to make it a formal life safety

        10 system, if firefighters wished to use the intercom as an

        11 ad-hoc means to communicate with residents, a flat

        12 number would need to be dialled and the firefighter

        13 would need to wait until a resident answered."

        14 A. That's correct.

        15 Q. "If a resident did not answer from a flat, the fire

        16 fighter would have no way of knowing if the flat was

        17 empty, if the resident was incapacitated or otherwise

        18 unable to come to the intercom, or if the system had

        19 been muted for the night."

        20 A. That's correct.

        21 Q. Again, have you noted that you can mute the system?

        22 A. Yes, exactly. There is a muting function that you can

        23 programme in and I have no information about how that

        24 operated at Grenfell Tower at this time.

        25 Q. The last point that you've made is:
        86

        1 "There are also other ways that use of such a system

        2 would not be effective, such as if the communications

        3 cable serving the intercoms was affected by the fire."

        4 A. Yes, that's correct. Also, there are other timings

        5 programmed into the system, in terms of how long it will

        6 ring the flat for, how long one is allowed to speak on

        7 the phone and all sorts of other functions.

        8 Again, we don't have that information at the moment,

        9 but all of that contributes to it not necessarily being

        10 a robust means of contacting every single flat

        11 methodically.

        12 Q. So based on what you know at the moment, do you think

        13 that was a practical option for use on the night?

        14 A. I understand that it's something that could be done. In

        15 the circumstances at Grenfell Tower, I don't know how

        16 one would go about using it effectively as was required

        17 that night with the number of people waiting for rescue.

        18 Q. You've also expressed concerns in that chapter as to how

        19 the limitations on communications would affect those who

        20 require assistance to escape in the event of fire; is

        21 that correct?

        22 A. That's correct. That's something I'm actually very

        23 concerned about.

        24 Q. Can you just briefly explain your concerns?

        25 A. Well, the issue for any person who isn't fully mobile
        87

        1 for whatever reason, there will be a category of person

        2 who lived at Grenfell Tower who could never use the

        3 staircase or could only use the staircase with

        4 difficulty. I think we might talk about lifts later.

        5 There was no proper firefighting lift for evacuation.

        6 So when it came to rescue not being possible, and

        7 self-evacuation was the only means to leave the tower,

        8 that left that category of person in a very hazardous

        9 condition, as I've been mentioning earlier.

        10 There is no statutory duty at this time to provide

        11 such means explicitly set out in the design guidance,

        12 and I find that very concerning to say the least.

        13 Q. Emergency lighting and signage. You dealt with that in

        14 chapter 15 of your report. Just a few questions on

        15 this.

        16 A. Yes.

        17 Q. You say on lighting that you're not able to tell whether

        18 the system complied with Approved Document B 2010

        19 because the lighting is now damaged and you can't

        20 determine if it complied with the relevant three-hour

        21 requirement for emergency lighting in sleeping

        22 accommodation that would be required in that guidance;

        23 is that correct?

        24 A. Yes, I don't have any drawings, actually, or

        25 specification.
        88

        1 I think it's probably worth explaining, emergency

        2 lighting only switches on if there is a power failure.

        3 Artificial lighting is required at all times on the

        4 escape route. So there's adequate lighting on the

        5 escape route, and then, in the event of a power failure,

        6 that a certain number of lights can switch on and

        7 maintain adequate lighting to the escape route.

        8 I'm not aware at the moment that there was

        9 necessarily a power failure, and I need more information

        10 to be able to explain if an adequate quantity of

        11 lighting was provided on the escape route to give a view

        12 on its compliance.

        13 So it's two things: power failure, but without power

        14 failure, an adequate quantity of lights or luminaires.

        15 Q. There is some evidence of failure of lobby emergency

        16 lighting.

        17 A. Yes.

        18 Q. You note that once the lobbies filled with black smoke,

        19 the lighting would've been of little use, but would it

        20 potentially have been significant if the lights had

        21 failed earlier than they should have?

        22 A. Yes. So if the lobby was filled with black smoke, it

        23 might be that the light was on but, because of its

        24 relative illuminance with the smoke particles, quite

        25 simply one can't see it, rather than it had failed off,
        89

        1 or the lighting in that lobby in themselves may have

        2 failed during the fire.

        3 Q. Given the difficulties that were experienced by the

        4 firefighters in reading the floor numbers --

        5 A. Oh, yes.

        6 Q. -- which were placed directly beneath the lighting on

        7 the stairs, are you able to comment on the lighting and

        8 the floor numbering? In particular do you think the

        9 floor numbers should've been more clearly marked than

        10 they were?

        11 A. Yes. So, actually, I've observed that on some parts of

        12 the stair, the emergency lighting actually covers over

        13 the number, and in other parts of the stair, the number

        14 is present. I didn't actually check if the number was

        15 correct when I was at the tower.

        16 Q. Is there anything in any of the statutory guidance or

        17 other relevant guidance --

        18 A. No, that's what I was going to say. So it's interesting

        19 that if you think about this adequate lighting on

        20 an escape route, the absence of guidance on adequate

        21 lighting on, say, a floor number sign for orientating

        22 oneself as a firefighter, that's not something that's

        23 a duty at this time. But there is evidence from other

        24 fires too that that orientation of the firefighters can

        25 be very difficult.
        90

        1 So I think that is something that should be

        2 considered: adequate lighting, with proper orientation

        3 information, so firefighters can be clear about where

        4 they are.

        5 Q. I want to turn now to some questions about the fire main

        6 at Grenfell Tower.

        7 You've dealt with this in chapter 2 and then 14 and

        8 15 of your report, if you want to make sure you have

        9 those to hand.

        10 A. Yes. It's okay, keep going, I'll be fine. Yes. I just

        11 have too many papers on my desk.

        12 SIR MARTIN MOORE-BICK: Do you want a moment to sort them

        13 out?

        14 A. No, no, I'll be okay. I'll tell you if I get stuck.

        15 MS GRANGE: You explain in your report that in modern design

        16 codes, the regulations require provisions only for

        17 internal firefighting in high-rise buildings?

        18 A. That's correct.

        19 Q. You've looked first at CP3 1971, the design guidance you

        20 think applied when Grenfell was constructed, and you've

        21 concluded that the risers were non-compliant because

        22 there should've been provision for a wet riser, given

        23 the height of the building; is that correct?

        24 A. That's correct.

        25 Q. So Grenfell Tower is more than 60 metres; it was
        91

        1 measured at 65.49, using the relevant height criteria

        2 under CP 371; is that correct?

        3 A. That's correct.

        4 Q. What we have at Grenfell Tower is dry risers.

        5 A. Yes.

        6 Q. Can we just look -- again, just to orientate ourselves

        7 as to what we're talking about here -- at some of the

        8 pictures of those dry risers that you have at

        9 Grenfell Tower in your report.

        10 If you go to BLAS0000014, page 117, figure 14.56.

        11 So there we have examples of the dry risers, and

        12 we're going to come to this in a minute, but these are

        13 in the lobbies, aren't they?

        14 A. Yes.

        15 Q. Basically, these are places where the firefighters plug

        16 in their hoses to conduct the firefighting.

        17 A. That's correct.

        18 Q. So it looks like the particular type may have slightly

        19 kind of -- the particular details in different bits of

        20 the tower; is that correct?

        21 A. Well, I think this picture is a little bit confusing

        22 because it shows the newer inlet provided --

        23 Q. Ah, I see --

        24 A. -- for the new works --

        25 Q. So we see -- yes -- the level 2 outlets, level 3 --
        92

        1 A. -- rather consistently at level 4 to level 23. So maybe

        2 just look at --

        3 Q. So the ones at the bottom, level 4 looks like that.

        4 A. Yes.

        5 Q. Level 9 looks like that.

        6 A. Yes.

        7 Q. You have said that under modern design guidance --

        8 that's Approved Document B 2013 -- a wet riser was also

        9 required.

        10 Can you just briefly explain for us the difference

        11 between a wet riser and a dry riser?

        12 A. Yes, so a dry riser is empty in normal use. The Fire

        13 Brigade arrive and pump the water from -- I call it the

        14 town mains or the area water supply, through pumping

        15 equipment, into the riser. It pumps the water up

        16 through the riser and makes it then available for use on

        17 any floor.

        18 A wet rising main is what's called permanently

        19 charged by means of tanks and pumps in the building, and

        20 so the only action for the Fire Brigade is to go to the

        21 floor and operate the system on the floor that it's

        22 needed.

        23 SIR MARTIN MOORE-BICK: And presumably top up the tanks from

        24 time to time, if necessary?

        25 A. The tanks are connected to the town main.
        93

        1 SIR MARTIN MOORE-BICK: Oh, are they?

        2 A. That's the idea. That's the idea. And so they should

        3 be replenished if they're emptied or being used. That's

        4 the idea.

        5 SIR MARTIN MOORE-BICK: Right.

        6 MS GRANGE: I just want to look at what you've said in your

        7 report at paragraph 15.8.17. That's BLAS0000015,

        8 page 37 of chapter 15.

        9 If we could zoom in on 15.8.17, you say that this

        10 relevant design standard, BS 9990:2006 gives us some

        11 reasons why you have taller buildings requiring wet fire

        12 mains.

        13 A. Yes.

        14 Q. So what it says there:

        15 "'wet fire mains should be installed owing to the

        16 pressures required to provide adequate fire-fighting

        17 water supplies at the landing valves at upper floors and

        18 also to ensure that water is immediately available at

        19 all floor levels.'"

        20 A. Yes, that's correct. Because in a dry rising main, the

        21 taller the floor, the more difficult, if you will, it is

        22 to pump the water there. It's entirely possible, but it

        23 becomes more difficult with height.

        24 Q. I now want to go to what you say -- and this is

        25 crystallised in your summary and conclusions chapter,
        94

        1 this is chapter 2.

        2 A. Yes.

        3 Q. If we look at BLAS0000002 at page 66.

        4 It's paragraphs 2.23.24, and 2.23.25, those two.

        5 Yes, if we can make those big.

        6 So you say there:

        7 "2.23.24. In a wet riser, the system would already

        8 have been charged with a pump connected when LFB

        9 arrived. There would have been no operations required

        10 by LFB to find external hydrants, connect to their

        11 pumping appliance and connect to the riser inlet.

        12 Therefore, the provision of a dry main would have

        13 contributed to increasing the time required by the LFB

        14 to get water to the initial fire event in Flat 16.

        15 "2.23.25. Therefore, a wet fire main could have

        16 enabled a faster initial response time to the fire in

        17 Flat 16 which might have increased the chances of

        18 extinguishing the fire before it spread externally.

        19 However, it cannot be asserted it would have absolutely

        20 achieved this."

        21 A. That's correct.

        22 Q. I want to ask you some questions about this speed of

        23 set-up topic.

        24 A. Okay, yes.

        25 Q. That is potentially consistent with what Watch Manager
        95

        1 Dowden said in his evidence. On Day 3, on 27 June, he

        2 said [page 3, lines 18 to 20]:

        3 "But generally, as a rule of thumb, it will increase

        4 our timing -- decrease the time to make a compartment

        5 entry, yes."

        6 A. Yes.

        7 Q. However, do you agree that the chairman will also need

        8 to consider the factual evidence more broadly about

        9 whether firefighters in fact had to wait to use the dry

        10 riser?

        11 A. Yes, I do agree, yes.

        12 Q. And that he will have to look at whether there's

        13 evidence as to whether they actually had to wait for the

        14 water and whether they were ready to go in any event?

        15 A. Yes, that's not something I've analysed at all. Yes.

        16 Q. Just on this, do you accept that the activity of

        17 connecting a supply to the dry riser, and also the fire

        18 crews setting up at the bridgehead, are likely to be

        19 simultaneous activities?

        20 A. That's a matter for a firefighting expert to give a view

        21 on.

        22 Q. Another topic on this is about the use of a wet main to

        23 cool the lobbies.

        24 A. Yes.

        25 Q. If we go back again within chapter 2 of your report to
        96

        1 2.23.26 -- that's chapter 2, BLAS0000002, page 66, the

        2 same page we were just on.

        3 If we can zoom in on that paragraph, 2.23.26.

        4 A. Yes.

        5 Q. So you've said this there:

        6 "2.23.26. A wet fire main, could have enabled

        7 greater water pressure for fire-fighting on the upper

        8 floors of Grenfell Tower, which may have allowed LFB to

        9 use water to cool lobbies and stair and therefore

        10 provide more assistance to people trying to escape."

        11 A. Yes. So this is something I'm very interested in in

        12 terms of understanding hazards to people in specific

        13 locations, because the design condition is to have a wet

        14 rising main which can cope with two hoses operating at

        15 the same time.

        16 I just would like to hear some more about, if that

        17 condition was present at Grenfell Tower, how it could

        18 have been used in the context of rescue. The two hoses

        19 are very important, because that's about protecting

        20 crews. And in the beginning it should be about

        21 extinguishing the fire and protecting the crew, but

        22 I would like to understand later on, if that provision

        23 had been available, a wet rising main with two

        24 functioning hoses, and it could've been applied that

        25 way, with two functioning hoses, how that might have
        97

        1 assisted protecting crews and dealing with localised

        2 conditions in the lobby.

        3 I would like to hear about that from a firefighting

        4 expert or a firefighter.

        5 SIR MARTIN MOORE-BICK: When you talk about two functioning

        6 hoses, what exactly do you have in mind?

        7 A. So the water supply is meant to be sufficient through

        8 the wet rising main to allow the full operation of two

        9 hoses simultaneously.

        10 SIR MARTIN MOORE-BICK: Right.

        11 A. So I accept entirely that if you've multiple hoses at

        12 the same time, even with the wet riser, the situation

        13 changes. But if one used it as it was designed, if it

        14 had been provided, how can that assist protecting crews

        15 and dealing with localised firefighting to aid rescue

        16 only? I can't take that off the table as such.

        17 MS GRANGE: Okay.

        18 Can we just look at paragraphs 15.8.22 and 15.8.23

        19 within the body of your report. That's BLAS0000015 at

        20 38.

        21 A. Yes.

        22 Q. And here you give some comparison calculations you say:

        23 "15.8.22. To compare the performance of wet and dry

        24 fire main systems, I have calculated ... whether the dry

        25 fire main in Grenfell Tower could provide an equivalent
        98

        1 flow rate (l/s) and pressure of water (bar) to the

        2 design requirements for a wet fire main system. In

        3 summary, I have found that assuming two hoses operating

        4 in the building, one each at Levels 22 & 23, the

        5 pressure at the outlet would be 2.57bar. This is 32% of

        6 the pressure required by ADB 2013 for a wet rising main

        7 (8 bar)."

        8 Is that correct?

        9 A. Yes, it's a simple theoretical analysis where all the

        10 water conditions are the same outside the tower, and it

        11 was just for the purposes of comparing a dry and wet

        12 riser in that context, to try and illustrate how it's

        13 different and how it would be potentially different in

        14 a building the height of Grenfell Tower.

        15 Q. You go on to say:

        16 "15.8.23. Similarly, to deliver the equivalent

        17 pressure to a wet fire main on the highest floors, the

        18 pressure required at Ground Level would be 15.5bar.

        19 This is over 50% more than the maximum operating

        20 pressure that dry fire mains are designed for (10 bar)."

        21 Is that correct?

        22 A. Yes, that's correct.

        23 Q. So I think you've accepted -- and you did, I think, make

        24 this point in your original report -- that even with

        25 a wet main, pumps and water supplies are not designed
        99

        1 for multiple fire streams; is that correct?

        2 A. Beyond two.

        3 Q. Yes.

        4 A. But I think understanding how two could have been used

        5 is important.

        6 Q. So at Grenfell Tower, would any shortcomings which are

        7 encountered in respect of the water pressure for the dry

        8 riser potentially also have been encountered for the wet

        9 riser due to the number of hydrants which were in use?

        10 A. Eventually, but there's proper expert detail required to

        11 understand the impact of the firefighting on the town

        12 main and I wouldn't like to stray there.

        13 But, yes, the more water that was used externally,

        14 in just very simple terms, I presume it impacted the

        15 water available for internal firefighting, and that

        16 proper analysis of network flows needs to be done.

        17 Q. And that's going to be done by probably Ivan Stoianov,

        18 who has been appointed as the water expert --

        19 A. Yes.

        20 Q. -- and potentially, presumably, Steve McGuirk, the

        21 firefighting expert may need to look at that as well.

        22 A. Yes. So I accept, because of all the ad hoc

        23 firefighting that became required outside the building,

        24 even though that's not what's meant to be required, will

        25 now have to be reviewed in the context of the remaining
        100

        1 water internally. But the evidence shows the

        2 effectiveness of the external firefighting at the levels

        3 it was possible, as I've explained in my report.

        4 Q. So on this basis, once the fire has spread to multiple

        5 floors, and they're doing firefighting in a large number

        6 of locations, would you accept that the wet riser may

        7 not have made a material difference?

        8 A. Once it went beyond two hoses, as I said.

        9 Q. Just moving to a slightly different point, you've said

        10 that under Approved Document B 2013, the risers,

        11 according to those current standards, have to be located

        12 within the stair enclosure --

        13 A. Yes.

        14 Q. -- and not within the lobbies.

        15 A. That's the recommendation yes.

        16 Q. That's if the current standards apply.

        17 A. Yes, it is, yes.

        18 Q. Do you consider that the siting of the outlets in the

        19 lobbies rather than the protected stairwell may have

        20 affected the firefighting effort within Grenfell Tower?

        21 A. Well, I observe in the evidence available to us that

        22 trying to get that distance to the dry riser, and in the

        23 shape of the lobby as it was, it did pose difficulties

        24 to London Fire Brigade as they have said themselves.

        25 Q. Yes.
        101

        1 A. And because of the conditions in the Grenfell Tower

        2 fire, the lobbies became a hazardous area, whereas if

        3 the dry riser was in the staircase in those extreme

        4 circumstances, that's something to contemplate.

        5 Q. Do you think that using a wet riser reduces the risk of

        6 compromise of the water supply caused by falling debris?

        7 A. I couldn't answer that question, sorry. Yes.

        8 Q. In terms of fire spread on the external wall --

        9 A. Yes.

        10 Q. -- do you think that the presence of a dry riser rather

        11 than a wet riser made any difference in terms of the

        12 firefighters' abilities to fight that external wall

        13 fire?

        14 A. Again, I actually don't understand that question,

        15 because the cladding fire was dealt with from outside

        16 the building for several hours, yes. Not with the dry

        17 riser. So I don't understand the question.

        18 Q. Would you accept that in an extended incident, such as

        19 that which was encountered at Grenfell Tower, had wet

        20 risers been used, the capacity of the tanks may have

        21 been exceeded early on in the fire?

        22 A. Indeed, and I think the analysis of the network supply

        23 in the area and around the building, therefore, is

        24 a useful exercise to understand what impact that might

        25 have had to replenishing those tanks.
        102

        1 Q. Just looking --

        2 SIR MARTIN MOORE-BICK: At that point, if you have a wet

        3 riser, you've got to draw water from the local mains.

        4 A. Yes.

        5 SIR MARTIN MOORE-BICK: And if you have a dry riser, you're

        6 drawing water from the local mains.

        7 A. Eventually, exactly.

        8 SIR MARTIN MOORE-BICK: So the difference is going to lie in

        9 the pumping capacity of the fixed pumps for the wet

        10 riser and the Fire Brigade's engines for the other?

        11 A. Absolutely, and not exceeding -- I keep saying two

        12 hoses -- the design basis of the wet rising system,

        13 which isn't 10 hoses, 20 hoses; it's two hoses.

        14 That's -- exactly, the pumping equipment and staying

        15 within the design limits of the system.

        16 SIR MARTIN MOORE-BICK: Yes.

        17 A. How one would do that systematically in an extreme

        18 event, that's the kind of information an expert in

        19 firefighting would need to bring.

        20 SIR MARTIN MOORE-BICK: Thank you.

        21 MS GRANGE: Just one set of questions on this topic now.

        22 Take the dry riser as a dry riser. Have you seen

        23 any evidence that suggests it didn't perform adequately

        24 as a dry riser, as in do you have any evidence that it

        25 didn't achieve the pressure that you would expect a dry
        103

        1 riser to achieve?

        2 A. Oh, I'm sorry. I was about to say, well, a dry riser is

        3 a dry riser.

        4 No, the evidence from early firefighting is that it

        5 performed effectively in their opinion.

        6 There is evidence of an incident at level 20 -- very

        7 unfortunately, I just can't bring the time to my mind

        8 right now, it wasn't late in the fire -- where the water

        9 pressure and flow rate at level 20 was less, if that's

        10 what you mean.

        11 SIR MARTIN MOORE-BICK: But the functioning of the dry riser

        12 is going to be related to the functioning of the Fire

        13 Brigade's pumping equipment --

        14 A. Correct.

        15 SIR MARTIN MOORE-BICK: -- and the supply of water to that

        16 equipment.

        17 A. Correct.

        18 SIR MARTIN MOORE-BICK: There's nothing intrinsic to the dry

        19 riser that you're aware of that compromised its --

        20 A. That's why I don't quite understand the question,

        21 because the dry riser is an empty pipe and it exists as

        22 an empty pipe in itself.

        23 SIR MARTIN MOORE-BICK: Well, you could've had a problem,

        24 for example, where you couldn't get the cap off or the

        25 valve didn't work or something like that.
        104

        1 A. Oh, I see, yes. I'm not aware that detailing of the

        2 physical infrastructure was a problem.

        3 SIR MARTIN MOORE-BICK: Right.

        4 MS GRANGE: This might help a little bit, but it's said that

        5 the dry riser did achieve the 10-bar pressure that you

        6 were referring to earlier, do you remember, a comparison

        7 between the pressure of a wet riser, 15.5, and the dry

        8 riser, 10-bar was the requirement.

        9 A. Yes.

        10 Q. It's suggested that it did, when tested, achieve that

        11 10-bar requirement. Have you considered that test

        12 evidence?

        13 A. No, I have not.

        14 Q. No.

        15 A. I'm not aware that it did.

        16 Q. But it would be appropriate for probably another inquiry

        17 expert to consider --

        18 A. Absolutely.

        19 Q. -- any testing of the dry riser that was done?

        20 A. Yes, and how it's done, replicating the exact

        21 circumstances of the external firefighting, and

        22 condition of the water network, around the tower on that

        23 night, particularly.

        24 MS GRANGE: Yes.

        25 Mr Chairman, I have no more questions on that topic,
        105

        1 and I'm about to move to a bigger topic, which is about

        2 the lift.

        3 SIR MARTIN MOORE-BICK: Would you like to break at that

        4 point?

        5 MS GRANGE: I think that would be an appropriate moment for

        6 a break, and I would be happy to come back at 2.00.

        7 SIR MARTIN MOORE-BICK: Are you sure?

        8 MS GRANGE: I'm sure.

        9 SIR MARTIN MOORE-BICK: There you are. Ms Grange thinks

        10 it's safe to have an extra 10 minutes for lunch.

        11 We're going to break at that point, then, and we

        12 will resume at 2 o'clock.

        13 THE WITNESS: Okay.

        14 SIR MARTIN MOORE-BICK: If you would like to go with the

        15 usher, and I have to remind you not to talk about your

        16 evidence.

        17 Good, thank you.

        18 Right, 2 o'clock, then, please. Thank you.

        19 (12.50 pm)

        20 (The short adjournment)

        21 (2.00 pm)

        22 SIR MARTIN MOORE-BICK: All right? Ready to go on?

        23 THE WITNESS: Yes.

        24 SIR MARTIN MOORE-BICK: Thank you very much.

        25 Yes, Ms Grange.
        106

        1 MS GRANGE: Thank you.

        2 I now want to ask you some questions about the fire

        3 lift at Grenfell Tower, for which purpose we will mainly

        4 be in appendix L of your report.

        5 As you explained in your presentation in June of

        6 this year, the lifts at Grenfell Tower were renovated in

        7 2005.

        8 A. That's correct.

        9 Q. That work was carried out by Apex as contractor against

        10 a Butler & Young specification.

        11 A. Correct.

        12 Q. You say in your report that at that time, it was

        13 Approved Document B 2000 that was the relevant statutory

        14 guidance under the Building Regulations.

        15 A. That's correct.

        16 Q. You say that Approved Document B 2000 required

        17 conformity to a particular British Standard, that's

        18 BS 55885:1991, which was the relevant standard at the

        19 time of those lift replacement works.

        20 A. Yes.

        21 Q. You say in your report that the Butler & Young

        22 specification did not provide for a full firefighting

        23 lift. We're going to look at the difference between

        24 that and a fire lift in a moment, but I just want to be

        25 clear. So it was not specified to be a full
        107

        1 firefighting lift; is that right?

        2 A. That's correct, based on the evidence provided to me.

        3 Q. Nor did it specify compliance with that British Standard

        4 I just referred to. You make that point in your report

        5 as well.

        6 A. Yes, I make that point.

        7 Q. You note that despite the TMO's policy that, when the

        8 lift are being refurbished, the reinstalled lift should

        9 be upgraded to a firefighter lift, the lift was not

        10 upgraded to that standard, but was replaced with another

        11 fire lift; is that correct?

        12 A. That's correct.

        13 Q. Can we just go back to CP3 1971 and just look at what

        14 a fire lift was required to have under that standard.

        15 A. Yes.

        16 Q. So if we go to figure L.2 in your report, BLAS0000033,

        17 at page 10.

        18 So here you've given the basic fire lift

        19 requirements as per that standard in 1971.

        20 A. Yes.

        21 Q. And you've got them in labels here.

        22 A. Yes, that's correct.

        23 Q. So we've got an independent power supply, various things

        24 about cabling, serving every residential level.

        25 A. Yes.
        108

        1 Q. Then a fire switch at access level; is that right?

        2 A. That's correct, yes.

        3 Q. That was a fire switch to enable it to be taken into

        4 firefighter control; is that correct?

        5 A. That's correct.

        6 Q. And we have a minimum lift car area. That's a basic

        7 fire life; is that correct?

        8 A. Basic fire -- well --

        9 Q. What we see there --

        10 A. Their dimensions are made clear, yes. And also it

        11 should serve every residential level, and then there's

        12 a walking distance to the door of the lift.

        13 Q. You've put the features of a full firefighting lift in

        14 a figure L.1 of your report, where we see those in

        15 diagram form. That's on page 7 within chapter 33.

        16 A. Yes.

        17 Q. Perhaps if we can pull that up.

        18 Again, you went through a number of these features

        19 in your presentation in June.

        20 A. Yes, I did.

        21 Q. This is just to remind ourselves of what a full

        22 firefighting lift requires.

        23 A. Yes, so it --

        24 Q. So --

        25 A. Oh, sorry.
        109

        1 Q. Yes, I mean, take it from the top: an independent

        2 primary and secondary power supply, that is a key

        3 feature.

        4 A. Yes, it's a key feature to ensure operation in

        5 an emergency.

        6 Q. Water ingress protection, the fourth label down.

        7 A. Yes, on the left.

        8 Q. I'm just highlighting some of the key features. We have

        9 them all in labels here.

        10 The provision of an escape hatch within the lift

        11 car.

        12 A. Yes, for the Fire Brigade and others, yes.

        13 Q. A compliant intercom system. So you talk about

        14 a two-way intercom from the lift car to the machine room

        15 and access level?

        16 A. Exactly, so you can communicate with someone outside the

        17 lift or for other reasons up at the machine room.

        18 Q. Again, we see the fire switch at access level.

        19 A. Yes, and fire-resisting landing doors, yes.

        20 Q. So those are all the features if you were to do

        21 a firefighting lift.

        22 A. Yes. I mean, that's a summary of, you know, a longer

        23 British Standard, so yes.

        24 Q. You've also noted in your report that the TMO has its

        25 own definition of a firefighting lift. What you say is
        110

        1 that that doesn't replicate the provisions of any design

        2 standard that you're aware of.

        3 A. As I read it. I don't know the basis for their

        4 definition.

        5 Q. What you said is, even looking at the lower fire lift

        6 standards, you've seen no evidence that in 2005 both

        7 lifts were connected to fire control switches; is that

        8 correct?

        9 A. In 2005?

        10 Q. Yes.

        11 A. Or to the 2005 standard?

        12 Q. Yes. In 2005, you say you found no evidence that the

        13 lifts were connected to fire control switches. You say

        14 the Butler & Young specification did not specify the

        15 provision of a fireman's control to any specific code or

        16 guidance; is that correct?

        17 A. Yes, that's correct. Not that I didn't find physical

        18 evidence of --

        19 Q. Sorry.

        20 A. Sorry, I misunderstood.

        21 Q. Yes, I think it's my question.

        22 A. Yes.

        23 Q. You've also noted that the relevant British Standard,

        24 the one we referred to earlier BS 55885:1991, required

        25 some very particular features for the firefighting
        111

        1 switch operation; is that correct?

        2 A. Yes, it did.

        3 Q. You've set these out at paragraph L3.3.6 and following

        4 of your report.

        5 A. Yes.

        6 Q. Perhaps we can bring that up on screen. We don't need

        7 to go through all the details of it, but it's at

        8 BLAS0000033, pages 12 and then on to 13. If we do

        9 page 12 first.

        10 So I think at the bottom of that page, you've

        11 included all the different --

        12 A. Yes, it's the next page.

        13 Q. -- requirements for a firefighting lift switch -- yes,

        14 it goes on to the next page.

        15 A. Yes, this list here.

        16 Q. So there's a long list here, but if I can just try and

        17 understand in summary what you're saying this shows.

        18 In essence, is it right that such a switch should

        19 enable the firefighters to bring the lift back to their

        20 access level, and then take control of the lifts?

        21 A. Yes, and prevent its use by any other person from

        22 a lobby.

        23 Q. Exactly. So it's taken out of all normal operation.

        24 A. Exactly.

        25 Q. So if you're a resident on floor 10 and you press the
        112

        1 switch, it shouldn't respond to that.

        2 A. Exactly, and if you happened to have pressed the switch

        3 and you're waiting, and the lift was taken under control

        4 whilst you were waiting, again, it wouldn't respond to

        5 your earlier call.

        6 Q. The way in which the firefighters control the lift, is

        7 it by putting pressure on certain switches within the

        8 lift car itself?

        9 A. Yes. So in that standard, it comes to where the fire

        10 control point is, and then the Fire Brigade can enter

        11 that lift and use the buttons inside the lift car to go

        12 to a floor and open the door slowly on that floor.

        13 Q. So it's basically under complete, sole firefighter

        14 control --

        15 A. Yes.

        16 Q. -- if that lift switch works?

        17 A. Yes, that's correct.

        18 Q. You've noted in your inspections at Grenfell Tower, as

        19 it existed at the time of the fire, that there are two

        20 firemen's control switches.

        21 A. Yes, I did.

        22 Q. There's one at ground floor.

        23 A. Yes, and one at level 2.

        24 Q. Yes. Let's just go to photographs of those. This is

        25 figure L.11, BLAS0000033, page 25.
        113

        1 So there we can see the switch that was present on

        2 ground level; yes?

        3 A. Yes.

        4 Q. And the switch at level 2.

        5 A. That's correct.

        6 Q. They've both cot "Fire control" written on them,

        7 although slightly --

        8 A. They're different shapes.

        9 Q. -- different shapes.

        10 A. Yes.

        11 Q. What you've said in your report -- is this right? -- is

        12 that you don't know if one or both of the switches at

        13 ground and level 2 were kept in 2005 or if they were

        14 new --

        15 A. Exactly.

        16 Q. -- or if there was a change during the refurbishment.

        17 You're a little bit unclear about the history of these

        18 switches?

        19 A. Exactly. So there should only be one because there's no

        20 way of understanding which -- there's not meant to be

        21 two, and if there is two, which one takes priority,

        22 okay? I've reviewed all sorts of documentation, so when

        23 I say I don't know, it's not for want of trying to find

        24 the information, as such.

        25 I don't know which switch was installed in 2005, or
        114

        1 if one was added during the primary refurbishment, or if

        2 they both existed before 2005, or they were both new or

        3 both old -- apologies for rambling, but it's a rambly

        4 subject.

        5 So, in short, I have no idea when each switch was

        6 installed at any stage.

        7 Q. We're going to come back to these switches in a moment,

        8 but in the principal refurbishment, you've ascertained

        9 that the extent of the work that was carried out to the

        10 lifts was basically two new landing doors to the lift

        11 shafts on levels 1 and 2 --

        12 A. Yes.

        13 Q. -- because of the new flats that were being converted in

        14 terms of change of use at that time.

        15 A. Exactly, works to allow the lifts to stop at every

        16 floor.

        17 Q. You've mentioned, L4.3.8 of your report, what the extent

        18 of that work was, and you say that the scope of work did

        19 not include fire control switches at this time in terms

        20 of what you can ascertain; is that correct?

        21 A. Based on the evidence provided to me, yes.

        22 Q. In terms of the lifts' performance on the night, what

        23 you've concluded is that the basic fire lift function,

        24 the override switch we were just looking at, did not

        25 work on the night; is that correct?
        115

        1 A. Yes. So when I wrote my first draft of this report, the

        2 evidence from the firefighters was a key was placed at

        3 the ground floor fire control key point, and they

        4 considered that nothing happened.

        5 Q. Yes. Again, we're going to come to this.

        6 Just in terms of the switch on the ground floor, as

        7 you've just said, we know that Firefighter Secrett tried

        8 to use a drop key to activate it --

        9 A. Yes.

        10 Q. -- but couldn't get the lift to return to ground when he

        11 attempted to operate the override switch.

        12 We can see an image of that if we go in your report,

        13 BLAS000033, page 39, figure L.20.

        14 A. Yes.

        15 Q. If we blow that figure up, there we see Firefighter

        16 Secrett, and he has put a key into the switch.

        17 A. Yes.

        18 Q. Is that what we can see? That's what you're referring

        19 to in your report?

        20 A. Yes, I am. Then his evidence that nothing happened.

        21 Q. You also note that the lift remained in general

        22 operation and was used by residents during the fire.

        23 A. Yes, based on the evidence from the night.

        24 Q. Again, we'll come back to that.

        25 You now have, and you had at the time of writing
        116

        1 your revised report, the benefit of a report from WSP --

        2 A. Yes.

        3 Q. -- which was prepared for the Metropolitan Police

        4 Service.

        5 A. That's correct.

        6 Q. We'll look at some aspects of that report in a moment,

        7 but just to summarise, that report first of all shows

        8 that the level 2 override switch had no wires connected

        9 to the firemen's switch.

        10 A. That's correct.

        11 Q. So that level 2 switch, which is still there, doesn't

        12 look like it was connected.

        13 A. Exactly, and if it was not connected, as an absolute

        14 minimum, notification should've been present in that

        15 location for the Fire Brigade, but far more preferably,

        16 that switch should've been removed.

        17 Q. WSP also state in the report that they tried to activate

        18 the fireman's switch on the ground floor and it was

        19 "difficult to operate".

        20 A. That's correct.

        21 Q. So is your understanding that they did try and operate

        22 it as part of their investigation?

        23 A. Yes, they did. I've read their activities. They tried

        24 to place the drop key in it in the wall and they also

        25 removed the box mechanism from the wall and made further
        117

        1 attempts there.

        2 Q. Yes.

        3 A. And neither were successful because the mechanism is

        4 jammed or seized. It can't be moved.

        5 Q. We can go to that in the report.

        6 A. Yes.

        7 Q. So they removed the faceplate, so they did a destructive

        8 examination.

        9 A. Yes, they went and looked at the innards of it all.

        10 Q. They said they discovered the mechanism was seized and

        11 damaged/deformed.

        12 A. Yes.

        13 Q. Can we look at that. So that's figure L.18,

        14 BLAS0000033, pages 31 to 32.

        15 So the left here is the level 2 switch --

        16 A. Yes.

        17 Q. -- with the faceplate removed, where they found the

        18 wires were not connected; is that correct?

        19 A. Yes, that's correct.

        20 Q. The right is the ground level switch with the faceplate

        21 removed.

        22 A. Yes, and the mechanisms at the back there hanging down.

        23 Q. And they found that to be deformed and damaged.

        24 A. Yes, I'll have to rely on their physical activity on

        25 site, which I'm happy to do so, yes.
        118

        1 Q. Do you think that that's consistent with the evidence of

        2 Firefighter Secrett as to the problems he encountered

        3 with activating the switch on the night?

        4 A. I very much do, yes.

        5 Q. Do you think it signifies a potential maintenance

        6 failure with the switch in terms of maintaining it?

        7 A. There is a duty to test those switches, a duty to

        8 understand if they're connected or not, and so, yes,

        9 there is a duty to maintain life safety equipment at all

        10 times in any building.

        11 Q. Do you think it's possible that the reason

        12 Firefighter Secrett could not operate the switch is that

        13 he was using a drop key which didn't have a pin across

        14 it to stop the pin going too far into the access point?

        15 A. No, I do not.

        16 Q. Can you just explain why you don't? Is that because of

        17 other evidence you've seen?

        18 A. Other evidence has been provided to me, and when the

        19 drop key is in the correct position in a mechanism the

        20 same as Grenfell Tower, there is no need for the key to

        21 be pushed as far as hitting off that split pin. So it's

        22 in the correct position, and then there is a gap and

        23 then there is the split pin. So you can't push it

        24 further.

        25 Therefore, I don't understand the relevance of the
        119

        1 split pin in that evidence sent in.

        2 Q. You've also said in your report that it remains unclear

        3 to you whether that ground floor override switch, which

        4 does seem to have been wired at that point --

        5 A. Yes.

        6 Q. -- was in fact interfaced with the lift controllers in

        7 the lift plant room and, if interfaced, whether it was

        8 operable?

        9 A. So, again, WSP have various findings from site and, as

        10 a result of their observations, I actually don't know

        11 now if both lifts or one lift is a fire lift, which one

        12 was connected to the key switch, and therefore how

        13 everything was meant to work, both and one, and if it

        14 was one, which one was it?

        15 SIR MARTIN MOORE-BICK: The drop key has a mechanical

        16 operation, does it? It doesn't have anything --

        17 A. It's in itself mechanical, but my understanding is it

        18 forms some kind of circuit, and that should then be

        19 connected to an interface somewhere else which would

        20 send a signal. Electrical engineering, absolutely

        21 outside my area of expertise.

        22 SIR MARTIN MOORE-BICK: I couldn't help noticing in one of

        23 the earlier pictures someone seemed to be holding what

        24 might be a drop key. Would you recognise one if you saw

        25 it?
        120

        1 A. Oh, I would, yes. I brought a brochure for you.

        2 MS GRANGE: Go to figure L.11, BLAS0000033 at page 25.

        3 A. Yes. So every lift expert in the country will be cross

        4 when I describe it this way, but --

        5 SIR MARTIN MOORE-BICK: It's all right, do your best.

        6 A. That's a drop key for the old-style control.

        7 SIR MARTIN MOORE-BICK: Right.

        8 A. And you can see -- sorry -- that's because this portion

        9 drops (Indicates). You push it in on the horizontal and

        10 it drops down once it gets to the right part for it to

        11 drop down in behind this plate. That's the old style

        12 express key they're called as well.

        13 SIR MARTIN MOORE-BICK: Thank you.

        14 A. Well illustrated in the WSP report.

        15 MS GRANGE: That point about the interfacing and whether

        16 this switch was interfaced with the lift controllers, is

        17 that something you think could be investigated further?

        18 A. I think it very much needs to be investigated to

        19 a considerable detail.

        20 Q. This is probably a good point to note, isn't it, that

        21 you have recommended in your latest report that the

        22 inquiry should appoint a specialist lift expert to look

        23 at this.

        24 A. Yes, I do, because we're getting into the complex

        25 question of what's connected where, how, why, and WSP
        121

        1 also found some curious connections where it may have

        2 been connected to the detection system, linked to the

        3 smoke control panel, which I don't understand at all.

        4 So those interfaces from the lift are very important

        5 to understand now.

        6 Q. Just a couple of questions about the lift as a mode of

        7 evacuation for those with mobility problems.

        8 A. Yes.

        9 Q. You consider that Grenfell Tower was non-compliant with

        10 the B1 means of escape provision. In particular, you

        11 say that Approved Document B does not make specific

        12 requirements, but that you think B1 would require

        13 an adequate means of escape for those who have mobility

        14 problems; is that correct?

        15 A. Yes. So the functional requirement is clear that

        16 everyone can evacuate the building independently without

        17 assistance. The statutory guidance then doesn't make

        18 any specific provision in residential buildings for

        19 those that require assistance.

        20 Q. You've noted in your report that Approved Document B

        21 2010 states that those in wheelchairs will need

        22 evacuation by lifts and, in particular, paragraph 5.39

        23 of ADB allows for a firefighter lift to be used to

        24 evacuate those with mobility problems.

        25 A. That's correct.
        122

        1 Q. That's there in that guidance.

        2 A. It is, and that's a common means of providing

        3 assistance, using the firefighting lift, with all the

        4 additional protection measures, whilst it's available.

        5 Q. But you note that in the event, the lifts could not be

        6 used for that purpose because they were not these

        7 upgraded firefighter lifts.

        8 A. Exactly. They don't have the right emergency power

        9 sources and other protection measures to make them safe

        10 enough to be used to transport people around the tower,

        11 that's correct.

        12 Q. You are aware of some of the issues which arose on the

        13 night, given that the operation of the lifts stayed in

        14 normal mode.

        15 A. Yes.

        16 Q. Firefighter Badillo talks about getting stuck on the

        17 15th when trying to go to the 20th.

        18 A. Yes.

        19 Q. We've also had evidence from Nadia Jafari about what

        20 happened to her father in relation to the lift.

        21 A. Yes, that's correct.

        22 Q. Do you think that given that the lift couldn't be used

        23 as a firefighter lift, or even a fire lift, on the

        24 night, it should've been disabled in the early stages of

        25 the fire to avoid the consequences of it being in normal
        123

        1 operation?

        2 A. Disabled by whom and how?

        3 Q. That's the question. Yes. I mean, possibly --

        4 A. Oh, sorry, I'm not allowed to ask you a question.

        5 Should it have been disabled? Well, frankly, if

        6 I may say, it shouldn't have been provided in that

        7 condition in the first place and that should have been

        8 known.

        9 Q. I take that point, but in terms of on the night, do you

        10 think it might have been possible to, say, block the

        11 doors with firefighting equipment and take it out of

        12 operation? Is that something that could've happened?

        13 A. I've never tried to block a lift with firefighting

        14 equipment. I did observe it being done in the early

        15 stages. You can see that in the CCTV.

        16 As to the practicalities of the Fire Brigade

        17 attempting to do that with equipment in the middle of

        18 an event like this, I think others should comment.

        19 But for me, the primary duty was not to provide

        20 lifts in that condition in the first place.

        21 SIR MARTIN MOORE-BICK: Can I take it that you're not

        22 yourself aware of any way in which the lift could've

        23 been put out of operation by having the power

        24 disconnected or any other way and that would be

        25 reasonably accessible?
        124

        1 A. I would prefer you to ask a lift expert that question,

        2 and then it's who do you phone, what do they do, how do

        3 they get there? A very interesting concept. A proper

        4 lift expert could answer all those questions.

        5 SIR MARTIN MOORE-BICK: Thank you.

        6 MS GRANGE: In terms of the use of the lifts in the very

        7 early stages to fight the fire in flat 16, you say in

        8 your report that the fact that it was not a firefighter

        9 lift may have caused a short delay in arriving at

        10 flat 16. However, you've also noted in your report that

        11 given that firefighters did actually use the lifts in

        12 the event to transport equipment up to the bridgehead in

        13 normal mode, you don't think this caused a delay to the

        14 initial firefighting response.

        15 A. It doesn't seem to have been significant, no, in times

        16 of time, as they relay events.

        17 Q. Yes. Just one final set of questions on this topic.

        18 Do you agree that, when considering whether the fact

        19 that the lifts were not firefighting lifts made

        20 a difference on the night, it may be relevant, for

        21 example, that the LFB policy was that the bridgehead is

        22 set up two floors below the fire floor, and that the

        23 policy is that lifts should not be used above the

        24 bridgehead in a high-rise incident?

        25 Do you think those are potentially relevant in terms
        125

        1 of the impact not having a firefighter lift had?

        2 A. Yes, I do. Yes, I do.

        3 Q. The lifts appear to fill with smoke at a fairly early

        4 stage when they are opened with lobbies.

        5 A. Yes.

        6 Q. Does that mean that using it for firefighting on the

        7 night may have been compromised?

        8 A. Yes, it is, and I've been thinking about that, actually.

        9 I think the overall flow of smoke through the building,

        10 when that's being considered, there is an interesting

        11 sudden change in state in the lifts when you look at the

        12 CCTV, and I would love to understand that to a much more

        13 substantial level of detail than I do at the moment.

        14 It's a very sudden change in state and I'd like to

        15 understand what caused that. Was there some kind of

        16 pressure or flow situation going on in the building

        17 caused by other matters? I think that would be a very

        18 interesting and useful study to do.

        19 Q. Yes.

        20 A. Just to point out, remember, that the lift shaft should

        21 also be provided with a supply of clean air in

        22 a standard pressurisation system, so we'll get on to

        23 that. So it's all interconnected where the smoke was

        24 flowing in terms of the lifts also.

        25 Q. In the light of those points that we've just been
        126

        1 discussing, do you agree that the fact that the lifts

        2 were not firefighting lifts made no difference or no

        3 material difference to the development of the fire in

        4 terms of the ability of the firefighters to carry out

        5 firefighting?

        6 A. In the early stages of the fire, or any stage?

        7 Q. At any stage.

        8 A. I wouldn't want to try and answer that question.

        9 Q. I then want to turn to the smoke ventilation system.

        10 A. Okay.

        11 Q. At this point, it's going to be appendix J, which is

        12 worth having.

        13 What I'd like to do -- this is potentially quite

        14 a complex topic -- is to start by looking back at some

        15 of the slides from your presentation back on 18 June,

        16 just to give a very overall picture of how the system

        17 was configured.

        18 So if we look at BLAS00005481, and go to page

        19 page 173 of that presentation.

        20 A. Yes.

        21 Q. So here what you've given, I think, is a schematic which

        22 shows the operation of the original smoke control

        23 system. That's original as in from the 1970s when

        24 Grenfell Tower was built.

        25 A. Yes.
        127

        1 Q. Can you just explain very briefly how that original

        2 system was intended to work?

        3 A. Yes. So in the event of a fire in a flat, once that

        4 flat door was opened, smoke would enter the lobby and

        5 will be extracted up to the roof by the shafts on the

        6 north side of the lobby, and fresh air was supplied into

        7 the south side of the lobby.

        8 Q. So it's a simple kind of flow of air --

        9 A. Yes, it's a very simple extract system.

        10 Q. Yes.

        11 A. It's important to note that the original system was

        12 a natural system first.

        13 Q. Yes.

        14 A. So the vents opened and the smoke moved by buoyancy

        15 first. Then there was a control for the Fire Brigade to

        16 use where they could switch it to being a mechanical

        17 system then, and then the fans would operate and extract

        18 the smoke.

        19 Q. Yes.

        20 A. So it was natural ventilation until the Fire Brigade

        21 switched on a mechanical extract system.

        22 Q. Is that what is termed a corridor smoke dispersal

        23 system?

        24 A. Dispersal -- yes, exactly, a dispersal system means you

        25 have a means of, I suppose, dispersing the smoke from
        128

        1 the lobby.

        2 Q. It was designed to work on one floor only at that point.

        3 A. Yes, that's correct.

        4 Q. Yes.

        5 If we then go within this presentation to page 179,

        6 you make it clear here -- so what we have, and we'll

        7 follow this through in a moment, is now in

        8 Grenfell Tower, at the time of the fire, there was

        9 a combined lobby environmental system and a smoke

        10 control system?

        11 A. Yes, that's correct.

        12 Q. Is that correct?

        13 A. So, there became a need for environmental air control

        14 because of the new services placed through the lobby

        15 which could cause a build-up of heat in normal

        16 conditions, and so a decision was made to make the

        17 existing system a combined environmental and smoke

        18 extract system.

        19 So day to day, the system was used to deal with

        20 temperature build-up in the lobbies, and then in

        21 an emergency it was to switch over and become a means of

        22 smoke control only.

        23 Q. Again, it's designed to work on one floor only --

        24 A. That's correct.

        25 Q. -- in smoke control mode.
        129

        1 A. Yes.

        2 Q. Can you just, very briefly -- again, because we'll get

        3 into this -- in the environmental mode, how was it meant

        4 to work?

        5 A. In environmental mode, there is a supply of fresh air in

        6 at level 2 that comes up and out on the vents on the

        7 south side. And then the heat is removed -- so that is

        8 supplying fresh air, and then the heat is removed by

        9 means of an environmental fan at the roof, up through

        10 the north side vents.

        11 Q. Then in smoke control mode, just in overview --

        12 A. Yes.

        13 Q. -- in contrast, how is it supposed to work in smoke

        14 control mode?

        15 A. So that mode of operation has to switch off, and then

        16 you extract smoke in two directions: down and out at

        17 level 2, and up and out at the roof.

        18 Q. Is it right that during the refurbishment -- 2012 to

        19 2016 -- new features were introduced to the existing

        20 smoke ventilation system?

        21 A. Yes, that's correct, so new fans, new dampers.

        22 Q. You've listed all to those out. Let's just look at that

        23 at J6.5.2 at BLAS0000031, pages 52 to 53.

        24 So, again, we don't need to go to all of these, but

        25 I wanted to pull out some of the features.
        130

        1 What you've done here in this section of your report

        2 is to explain all the new features that came in at the

        3 time that the smoke vent system was refurbished.

        4 A. Yes. So the existing -- they're called builders' ducts.

        5 Instead of being metal, they're formed with blocks or

        6 concrete. The existing builders' ducts were maintained,

        7 two on either side of the lobby, north side and south

        8 side.

        9 And then new equipment was installed into the tower.

        10 So you've got the four automatically openable vents or

        11 fire dampers, the dampers, at every lobby; there was

        12 a new extract fan combined with the environmental fan

        13 placed up at the roof level; and then there was new

        14 extract fans and new environmental fan down at level 2.

        15 Then down at those lower levels, a series of dampers

        16 also, to allow environmental mode and smoke mode to be

        17 fully -- it was meant to be fully separated at level 2.

        18 There was a need for some new ductwork at level 2

        19 also to bring the system out to the external wall.

        20 Q. Then I think as you go on and explain over the page,

        21 there were a number of other things, including new

        22 controls, control panels, detectors, which we will come

        23 back to?

        24 A. Yes.

        25 Q. So a whole lot of new --
        131

        1 A. Yes.

        2 Q. -- electronic control panels that were introduced.

        3 A. Exactly. It's called a human-machine interface panel

        4 out in the main lobby, which allows day-to-day or

        5 emergency interaction with the system, and then a more

        6 complex control panel in -- I think it's the hub room,

        7 it's called, yes.

        8 Q. Yes.

        9 A. Yes.

        10 Q. Is it right that both the original system that was there

        11 in the 1970s and the refurbished system with all this

        12 new work were bespoke systems?

        13 A. Okay, so the original system had a smaller area of vents

        14 for natural ventilation than CP3 called for.

        15 Q. I am coming to that, yes.

        16 A. Oh, was I meant to just say "yes"? Sorry, yes, just ask

        17 me the question again --

        18 Q. Were they both bespoke systems?

        19 A. Yes, but there's a lot of caveats there. I can't quite

        20 say yes. So, yes, nearly they were.

        21 Q. In terms of combining that environmental system and the

        22 smoke extract system is it common for both systems to be

        23 combined? Do we see that in other buildings?

        24 A. You can see it in other buildings, but I'm relying on

        25 Max Fordham, who said it was unusual in their paperwork.
        132

        1 But it would be a lie to say it's never been done

        2 before; it is done.

        3 Q. Is it common that both systems can share the same

        4 shafts? Is that common?

        5 A. It's not very common.

        6 SIR MARTIN MOORE-BICK: Can I make sure I've understood what

        7 is going on here?

        8 A. Yes.

        9 SIR MARTIN MOORE-BICK: The north side vents and trunking

        10 was essentially always there?

        11 A. Was always there, yes.

        12 SIR MARTIN MOORE-BICK: And it was always an exhaust system

        13 to the roof?

        14 A. Yes.

        15 SIR MARTIN MOORE-BICK: The south side started life as

        16 an inflow system and had to be changed as a result of

        17 the refurbishment --

        18 A. Indeed.

        19 SIR MARTIN MOORE-BICK: -- to an outflow system?

        20 A. Yes, it had to do two things after the refurbishment.

        21 SIR MARTIN MOORE-BICK: So when the system was operating

        22 in -- what do you call it? -- ventilation or --

        23 A. Environmental mode.

        24 SIR MARTIN MOORE-BICK: Environmental mode.

        25 A. Yes.
        133

        1 SIR MARTIN MOORE-BICK: What was the south system doing?

        2 A. It was supplying -- there was a supply fan at level 2

        3 taking air from outside the building, pushing it up --

        4 if you imagine pushing that pressure up --

        5 SIR MARTIN MOORE-BICK: So it was doing the same job as it

        6 was before, it was feeding air into the system?

        7 A. Yes, but for environmental reasons only.

        8 SIR MARTIN MOORE-BICK: Sure, sure.

        9 A. Correct, yes.

        10 SIR MARTIN MOORE-BICK: I probably ought to know the answer

        11 to this but I don't off the top of my head: when it

        12 changed into smoke extract system --

        13 A. Yes.

        14 SIR MARTIN MOORE-BICK: -- did the fan on the south side

        15 simply turn the other way, or was there a second fan

        16 that --

        17 A. There was a second fan.

        18 SIR MARTIN MOORE-BICK: Right.

        19 A. So the environmental fan switches off, the dampers go

        20 into a specific arrangement to seal that part of the

        21 system, and then your extract fan goes on, the dampers

        22 open, and now you can pull the smoke down.

        23 SIR MARTIN MOORE-BICK: And you've presumably got a second

        24 line of trunking between, at some point --

        25 A. At some point.
        134

        1 SIR MARTIN MOORE-BICK: In which the extract fan is

        2 operating.

        3 A. That's correct.

        4 SIR MARTIN MOORE-BICK: Right.

        5 A. They shared a lot of that. There is a good drawing in

        6 my report -- I don't know if you want to look at it --

        7 but they did share some of the ductwork there and the

        8 dampers were placed to separate the the two fans.

        9 SIR MARTIN MOORE-BICK: I think I understand the basic.

        10 A. But, in essence, it's meant to separate, and then the

        11 extract fan and ductwork are safely used to extract

        12 smoke, or that switches off and you go back to opening

        13 up the right piece of ductwork for the supply fan and

        14 operate in environmental mode.

        15 SIR MARTIN MOORE-BICK: Thank you very much.

        16 MS GRANGE: I think we're going to come to that diagram in

        17 a moment.

        18 Just going back to the original system -- I think

        19 you've just said this -- you've said the key reason why

        20 you think the original system didn't comply with CP 371

        21 was that there was an inadequate aggregate area of the

        22 smoke shafts. You've said that the aggregate area was

        23 significantly lower than the area recommended; it was

        24 only about 0.48 metres squared, whereas it should've

        25 been 1.5 metres squared; is that correct?
        135

        1 A. That's correct.

        2 Q. Could that makes a difference to the operation of the

        3 system when you don't have the right aggregate area?

        4 A. Yes, there's less -- I suppose the best way of putting

        5 it is that there is less room for the smoke to flow out

        6 under buoyancy and get to the top of the building.

        7 Q. So then let's come to the newly-refurbished smoke

        8 control system.

        9 You have in your appendix J assessed that system in

        10 accordance with the guidance in Approved Document B

        11 2013.

        12 A. Yes, I have.

        13 Q. Do you agree that the design basis assumed in Approved

        14 Document B for a smoke control system is on the basis of

        15 a fire starting in a single location and being contained

        16 within a single apartment?

        17 A. Yes, I do.

        18 Q. So, consequently, a smoke control system designed in

        19 accordance with that guidance would only be required to

        20 disperse smoke from a single common lobby, not in

        21 multiple lobbies on multiple levels?

        22 A. That's correct.

        23 Q. Section 2.27 of Approved Document B 2013 gives us

        24 an alternative to the natural ventilation route to

        25 compliance, a mechanical option using pressure
        136

        1 differentials; is that correct?

        2 A. Yes, so there's natural, there's mechanical and there's

        3 pressure differentials, which is a form of mechanical.

        4 There are other mechanical types.

        5 Q. We're going to look at the differences between those in

        6 a moment.

        7 Can we look at Approved Document B 2013, that's

        8 CLG00000224 on page 28.

        9 Yes, I just want to start by looking at the bottom

        10 right-hand column, "Smoke control of common escape

        11 routes", 2.25, right at the very bottom.

        12 A. Yes.

        13 Q. So this, I think, tells you the purpose of providing

        14 smoke control. So it says:

        15 "Despite the provisions described in this Approved

        16 Document, it is probable that some smoke will get into a

        17 common corridor or lobby from a fire in a flat, if only

        18 because the entrance door will be opened when the

        19 occupants escape."

        20 A. That's correct.

        21 Q. If we can go on to the next page, if we can highlight

        22 the top of that page to start with, it says:

        23 "There should therefore be some means of ventilating

        24 the common corridors/lobbies to control smoke and so

        25 protect the common stairs. This offers additional
        137

        1 protection to that provided by the fire doors to the

        2 stair."

        3 And then we see this:

        4 "This can be achieved by either natural means in

        5 accordance with paragraph 2.26 or by means of mechanical

        6 ventilation as described in paragraph 2.27."

        7 A. That's correct.

        8 Q. If we can then look at paragraph 2.27, on that same

        9 page. There it says:

        10 "2.27. As an alternative to the natural ventilation

        11 provisions in paragraph 2.26, mechanical ventilation to

        12 the stair and/or corridor/lobby may be provided to

        13 protect the stair(s) from smoke. Guidance on the design

        14 of smoke control systems using pressure differentials is

        15 available in BS EN 12101-6:2005."

        16 A. That's correct.

        17 Q. So those are the key parts of Approved Document B; is

        18 that correct?

        19 A. Yes, they are.

        20 Q. So it's directing the reader to the guidance in that

        21 British Standard for pressure differential systems?

        22 A. If one is going to design based on pressure

        23 differentials.

        24 Q. Just pausing there -- and I know you were just touching

        25 on it -- can you just first explain the difference
        138

        1 between a natural ventilation and mechanical ventilation

        2 system?

        3 A. Okay. So just in very, very simplistic terms -- again,

        4 these things are explained in substantially more detail

        5 in various British Standards -- a natural smoke extract

        6 system is providing an opening so smoke can leave the

        7 space by means of its own natural buoyancy while it's

        8 hot.

        9 A mechanical system is using fans to extract smoke

        10 from the fire zone.

        11 A pressure differential system is somewhat

        12 different. It does use mechanical devices, but it isn't

        13 to extract smoke from the fire zone; it's to stop the

        14 smoke from leaving the fire zone.

        15 So it's really important that I make it clear that

        16 there is a difference between a mechanical system and

        17 a pressure differential system and what they're trying

        18 to do.

        19 So when you provide fans and other devices for

        20 a pressure differential system, your goal only is to

        21 stop the smoke leaving the fire zone. It isn't to

        22 remove the smoke from the fire zone.

        23 SIR MARTIN MOORE-BICK: So you're, what, raising the

        24 pressure in the lobby in this case?

        25 A. Well, I'm afraid I can't say that here, but --
        139

        1 SIR MARTIN MOORE-BICK: No, no, just to get the concept.

        2 A. The concept is you raise the pressure in a protected

        3 zone to stop the smoke leaving the fire zone.

        4 SIR MARTIN MOORE-BICK: And effectively, if there's

        5 leakages, it's going to be of clean air into the fire

        6 zone?

        7 A. It's -- yes. Yes.

        8 SIR MARTIN MOORE-BICK: So you wouldn't have the sort of

        9 grilles and trunking that we've got on the north side,

        10 which is simply letting air escape to the outside?

        11 A. Can I answer that question a little bit later? Just ...

        12 MS GRANGE: Yes, I think some of the diagrams we're about to

        13 come to can help.

        14 A. Yes. So there is Grenfell Tower and then there is

        15 a pressurisation and depressurisation system as it

        16 should be done, yes.

        17 SIR MARTIN MOORE-BICK: A very simple -- well, it may not be

        18 simple. I've come across this in the context of

        19 laboratories, for example, handling dangerous materials.

        20 A. Yes.

        21 SIR MARTIN MOORE-BICK: So you pressurise the laboratory to

        22 keep the air out.

        23 A. Exactly. Exactly. That's what should happen. So the

        24 location of your equipment must be in the right place to

        25 allow you to pressurise the right zone, to prevent the
        140

        1 products of combustion leaving the fire zone. Exactly.

        2 MS GRANGE: So just to be clear, a pressurised system, that

        3 could be pressurisation of the stair and the lobby and

        4 the lift shaft, that's the protected space is

        5 pressurised relative to the fire zone or flats; is that

        6 right?

        7 A. Yes. So there's two types of pressure differential

        8 system, one where you pressurise and one where you

        9 depressurise, and I'd really love to be able to refer to

        10 some diagrams while I explain this.

        11 Q. Is this the point where you want to refer to your

        12 sketches?

        13 A. I would like to, because I do think it's fiendishly

        14 complex to understand.

        15 Q. If we go to BLAS0000038, I think what you've done is,

        16 for the purposes of your oral evidence, you've prepared

        17 some very basic cartoons or sketches --

        18 A. Yes.

        19 Q. -- to try and help you explain this; is that correct?

        20 A. Yes.

        21 Q. BLAS0000038.

        22 A. Yes.

        23 Q. So can you talk us through this slide?

        24 A. So a pressure differential system comes in two

        25 forms: a pressurisation system and a depressurisation
        141

        1 system.

        2 In a pressurisation system, air is supplied into the

        3 lift, it's supplied into the lobby and it's supplied

        4 into the stair. Okay? The idea, then, is when you open

        5 the fire zone door, the products of combustion are

        6 prevented from leaving. Okay? So that's a

        7 pressurisation system.

        8 If I'm able to look at the next one. Okay.

        9 So it's important to understand that

        10 a depressurisation system in the British Standard is

        11 typically recommended for basements only, where the fire

        12 zone is sealed. There, the idea is you extract the

        13 products of combustion from the fire zone, at a rate

        14 that, when you open this door, because of air supply in

        15 the protected space, again, the products of combustion

        16 cannot leave the fire zone.

        17 So you have your pressure differential, but the

        18 extract rates and design here are not to remove the

        19 products of combustion completely from the fire zone;

        20 it's at enough of a rate, with the pressure

        21 differential, to prevent the smoke flowing out onto the

        22 lobby, mainly. Okay?

        23 So pressurisation, all the equipment focuses on the

        24 protected escape route; depressurisation is meant to

        25 focus on the fire zone to prevent smoke leaving the fire
        142

        1 zone and going out to the lobby.

        2 SIR MARTIN MOORE-BICK: Thank you.

        3 MS GRANGE: I think it's worth sticking with these. Do you

        4 want to go through your next slide?

        5 A. Okay, if I can see the next one.

        6 Q. Can you just explain, this is the Grenfell smoke

        7 ventilation system --

        8 A. Yes, okay.

        9 Q. -- is that right, that you're trying to illustrate?

        10 A. Yes. So here I'm trying to explain that, at

        11 Grenfell Tower, we appear to have a depressurisation

        12 system, but it isn't installed to deal with the fire

        13 zone; instead, it is installed to deal with the lobby.

        14 Okay?

        15 What that means, because of that pressure

        16 differential and the focus being the lobby, once you

        17 open the fire zone door, the products of combustion are

        18 attracted out to the location of where the equipment is

        19 extracting from the lobby.

        20 SIR MARTIN MOORE-BICK: Yes.

        21 A. Okay?

        22 MS GRANGE: And I think there's another slide that completes

        23 this run.

        24 A. Yes.

        25 Q. It's not the next page because the next page is blank,
        143

        1 I think.

        2 A. That's fine.

        3 Q. That slide.

        4 A. Actually, can we just go back to the other slide?

        5 Sorry.

        6 So at Grenfell, the system is designed that there is

        7 an extract rate from the lobby, and the system is

        8 balanced such that when you open this one stair door,

        9 the idea is the airflow across that door should prevent

        10 smoke moving from the lobby to the stair. But it

        11 assumes every other door was closed in making the

        12 calculations for that.

        13 When we go to the next slide, once you open a second

        14 door, the area of opening, if you like, increases, and

        15 so you can't maintain the necessary airflow across one

        16 door because now you've got two doors open.

        17 Also, the extract is pulling the smoke from the fire

        18 zone out.

        19 So it causes two things: attracting the smoke out,

        20 and reducing the ability to maintain the required

        21 airflow at that door, because a second door has been

        22 open.

        23 SIR MARTIN MOORE-BICK: Right.

        24 MS GRANGE: Just a few questions to build up to your

        25 preliminary views about this.
        144

        1 A. Yes.

        2 Q. So is it right that in all types of smoke control

        3 system, vents on the fire floor are opened and vents on

        4 all other floors are closed in order to allow the full

        5 capacity of the smoke control system to be directed at

        6 a single floor?

        7 A. Typically, yes.

        8 Q. Can you explain for us why it is that you've assessed

        9 the compliance of the system at this stage against the

        10 requirements of BS EN 12101-6:2005, the British Standard

        11 we saw in ADB?

        12 A. Yes, because in the PSB documentation, it refers to some

        13 specific criteria from the pressure differential

        14 standard.

        15 Q. So in the documentation you've seen, it's referring to

        16 some of the --

        17 A. Yes, it does.

        18 Q. -- criteria that are in that British Standard?

        19 A. Yes, it does.

        20 Q. That's a British Standard for pressure differential

        21 systems?

        22 A. Yes. But it wasn't called a depressurisation system in

        23 the documentation dated from before the fire.

        24 Q. That's what I was coming onto. So it's clearly not

        25 a pressurisation system; do you think it was
        145

        1 a depressurisation system?

        2 A. In the sense that there is extract from a zone relative

        3 to the fire zone, and a stated attempt in the

        4 documentation to provide a pressure differential across

        5 a particular door and provide a flow rate across the

        6 stair door, and looking at the ability to open a door.

        7 And they're all features of the design basis using

        8 pressure differentials.

        9 Q. Is it right that that pressure differential between the

        10 stairs and the lobby that you were just talking about

        11 was -25 Pa; is that right?

        12 A. That's stated in the documentation.

        13 Q. Yes. What does PA stand for?

        14 A. Pascals.

        15 Q. Yes.

        16 A. Yes, Pascals.

        17 Q. Is that a unit used to measure pressure equal to

        18 1 Newton per meter squared?

        19 A. Yes, yes.

        20 Q. Back to that British Standard, and you mentioned

        21 basements before, do you think that the British Standard

        22 only applies to depressurisation systems in basements?

        23 A. No, it says "typically" rather than "always", yes.

        24 Q. We can perhaps look at what it actually says at

        25 paragraph J5.2.22 of your report. That's BLAS0000031,
        146

        1 page 34, where you've set out a key part of that

        2 standard, if we just zoom in on that.

        3 A. Oh, that's a different part. Yes, yes.

        4 Q. Is it right that it gives an example -- we see that in

        5 the second line --

        6 A. Yes.

        7 Q. -- of a basement. So it says:

        8 "The objective of a depressurization system is to

        9 achieve the same protection at a doorway between the

        10 depressurized space (e.g. a basement) and the protected

        11 space ..."

        12 Is that right?

        13 A. Yes.

        14 Q. In the very last part of this extract from the

        15 British Standard, it says, the last sentence:

        16 "The most appropriate use of depressurization

        17 systems is likely to be in basement spaces, see

        18 Figure 18 ..."

        19 A. Yes.

        20 Q. Is that why you said most frequently used in basements,

        21 but you don't think it's only confined to basements?

        22 A. Yes, and I think that's got to do with the earlier

        23 sentence "bounded on all sides by fire-resisting

        24 constructions". Just slightly up there:

        25 "To be effective, each depressurized space shall be
        147

        1 bounded on all sides by fire-resisting constructions,

        2 because any loss of integrity would result in

        3 equalization of pressure between the depressurization

        4 zone and external air."

        5 To cut a very long story short, if a window can

        6 break, the balancing of your system is lost, and that's

        7 why in a basement space, you know that risk isn't there.

        8 Q. Yes.

        9 A. Okay?

        10 Q. Is that why it's so important to know what you're doing

        11 about doors being opened?

        12 A. Absolutely.

        13 Q. Which we'll come on to in a moment.

        14 A. Absolutely.

        15 Q. So if you open more doors, it's going to affect your

        16 calculations.

        17 A. Exactly. The purpose of all your design decisions are

        18 to create what I would call a balanced system with the

        19 correct openings allowed for.

        20 Q. Is your position that that British Standard that we're

        21 just reading from could be viewed as setting out

        22 functional objectives or measurable performance

        23 requirements which could be used to assess the adequacy

        24 of a pressure differential system as against the

        25 Building Regulations? Is that one way you could use it,
        148

        1 ie not strictly following every letter of it, but

        2 looking at functional objectives or performance

        3 requirements that it's setting?

        4 A. Yes, I do. It actually is very clear on functional

        5 objectives, particularly when it gets to explaining

        6 where the smoke should not go, in terms of a single

        7 stair and lobby used for firefighting.

        8 So I think that British Standard is very clear on

        9 functional objectives, and then it gives additional

        10 guidance on how to achieve them.

        11 Q. Is it right that you've said in your latest report that

        12 you'd like to be provided with evidence from the design

        13 team at Phase 2 about what route to compliance they

        14 thought they were adopting, and that you will review any

        15 such evidence before you reach any final view on

        16 compliance of the system?

        17 A. That's correct.

        18 Q. I think you've already accepted that the Building

        19 Regulations required the system to be no worse than the

        20 original smoke vent system.

        21 A. I don't accept that, no.

        22 Q. But you haven't considered anything to do with the

        23 non-worsening principle yet.

        24 A. I haven't done that, and it will be interesting to see

        25 the calculations as to what the original mechanical
        149

        1 extract system could do relative to this version now.

        2 Q. Would you agree that a smoke ventilation system using

        3 pressure differential principles is not the only type of

        4 mechanical ventilation system which could be considered

        5 acceptable to comply with the Building Regulations?

        6 A. Yes, I do.

        7 Q. Do you agree that tailor-made solutions can be

        8 appropriate?

        9 A. Tailor-made solutions that deliver on the required life

        10 safety objectives and fire safety objectives, yes, and

        11 this British Standard is very clear that the stair and

        12 lobby are to be kept safe for firefighting purposes when

        13 the flat door is open and multiple other doors are open

        14 at the same time.

        15 Q. Would you agree that most smoke ventilation systems are

        16 usually bespoke and that they don't use natural

        17 ventilation or pressurisation or depressurised

        18 principles?

        19 A. No, I would not.

        20 Q. Would you agree that there are known alternatives to

        21 such systems, such as the BRE shaft system or the

        22 ColtShaft system?

        23 A. I'm aware that they exist.

        24 Q. Are either of those similar to what was installed at

        25 Grenfell Tower?
        150

        1 A. I don't want to answer that question at the moment.

        2 Q. Because you don't have enough information?

        3 A. I don't have enough information, and I haven't done

        4 a proper comparison of those systems to give my view.

        5 I'm happy to do so.

        6 Q. Could such systems comply with the functional

        7 requirements of the Building Regulations in principle?

        8 A. If they were designed and installed appropriately.

        9 MS GRANGE: What I'm going to do is just turn to your

        10 current assessment of the system and just look in

        11 general at that.

        12 Before we get to smoke dampers, we might take

        13 a break. If I can just do a few more questions before

        14 that.

        15 SIR MARTIN MOORE-BICK: Yes, all right.

        16 MS GRANGE: So what you have concluded -- is this right? --

        17 is that the system appears to have been intended to

        18 comply with one aspect of that British standard, namely

        19 the airflow performance of a class B pressure

        20 differential system as defined in that spec.

        21 A. Yes, it refers to the airflow across the stair to lobby

        22 door, and it also refers to the correct force to allow

        23 one to open that door.

        24 Q. But as I understand your evidence, you consider that

        25 there are five key requirements for a class B system,
        151

        1 not just that airflow performance, and that includes

        2 a pressure differential criterion; is that correct?

        3 A. Yes.

        4 Q. We can see those five key requirements listed out in

        5 your paragraph J5.2.16, if we could just bring that up.

        6 That's BLAS0000031, at page 33.

        7 So you've listed them out.

        8 A. Yes, that's easier.

        9 So a class B pressure differential system is for the

        10 purposes of protecting a firefighting stair and lobby.

        11 So it requires the designer to consider the flat door

        12 being open, the stair door on that lobby being open, as

        13 well as the stair door below, and also there's

        14 requirements for the lift.

        15 So there's rules for providing the right pressures,

        16 and they're multiple requirements; the right airflow,

        17 and they're multiple requirements; also air supply and

        18 various other things.

        19 So all together, they provide a balanced system that

        20 keeps smoke away from the lobby and stair as a result of

        21 it flowing out of the flats.

        22 Q. Can we go to your figure J.50. I think this is where we

        23 see a good diagram that you've marked up of the

        24 refurbished system.

        25 That's it, yes. If we can blow that up.
        152

        1 So there, this is your attempt to try and explain

        2 the programmed operation of the smoke control system is

        3 that correct?

        4 A. Yes, that it operates on one floor.

        5 Q. Yes.

        6 A. And the smoke is extracted down the south shaft and up

        7 the north shaft.

        8 Q. So we see it going out of the south shaft --

        9 A. Yes.

        10 Q. -- up and out of the north shaft --

        11 A. At the roof, yes.

        12 Q. -- removal of the air from the lobby --

        13 A. Yes.

        14 Q. -- and you say design intent 2 metres per square through

        15 the one open stair door; yes?

        16 A. Yes, exactly. So that airflow was designed for with the

        17 stair door open, that the system would cause that

        18 airflow at that door and prevent the smoke flowing into

        19 the stair. But in this design, no other door being open

        20 was provided for. So everything was shut, except the

        21 stair door.

        22 SIR MARTIN MOORE-BICK: If the system is operating, it's

        23 taking air out of the lobby --

        24 A. Yes.

        25 SIR MARTIN MOORE-BICK: -- in two different directions.
        153

        1 A. Yes. Yes.

        2 SIR MARTIN MOORE-BICK: To that extent, it's exerting some

        3 degree of pressure on the stair door to keep it closed.

        4 A. Yes.

        5 SIR MARTIN MOORE-BICK: The stair door ought to be fitted

        6 with smoke seals.

        7 A. Yes.

        8 SIR MARTIN MOORE-BICK: But it still lets enough air in,

        9 does it, to compensate for the loss of pressure in the

        10 lobby?

        11 A. One has to make that decision during design, how you are

        12 going to allow that release of pressure so you can open

        13 the door.

        14 SIR MARTIN MOORE-BICK: In layman's terms, you've got to get

        15 air from somewhere?

        16 A. You certainly do.

        17 SIR MARTIN MOORE-BICK: It could come from the flats

        18 surrounding the lobby, whose doors won't be airtight.

        19 A. Correct.

        20 SIR MARTIN MOORE-BICK: But should be smoke-tight.

        21 A. Should be, same with the stair door, or you might

        22 provide air release -- you might provide something

        23 specifically in the lobby to allow that air release.

        24 SIR MARTIN MOORE-BICK: Okay.

        25 A. Okay?
        154

        1 SIR MARTIN MOORE-BICK: But as soon as you open the door to

        2 the flat where the fire is --

        3 A. Yes.

        4 SIR MARTIN MOORE-BICK: -- you are inevitably -- again, in

        5 layman's terms -- sucking combustion products out of

        6 that flat?

        7 A. That's correct, yes.

        8 SIR MARTIN MOORE-BICK: Yes, all right, thank you.

        9 A. Yes.

        10 MS GRANGE: Just back to how this was meant to work, as you

        11 explained earlier, the environmental system was to

        12 deactivate, shutting down and isolating the

        13 environmental fans at lower level.

        14 A. Yes.

        15 Q. And then the automatic opening vents on the fire floor

        16 only were to open --

        17 A. That's correct.

        18 Q. -- and all other floors, the automatic opening vents

        19 were meant to stay shut.

        20 A. They were to shut if they were open or stay shut.

        21 Q. The role of those dampers -- we're going to come back to

        22 those in a little bit of time -- they are to stop the

        23 flow of air through a duct. Is that what a damper does?

        24 A. So --

        25 Q. We have dampers all the way up, don't we, on the AOVs,
        155

        1 behind the AOVs?

        2 A. Yes. So those dampers shut to seal that riser. It's

        3 almost like closing the compartment. So it prevents

        4 anything leaving the duct, ideally, as it's moving down

        5 to the south, up to the north. That's one reason why

        6 it's sealed. And it's also acting as the wall, if you

        7 will, to prevent fire and smoke products from other

        8 floors.

        9 So dampers are -- it's like a door sealing

        10 a compartment, again. You're closing a hole in

        11 a protected riser.

        12 Q. In this diagram, you've identified some concerns you

        13 have about the way the system was set up to run at the

        14 bottom in little red boxes.

        15 A. Yes.

        16 Q. Are any of those likely to have made a difference on the

        17 night, given that --

        18 A. So I don't know, and I've made clear in my report what

        19 I need to know. It's either just a paperwork error, so

        20 the papers I have aren't up to date -- but at the

        21 moment, based on the programming in the panel, it

        22 doesn't appear that there is a proper power supply in

        23 and out of those dampers. But that's what I've asked

        24 for documentation to confirm either way.

        25 Q. I just want to try and summarise your current views
        156

        1 about the design of the system based on what you've seen

        2 to date.

        3 A. Yes.

        4 Q. So you said that at Grenfell Tower it was a system

        5 whereby each flat should have been a depressurised zone,

        6 but in fact it was a system which depressurised the

        7 lobbies relative to the flats and the stairs, and that's

        8 not a system envisaged by the British Standard.

        9 A. Not as I understand it.

        10 Q. You say that the airflow criterion in the British

        11 Standard is a minimum airflow of 2 metres per second

        12 through the open door between the lobby and the fire

        13 flat must exist.

        14 A. Yes.

        15 Q. But is it right that the design at Grenfell was such

        16 that the system was said to provide an average open-door

        17 velocity, with no other open-door conditions?

        18 A. That's correct, as I read the technical specification,

        19 yes.

        20 Q. So you have a concern at the moment that there may have

        21 been no allowance for the fact that both the flat door

        22 and the stair door might have to be open during

        23 firefighting operations and the system should still be

        24 able to deal with that and cope with that.

        25 A. Yes, that's the whole functional point of a class B
        157

        1 system, which is to aid firefighting.

        2 Q. You've also referred to the fact that it provides for

        3 a single pressure differential of -25 Pascals, which was

        4 not referred to in the British Standard.

        5 A. That's correct.

        6 Q. That referred to pressure differential requirements at

        7 three different locations.

        8 A. Yes, it did.

        9 Q. And that the British Standard required four more

        10 performance requirements for a class B system --

        11 A. Yes.

        12 Q. -- which we just looked at.

        13 A. That's correct.

        14 Q. You also say, since it was based on depressurisation

        15 principles, there were ten separate additional

        16 requirements which you've looked for and you've not

        17 found.

        18 A. Yes, no, I haven't.

        19 Q. Only one you think may have been met at this stage.

        20 A. Yes, that's correct.

        21 Q. Is it right that your fundamental concern is that, in

        22 a depressurisation system, the flats should be

        23 depressurised relative to the stair and the lobby, but

        24 at Grenfell Tower the lobby was depressurised relative

        25 to the flats and the stair?
        158

        1 A. Yes.

        2 Q. Is the concern that this might draw smoke into the lobby

        3 both from the flats and also the stair?

        4 A. Yes.

        5 Q. And that's your --

        6 A. Particularly the flats, yes.

        7 Q. What about if other flat doors were open onto the lobby?

        8 Is that something that also should have been thought

        9 about?

        10 A. Well, because of depressurising that zone, the more

        11 doors you open, the more the zone is impacted.

        12 Q. Yes.

        13 SIR MARTIN MOORE-BICK: But the other flat doors which are

        14 not affected by fire will simply give you a better

        15 airflow, won't they?

        16 A. It's not just about airflow; it's about pressure balance

        17 as well, and the fans are connected to pressure sensors.

        18 So everything changes all the time in a pressure

        19 differential system.

        20 SIR MARTIN MOORE-BICK: Right.

        21 MS GRANGE: Yes.

        22 A. So it isn't just that there's good airflow coming

        23 through the flat door.

        24 SIR MARTIN MOORE-BICK: Mm, all right.

        25 A. It's how the pressure balance is then impacted and what
        159

        1 other resulting flows are near the stair. Yes.

        2 Q. Just to be clear, you've not formed any final view on

        3 compliance in relation to this and you would like to

        4 hear from the design team --

        5 A. Yes, I would.

        6 Q. -- at Phase 2 so you can understand --

        7 A. Understand all --

        8 Q. -- how the system was meant to work --

        9 A. Exactly, yes.

        10 Q. -- and how they were complying with the functional

        11 requirements of the Building Regulations.

        12 A. Yes, because as I read it now, I don't understand how at

        13 all it could be a class B system.

        14 MS GRANGE: Thank you.

        15 Mr Chairman, I think that's a good time for a break

        16 because I'm moving on to another subtopic within this,

        17 but I think we're still in good shape to finish.

        18 SIR MARTIN MOORE-BICK: We're going to either have

        19 a slightly shorter break or a longer break.

        20 MS GRANGE: I suggest we have a slightly longer break, and

        21 I aim to then finish -- oh, we will have to have another

        22 break.

        23 SIR MARTIN MOORE-BICK: No, no, I don't think we need

        24 another one after that.

        25 MS GRANGE: Well, I'll have to mop up any questions.
        160

        1 SIR MARTIN MOORE-BICK: Oh, that one doesn't count.

        2 I think we'll have a slightly longer break,

        3 otherwise it will be very short. I'm going to stop for

        4 just over 10 minutes.

        5 MS GRANGE: 3.25.

        6 SIR MARTIN MOORE-BICK: 3.25, exactly. All right? Thank

        7 you very much.

        8 Good, thank you. 3.25, please, thank you.

        9 (3.10 pm)

        10 (A short break)

        11 (3.25 pm)

        12 SIR MARTIN MOORE-BICK: Yes, now ...

        13 THE WITNESS: Yes.

        14 SIR MARTIN MOORE-BICK: Ready?

        15 THE WITNESS: Yes.

        16 SIR MARTIN MOORE-BICK: Good.

        17 MS GRANGE: Yes, thank you.

        18 A. Could I just add to something from earlier? It's good

        19 to have a coffee break sometimes.

        20 So I think I should be clear that when a system

        21 based on pressure differentials is being allowed for,

        22 the S requirement for fire doors is not provided. So

        23 the smoke seals. Okay?

        24 SIR MARTIN MOORE-BICK: Oh, right.

        25 A. In a new building.
        161

        1 SIR MARTIN MOORE-BICK: Yes.

        2 A. The second thing I should have said is the fans are

        3 connected to a pressure sensor, which is monitoring the

        4 pressure difference between the stair and the lobby all

        5 the time, and so the fans -- you could say they're

        6 changing. You asked about what happens if X, Y door

        7 start to open. So all the time it's monitoring that

        8 pressure difference. So it's not a steady state system.

        9 SIR MARTIN MOORE-BICK: It's much more sophisticated than

        10 I gave it credit for.

        11 A. Potentially, yes. It's much more complex, anyway. Yes.

        12 SIR MARTIN MOORE-BICK: All right. Thank you.

        13 Yes, Ms Grange.

        14 MS GRANGE: Thank you.

        15 I want to move to the topic of smoke dampers now,

        16 because you've raised some concerns about those in your

        17 report.

        18 A. Yes.

        19 Q. Can we just look at a picture of what we're talking

        20 about. I think there's a good one in your presentation

        21 of the 18 of June, if we go to page 176 of that. That's

        22 BLAS00005481, page 176.

        23 Have I got this right? So you've got them as

        24 rotating blades here. Can we see the dampers on here?

        25 A. Yes, I can. I think they're from the new floors, but
        162

        1 they're dampers, sorry, yes.

        2 Q. I'm trying to get the principle of what a damper is.

        3 A. Yes.

        4 Q. If you can just explain to us.

        5 A. So it's a metal mechanical device that can be controlled

        6 into the shut position on the right.

        7 Q. Yes. So open on the left and the shut on the right.

        8 A. Yes.

        9 Q. It's meant to then provide a seal so that the smoke

        10 going behind it doesn't leak through; is that correct?

        11 A. Where a seal is required.

        12 Q. Yes.

        13 A. And so -- yes, because in other buildings, a seal may

        14 not be required.

        15 Q. I see, yes.

        16 A. Yes.

        17 Q. You've explained in detail in your report that because

        18 the smoke extract system was a powered pressure

        19 differential system, these dampers were required to meet

        20 certain enhanced standards for smoke control dampers to

        21 ensure that they achieved a 60-minute rating for

        22 integrity and smoke leakage; is that correct?

        23 A. Yes, because they're in a lobby in a residential

        24 building.

        25 Q. Yes.
        163

        1 A. Yes.

        2 Q. I understand.

        3 You've explained in your report that the smoke

        4 dampers in the north and south shafts were series 54

        5 smoke dampers manufactured by a company called Gilberts

        6 and supplied to Rydon's subcontractor, PSB; is that

        7 correct?

        8 A. Correct.

        9 Q. You've identified some evidence in your most recent work

        10 which would suggest that these dampers weren't tested to

        11 the relevant enhanced standards for smoke control

        12 dampers. Indeed, it would appear that they weren't

        13 properly tested to certain lower standards; is that

        14 correct?

        15 A. Yes, they've actually failed the smoke leakage test, and

        16 they were not tested in the proper I would say position

        17 in the fire damper tests.

        18 Q. Is it right that in order to satisfy the requirements of

        19 that lower standard, they had to be tested from the open

        20 position, and if they take a certain amount of time, or

        21 in excess of 2 minutes, to close, the test is failed?

        22 A. That's correct. It has to show it can do its opening

        23 and closing action in the test.

        24 Q. Was the ability of a damper to close effectively on all

        25 floors away from the fire, on being subjected to heat
        164

        1 and smoke, fundamental to the performance of the smoke

        2 control system at Grenfell Tower?

        3 A. It was fundamental to the function of the builders'

        4 ducts acting as an adequate compartment.

        5 Q. So these are the shafts -- the builders' ducts that have

        6 been used are the shafts --

        7 A. Yes.

        8 Q. Particularly the north shaft, to extract the smoke away

        9 from the lobby.

        10 A. Yes.

        11 Q. These are what protects --

        12 A. Yes.

        13 Q. -- the lobby on all floors.

        14 A. On all floors, exactly.

        15 Q. On the fire floor where it's working, it opens.

        16 A. It opens, and that's absolutely fine. The products of

        17 combustion can enter, but then those products have to be

        18 kept within that protected riser. They cannot exit on

        19 any floor.

        20 Q. Is it right that you have picked up that there is some

        21 evidence from the BSRs which would suggest that smoke

        22 was entering the lobbies via these kind of smoke

        23 vents --

        24 A. Yes.

        25 Q. -- on particular floors?
        165

        1 A. There is some evidence on some floors that smoke was

        2 observed to leak from the location of the builders'

        3 ducts, yes.

        4 Q. We had oral evidence from Farhad Neda in particular in

        5 relation to that; is that correct?

        6 A. Yes, we did.

        7 Q. Do you think that that evidence is potentially important

        8 in the context of the problems that you have identified

        9 with the dampers?

        10 A. Yes, yes, I do.

        11 Q. Could this potentially indicate a failure to comply with

        12 compartmentation rules for protected shafts?

        13 A. Yes, it could.

        14 Q. Do you think there are any other potential explanations

        15 that you're aware of at this stage for what Mr Neda says

        16 he witnessed on his floor? Could it have been anything

        17 to do, for example, with the firefighters operating the

        18 HMI panel? I mean, is that possible?

        19 A. Oh, so this is a recent piece of evidence for me, and

        20 I have set out in appendix J all the things I now want

        21 to look at.

        22 I don't have any evidence, remember, that the

        23 firefighters actively opened or shut dampers on any

        24 floor.

        25 Q. Professor Torero in his evidence was asked about the
        166

        1 potential smoke leakage onto the lobbies through these

        2 dampers, and he said this [Transcript of 20 November,

        3 page 192, lines 7 to 11]:

        4 "Answer: Well, the evidence is that the system is

        5 performing poorly because it's bringing smoke into the

        6 lobbies. Now, that could have been because of the

        7 non-compliances, but it could also have been because the

        8 system was designed to basically deal with one floor."

        9 I think what he was implying is that if you've got

        10 a fire and multi-storey fire across the building,

        11 potentially that system is dealing with a quantity of

        12 smoke that it wouldn't have otherwise dealt with.

        13 The question for you is: would you have expected the

        14 system, particularly in terms of leakage through those

        15 dampers, to have coped with those smoke levels?

        16 A. Okay, so can we just break that down a bit?

        17 So the system isn't dealing with a fire on multiple

        18 floors, in the sense it's not meant to be open on

        19 multiple floors, okay?

        20 Q. Yes.

        21 A. So at the moment, therefore, I don't understand

        22 Professor Torero's issue about smoke quantities.

        23 The system as a protected riser is required to

        24 provide compartmentation, yes, for a certain period in

        25 every lobby.
        167

        1 Q. That's 60 minutes?

        2 A. Yes, it is.

        3 Q. Yes.

        4 A. Yes. There are other pressure imbalances that might

        5 cause flowing of smoke out at level 23 particularly, but

        6 as I've said, there's all sorts of different things

        7 I must consider before I offer up any kind of opinion on

        8 why the smoke leaked on certain floors.

        9 I am clear in my own mind about the damper

        10 performance, but there are other things that I must

        11 consider too.

        12 Q. There's potentially some other written evidence. For

        13 example, Daniel Griffin, in a witness statement that was

        14 read out to the inquiry, refers to smoke spread via the

        15 vents into the 6th floor lobby.

        16 A. Yes.

        17 Q. Is that something that you will want to look into?

        18 A. I have been thinking -- yes, I am considering that.

        19 Q. So in terms of those smoke shafts on the north and the

        20 south side, you've also highlighted some potential

        21 issues around those shafts.

        22 They were retained in the refurbishment. They were

        23 originally builders' work shafts, serving the north and

        24 south sides of the lobbies; is that right?

        25 A. That's correct.
        168

        1 Q. You've examined them. Can we look at figure J.16 of

        2 your report, BLAS0000031 at page 56.

        3 A. Yes.

        4 Q. I think what we see -- I just want to look at a number

        5 of these figures -- is you have concluded that neither

        6 shaft was rendered, nor was it metal-lined.

        7 Let's stick with rendering.

        8 A. Yes.

        9 Q. Does that mean cemented to make it a smooth surface?

        10 A. Yes. So when someone like me wants to rely on

        11 a builders' work shaft for a smoke control system, both

        12 the British Standard and, actually, the Smoke Control

        13 Association guidance makes clear (a) that's perfectly

        14 appropriate, but (b) there's certain checks you have to

        15 do. So it's about making it as smooth as possible, and

        16 also checking if it leaks just by nature of its current

        17 condition.

        18 Q. If this was leaking, this shaft, what are the potential

        19 candidates in terms of where it leaks to?

        20 A. Oh, okay. Well, I would need to show you on a plan, but

        21 the walls here that we're looking at for the builders'

        22 duct are in the flats.

        23 Q. They're in the flats?

        24 A. Yes, they are, near -- well, it depends which flat, but

        25 they're near the front door, yes.
        169

        1 Q. You've noted it wasn't metal-lined either. Is that

        2 something you sometimes see in a smoke shaft like

        3 this --

        4 A. Yes.

        5 Q. -- that you will metal-line the whole thing?

        6 A. So if you can't apply a smooth finish, it might be that

        7 a designer would choose to provide a lining instead.

        8 But it has to be contemplated, is the point I'm making,

        9 in terms of then preventing so much friction when the

        10 fans switch on. Okay? It's trying to get the smoke up

        11 easily.

        12 Q. You've drawn attention in this particular photograph to

        13 mortar joints between blocks, which you say are visible,

        14 and then you've got the same diagonal line pattern as

        15 exhibited on the outside of shaft.

        16 A. I was trying to say that it's not been covered with

        17 something else from what I can see.

        18 The mortar joint is a good thing in the sense that

        19 that means it is sealed.

        20 Q. Can we look at a couple of other photographs after this.

        21 J.17, which is on the next page.

        22 A. Yes. So, again, just trying to say that I can see

        23 an external surface rather than a surface that's been

        24 covered with something else.

        25 Q. So, to you, is this concerning that you're seeing it in
        170

        1 this condition?

        2 A. On the inside, I would like to understand how the lining

        3 of the builders' work duct and its leakage was

        4 considered by the design team and factored in to the

        5 final design condition they provided.

        6 Q. Because you say at the moment you've not seen currently

        7 on what you've had any evidence that it was checked or

        8 tested during the refurbishment.

        9 A. That's correct, based on the papers given to me.

        10 Q. Let's finish off. If we look at J.18 and then J.19.

        11 A. Yes. I mean, it's the same thing again.

        12 Q. It's the same points.

        13 A. Just trying to show what is there so people can have

        14 that transparency.

        15 Q. Those builders' works ducts should've had a one-hour

        16 fire resistance, I think you say.

        17 A. Well, as an extension of the lobby, it should be two

        18 hours, but the dampers are one hour for the

        19 floor-to-floor separation.

        20 Q. Yes.

        21 A. Yes.

        22 Q. In terms of the contribution of these kind of issues,

        23 ie with the dampers and the shafts -- let's just think

        24 about them -- and the contribution they potentially

        25 might have played to smoke spread in the building, given
        171

        1 the scale of the fire and the fact that we know that

        2 numerous flat front doors did not have functioning

        3 door-closers or the doors were left open, isn't the most

        4 likely source of smoke in the lobbies due to the failure

        5 of the doors as people escaped into the lobbies, rather

        6 than these kind of compartmentation failings?

        7 A. So I have to say what I said this morning: it depends

        8 which lobby it is. There may have been lobbies where

        9 the doors were not left open, or opening very

        10 frequently, and smoke spread by other means is relevant.

        11 Q. Commissioning.

        12 You have looked at the available commissioning

        13 documentation that you've seen to date for the system.

        14 A. Yes.

        15 Q. Your view is, I think, that the Building Regulations

        16 require the works to have been carried out such that

        17 they can adequately perform the functions for which

        18 they're designed. Does that mean, in your view, that

        19 such systems need to be properly commissioned so as to

        20 demonstrate the adequate performance?

        21 A. Yes, to comply with regulation 7.

        22 Q. On the basis of commissioning documents you've seen to

        23 date, is it right that you have concerns about the

        24 commissioning process that was followed?

        25 A. Yes, I have.
        172

        1 Q. The detail is in your report, but in summary, is it

        2 right that you've looked at relevant guidance for

        3 commissioning, including the Smoke Control Association

        4 guidance, and you can't see evidence that all the

        5 relevant checks were carried out when commissioning the

        6 system?

        7 A. Yes, that's correct.

        8 Q. In terms of the evidence of its operation, both before

        9 and on the night, and whether the system was operating

        10 properly, you have said in your latest report that you

        11 want to revisit this in Phase 2, given the wealth of

        12 evidence that you've heard from firefighters and BSRs

        13 about the operation on the night.

        14 A. That's correct.

        15 Q. I'm therefore not going to put any points in detail

        16 about this, except to just look at a few points on the

        17 extent of what you have examined.

        18 You say that you know that the system worked in some

        19 way on the 4th floor because the building management

        20 system triggered an alert to Tunstall, that's the remote

        21 monitoring platform, at 00.54; is that right?

        22 A. That's correct. So we know that happened and I assume

        23 it was because of smoke at level 4 because of the time

        24 that that signal was sent. But, yes, I don't have any

        25 information, remember, about how that whole remote
        173

        1 monitoring system actually works.

        2 But we know a signal was received at a certain time,

        3 and there's no reason to think there was smoke anywhere

        4 else at that stage of events, so before 1 o'clock.

        5 Q. And that would be smoke relevant to the fire in flat 16

        6 at that point; is that correct?

        7 A. Correct.

        8 Q. You've referred to some resident evidence, resident

        9 Ahmed, relating to smoke coming from the level 4 lobby

        10 into the stair.

        11 A. Yes.

        12 Q. You say you're concerned that this might indicate that

        13 the system was not functioning as intended.

        14 Do you think it's going to be necessary to look at

        15 all of the evidence, including the firefighter evidence

        16 we've now heard, some of which might suggest that the

        17 lobby was less congested with smoke in the early stages?

        18 A. Yes, that's correct. So there's evidence of limited

        19 smoke in the level 4 lobby and then things changing, and

        20 this issue of doors being open and closed and where is

        21 very important.

        22 So all the very detailed breakdown of early

        23 firefighting activity, I'd like to compare that then

        24 with the different evidence about the conditions of

        25 smoke at level 4, and in the early stages when that was
        174

        1 a single fire condition, and if the system operated as

        2 intended.

        3 Q. You say in your report you've been able to look at the

        4 programming for the smoke control system.

        5 A. Yes.

        6 Q. You say that it does appear to have been correctly

        7 programmed to respond appropriately to the detection of

        8 smoke on level 4; is that correct?

        9 A. That's correct.

        10 Q. But you're unable to say on the night precisely which

        11 pieces of equipment activated as the system activation

        12 log in the HMI panel was overwritten by events after

        13 14 June before it was seized --

        14 A. That's correct.

        15 Q. -- and therefore is no longer available to you. So we

        16 don't have the data from the night; is that the point?

        17 A. Yes. So very unfortunately, we don't know the order of

        18 devices triggered.

        19 The software being correct is one positive thing,

        20 but then it means what it's controlling needs to

        21 physically be able to perform also.

        22 So there are two -- when you're checking a system in

        23 terms of handing over a building: does the software

        24 trigger the right devices at the right time, and can

        25 they physically react to the programming?
        175

        1 Q. The fact that that data is not available from the night,

        2 is that a significant gap in your knowledge in terms of

        3 how the system operated?

        4 A. I think it's very unfortunate.

        5 Q. Do you think that's going to hamper a conclusion about

        6 whether the system did operate properly, or do you think

        7 there are other things you can look at to --

        8 A. So it would have been the most useful piece of data, but

        9 instead -- and I've listed everything out at the back of

        10 appendix J -- there's all sorts of other data now I need

        11 to consider: noise, physical observations up at the

        12 roof, from the helicopter footage -- there's all pieces

        13 of data now that I need to piece together to understand

        14 if smoke indeed entered the shafts and left the shafts

        15 at the roof, and, remember, down at level 2 above the

        16 door.

        17 Q. You've also analysed at this stage the available

        18 firefighter evidence as to their attempts to operate the

        19 system.

        20 A. Yes, I have.

        21 Q. You've also reviewed the instructions available to the

        22 firefighters in the lobby next to the HMI panel; is that

        23 correct?

        24 A. Yes, I have.

        25 Q. To look at their clarity.
        176

        1 A. Yes.

        2 Q. We should bear in mind, I think -- is this right? -- the

        3 system operates in automatic mode when it's detected on

        4 the fire floor and it should operate automatically --

        5 A. Yes.

        6 Q. -- but there was a function, and there were various

        7 instructions given, about how the firefighters could

        8 override that and select a different floor --

        9 A. That's correct.

        10 Q. -- for the smoke control system to operate on if they

        11 wanted, for example, to operate it on floor 11 as

        12 opposed to floor 4?

        13 A. Yes, so the system provides two ways to do that: you

        14 switch the panel to on, and there is a touch-screen that

        15 allows you to pick a floor to change the function, to

        16 change the floor of operation; or you switch to on, and

        17 you go to the floor and use the yellow key switch in the

        18 lobby.

        19 The instructions actually only offer going to the

        20 floor with the yellow key switch as they were printed

        21 out underneath the panel on the night.

        22 Q. Yes.

        23 A. And I don't know why that is.

        24 Q. I just wanted to ask you about a few things to do with

        25 these instructions.
        177

        1 You've said in your report that the instructions to

        2 access the damper status are clear, so that's to look at

        3 what was happening for each individual damper on each

        4 individual floor; is that correct?

        5 A. Yes, it provides that function, yes.

        6 Q. But you say that the damper status indicators might not

        7 be providing accurate information, because what you've

        8 identified is that the switches from the dampers may not

        9 have been connected to the system, so that what you're

        10 seeing on the screen may not be telling you accurate

        11 information about the dampers.

        12 A. Exactly. You can get this kind of return signal, so the

        13 damper tells the controller, "I am open, I am shut".

        14 And that was disconnected in the tower.

        15 Q. Can we just go to that. That's BLAS0000031, page 141.

        16 If we go to J9.4.10.

        17 So I think this is where you explain that point.

        18 A. Yes.

        19 Q. Four lines down:

        20 "However, in Grenfell Tower these switches were not

        21 connected to the system."

        22 A. Yes.

        23 Q. Can you explain the basis on which you've concluded that

        24 they weren't connected to the system? How do you know

        25 that?
        178

        1 A. Because the wires are bundled and tied together.

        2 Q. Right. My next question falls away.

        3 You've just made this point, you also conclude that

        4 the instructions state that only one floor can be

        5 controlled at once, but do not state that the user must

        6 turn off the key at the floor of operation before

        7 another key switch could be operated to change the

        8 floor.

        9 A. That's correct.

        10 Q. So if someone's put their key in the little yellow box

        11 in floor 11 and they want to change it to floor 12, the

        12 instructions don't tell them they've got to take the key

        13 out at floor 11 --

        14 A. Yes, exactly. You have to finish your operation there

        15 and then go to another floor.

        16 Q. You've also pointed out that the restart system option

        17 would restart the system on the floor of activation,

        18 regardless of whether a key switch had been operated; is

        19 that right?

        20 A. Yes.

        21 Q. Do you think these instructions were as clear as they

        22 should've been to guide firefighters on the night?

        23 A. No, I do not.

        24 Q. Is it right that at Phase 2, in terms of the work you're

        25 going to do, you're going to review the operation by the
        179

        1 firefighters of the system on the night to try and look

        2 at what they might have done?

        3 A. Yes.

        4 Q. You say that the key to the HMI panel on the ground

        5 floor was found in the on position --

        6 A. It was, yes.

        7 Q. -- rather than in the "auto" position.

        8 A. That's correct. London Fire Brigade provided a photo of

        9 the key in the on position.

        10 Q. But you say it's unclear how or precisely when that

        11 happened, and there's no evidence that anyone did that

        12 intentionally, is that right, or shut down the system

        13 intentionally?

        14 A. Yes. So I don't know when that happened, and I don't

        15 know if either the touch-screen or the yellow key

        16 switches were then also used as they could have been

        17 when the main key was in the on position.

        18 Q. Do you intend to review the CCTV footage further in

        19 terms of those considerations?

        20 A. I will review it further and -- yes.

        21 Q. Watch Manager Dowden appears to have used a key to

        22 activate the yellow key panel in the lift lobby at

        23 ground floor.

        24 A. Yes.

        25 Q. We've seen pictures of that.
        180

        1 Based on your review of the software and how the

        2 system was supposed to operate, what would be the effect

        3 of that, of putting the key into the ground floor?

        4 A. Well, it depends what the condition at the main HMI

        5 panel was, and I don't know if it was in on or not when

        6 he did that.

        7 Q. If it was in on, would the effect of him putting his key

        8 into the yellow key switch mean that it was diverted to

        9 operate on the ground floor?

        10 A. Theoretically, yes. It should've opened the vents at

        11 ground floor.

        12 Q. Just generally in relation to that override facility in

        13 the smoke control system, are you aware of the LFB

        14 policy guidance in GRA 3.2 that the incident commander

        15 must not make any changes to a high-rise building's

        16 ventilation or fire safety system without first taking

        17 appropriate advice from either the responsible person or

        18 appropriately trained fire and rescue authority

        19 personnel?

        20 A. Yes, I'm aware of that.

        21 Q. Are you aware of any attempt by anyone during the course

        22 of the fire to seek advice or assistance from the

        23 responsible person as to the way in which that smoke

        24 ventilation system was supposed to operate?

        25 A. That's not something I've looked at yet, but I will be
        181

        1 looking at those types of activities when it comes to

        2 duties regarding the Regulatory Reform (Fire Safety)

        3 Order, which I haven't done yet, for responsible

        4 persons.

        5 Q. In relation to the performance of the lift doors --

        6 A. Yes.

        7 Q. -- your site inspection and report make no observations

        8 with regard to the performance and conditions of the

        9 lift doors, despite the fact you've noted that the doors

        10 were seemingly not specified as fire rated. Do you

        11 think that in order to fully consider possible smoke

        12 contamination routes, it's going to be important to have

        13 regard to the lift doors?

        14 A. Yes. I would like to have had the opportunity to do

        15 that, and I'm sure the lift expert can do that work.

        16 Q. If we leave aside the damper compartmentation issue for

        17 a moment and simply assume that the system was compliant

        18 but it didn't work on the fire floor on the night, would

        19 you agree that that would have limited effect on the

        20 spread of fire and smoke throughout the building?

        21 A. Its role is to stop smoke entering the staircase during

        22 early firefighting.

        23 Q. So does that mean you wouldn't agree with that, that you

        24 still think a compliance system on that --

        25 A. A perfect system designed to either extract smoke or
        182

        1 limit smoke movement on one floor obviously cannot

        2 operate on all floors simultaneously unless such

        3 a feature was provided.

        4 Q. Finally, I just wanted to look at your section J.11,

        5 which lists out all the further investigations that you

        6 wish to do as part of your Phase 2 work. Can we go to

        7 BLAS0000031, and start with page 152.

        8 A. Yes.

        9 Q. We don't have to go through all the detail of this, but

        10 is it right that what you've done in this last section

        11 is set out all the different work strands that you would

        12 like to do in order to understand better --

        13 A. Yes.

        14 Q. -- the system and whether it operated correctly on the

        15 night?

        16 A. Exactly.

        17 Q. And what the consequences were?

        18 A. Yes, exactly.

        19 Q. You have considering whether there's any evidence of

        20 noise from the fans.

        21 A. Yes.

        22 Q. All those questions that poor Mr Rawat had to keep on

        23 asking about noise and fans.

        24 A. Yes.

        25 Q. They're potentially important to you; is that right?
        183

        1 A. No, it's very important to understand if either

        2 firefighters or residents could hear these noises.

        3 The problem about fan noise at Grenfell Tower is the

        4 system was a combined system. So --

        5 Q. Yes. If we go over the page --

        6 SIR MARTIN MOORE-BICK: Sorry, did you finish?

        7 A. Yes. So I won't be able to rely just on noise in

        8 isolation.

        9 MS GRANGE: But these are all pieces of a jigsaw?

        10 A. All the different pieces, yes.

        11 SIR MARTIN MOORE-BICK: Mm.

        12 MS GRANGE: Then you have considering whether there's

        13 evidence of air movement, analyse the data from the

        14 post-fire condition of the smoke control system. You

        15 refer there to LFB Officer James Flin taking

        16 photographs.

        17 A. Yes.

        18 Q. I believe he's also provided a witness statement --

        19 A. Yes.

        20 Q. -- which you'll have to look at as well.

        21 A. Yes. I'll go through all of that. Also, I think the

        22 thing I'm most interested in is where soot was actually

        23 deposited. I think that's a really good piece of

        24 physical evidence.

        25 Q. Professor Stec of the University of Central Lancashire,
        184

        1 who has been appointed as an inquiry expert, she's done

        2 an investigation of soot deposits, and she's done

        3 a short summary, and you want to look in more detail at

        4 that.

        5 A. Yes, I do, because is there soot all the way up to the

        6 roof? Is there soot all the way down to level 2? Is

        7 there soot on the fan at level 2? Et cetera, et cetera.

        8 All of those things will allow us to understand if there

        9 ever was smoke in the system.

        10 Q. Do you agree it's going to be necessary to establish

        11 an accurate timeline in relation to internal and

        12 external smoke spread before you can reach any more

        13 definitive conclusions about whether the system operated

        14 as intended?

        15 A. I think that study is very important for a multitude of

        16 reasons. I mentioned the lifts getting filled with

        17 smoke earlier and all sorts of other things. Yes.

        18 MS GRANGE: Thank you.

        19 Mr Chairman, those are all of my questions.

        20 SIR MARTIN MOORE-BICK: Right. Would you like a chance to

        21 consider your homework?

        22 MS GRANGE: Exactly. So if we can just have a break, maybe

        23 10 minutes.

        24 SIR MARTIN MOORE-BICK: Yes.

        25 MS GRANGE: Well, 9 minutes. Let's go 4.05.
        185

        1 SIR MARTIN MOORE-BICK: Let's say 4.05, shall we?

        2 MS GRANGE: Then if there are any further questions --

        3 THE WITNESS: Do I need to leave?

        4 SIR MARTIN MOORE-BICK: It's usually convenient because

        5 other people may want to talk to counsel, so we'll both

        6 leave and come back at 4.05. All right? Thank very

        7 much.

        8 All right, 4.05, then, please.

        9 (3.55 pm)

        10 (A short break)

        11 (4.05 pm)

        12 SIR MARTIN MOORE-BICK: All right, Dr Lane. I haven't asked

        13 Ms Grange whether she has any more questions, but

        14 I suspect she has.

        15 MS GRANGE: Only one.

        16 SIR MARTIN MOORE-BICK: Only one.

        17 MS GRANGE: Which is good, about the roof. It's a question

        18 I put to Professor Torero, and I should have put it to

        19 you as well.

        20 Do you think on the night that the roof might have

        21 provided a refuge for occupants of the tower, had it

        22 been able to be accessed?

        23 A. When I was in the roof, I observed areas that were not

        24 impacted by fire and smoke.

        25 Q. So does that mean you think it might have been able to
        186

        1 be a refuge?

        2 A. Well, it's hypothetical because it was inaccessible. It

        3 is something that I do consider, as such, in my own

        4 work. But it was locked and inaccessible.

        5 Q. Okay.

        6 A. As I understand it.

        7 SIR MARTIN MOORE-BICK: I think the question asked you to

        8 assume that it was not.

        9 A. I know. Sorry, I just have that kind of brain, it's

        10 hard for me to do that. So all I can tell you is

        11 I observed myself there were areas not impacted by fire

        12 and smoke, and that's actually quite upsetting when you

        13 see that, but I don't know how it could have been

        14 actually used. I don't know how to answer that question

        15 at the moment.

        16 MS GRANGE: Do you think the proximity to the crown may have

        17 been an issue in terms of accessing the roof? Because

        18 as I understand it, you come up and you're out onto

        19 a lower parapet along the outside, right adjacent to the

        20 crown.

        21 A. That's correct.

        22 Q. Then if you want to access the inner roof, you have to

        23 go up a pretty scary ladder.

        24 A. Yes. So I'm happy to explain the access point and the

        25 location of the hazard when I doing that part of my
        187

        1 work. I will be much clearer then.

        2 MS GRANGE: Yes.

        3 Dr Lane, those are all the questions we have for

        4 you.

        5 I would just like to thank you and your team. All

        6 of our experts have worked incredibly hard within the

        7 timescales, but that really does particularly apply to

        8 you and your team. I think only we as the inquiry team

        9 know quite how hard you have all worked to produce the

        10 detailed report that you have, and I just want to give

        11 you our thanks, because we know an awful lot of blood,

        12 sweat and tears has gone into the writing of that

        13 report.

        14 THE WITNESS: Yes, it has, and I do want to say thank you to

        15 my own team. They have worked tirelessly for a very

        16 long period of time, but we were very happy to do so.

        17 SIR MARTIN MOORE-BICK: Well, we are very grateful to you

        18 because one can see how much time and effort has gone

        19 into this work and you giving us your opinion. I mean,

        20 it's a very substantial report.

        21 THE WITNESS: Thank you very much.

        22 SIR MARTIN MOORE-BICK: We are very grateful to you for

        23 putting your expertise at our disposal. Thank you very

        24 much indeed.

        25 THE WITNESS: Thank you very much.
        188

        1 SIR MARTIN MOORE-BICK: All right. Well, that's all, so you

        2 can go with the usher, if you would like to. Thank you

        3 very much.

        4 (The witness withdrew)

        5 SIR MARTIN MOORE-BICK: Right, Ms Grange, that's perhaps it

        6 for the day, is it?

        7 MS GRANGE: It is. I think we have Dr Glover tomorrow.

        8 SIR MARTIN MOORE-BICK: Yes. More expert evidence tomorrow

        9 in the form of Dr Glover.

        10 MS GRANGE: With Mr Kinnier.

        11 SIR MARTIN MOORE-BICK: Good. Thank you very much indeed.

        12 10 o'clock tomorrow, then, please, thank you.

        13 (4.10 pm)

        14 (The hearing adjourned until Tuesday, 27 November 2018

        15 at 10.00 am)

        16

        17 I N D E X

        18 DR BARBARA LANE (continued) ..........................1
        Questions by MS GRANGE (continued) ...............1
        19

        20

        21

        22

        23

        24

        25
        189